## TWR - 02042024
Project Name | Project Number | Connected Scheme Name | Account: Account Name | Connection Site: Site Name | Scheme: Scheme Name | Scheme Description | MW Effective From
[23-0225] UPPER GREENFIELDS - 175MW BESS | PRO-003682 | CS-09698 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-09705 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-09695 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 31/10/2033
|  | CS-09694 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-09700 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2033
|  | CS-09696 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-09704 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-09706 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-188 | St Fergus to New Deer 2 132kV Reinforcement – At New Deer 2 400kV Substation, establish a new 132kV busbar at New Deer 2 substation and install 2x240MVA 400/132kV transformers. Construct a new 132kV double circuit overhead line from New Deer 2 to St Fergus substation (Approx. 26 km). | 31/10/2033
|  | CS-09693 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-09697 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-09699 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-09701 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-09702 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-09703 | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
Aberarder Wind Farm | PRO-000368 | CS-06328 | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation | SHET-RI-129 | Farigaig SGT1 Upgrade - Upgrade the 120MVA 275/132kV SGT1 at Farigaig substation to a 240MVA SGT, to facilitate the connection of generation in the area. | 30/08/2025
|  | CS-05449 | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation | SHET-RI-089 | Upgrade the 120MVA 275/132kV SGT1 at Farigaig substation to a 240MVA SGT to facilitate the connection of generation in the area. | 30/08/2025
|  | CS-05446 | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/08/2025
|  | CS-05447 | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation | Aberarder item 2 | Modification of the protection and telecommunication equipment at Farigaig 132kV and Dunmaglass 132kV substations. | 30/08/2025
|  | CS-05448 | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation | Aberarder item 1 | Construction of approximately 5km of 132kV overhead line between Dunmaglass – Farigaig 132kV overhead line, 10km south of Farigaig 275/132kV substation, and the wind farm substation. At the wind farm substation, the 132kV overhead line will terminate onto a new 132kV line disconnector located within the substation compound. | 30/08/2025
Aberthaw (Tertiary) | PRO-000376 | CS-05450 | ENSO GREEN HOLDINGS LIMITED | Aberthaw 275kV Substation | 100649-201328 | Install earthing transformer on 13kV tertiary connection with standard impedance. Install 13kV cable connecting earthing transformer to DCB. Install 72.5kV, 40kA rated DCB to connection assets for Users connection. | 31/10/2024
Aberthaw Energy | PRO-001697 | CS-04589 | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation | 101328-202648 | 1. Works to facilitate the use of Aberthaw 275kV substation’s spare bay for the User’s connection. | 30/10/2028
|  | CS-04590 | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 30/10/2028
|  | CS-04591 | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation | 020903-020903 | Uprating of the Cowley - Walham 400kV circuit cables to achieve 1500MVA post-fault summer rating. | 30/10/2028
|  | CS-04592 | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 30/10/2028
|  | CS-04771 | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation | 033769-033769 | Reconductor Hinkley Point – Taunton circuits 1 and 2 to achieve 2680MVA pre-fault summer rating. | 30/10/2028
Aberthaw PV & BESS Generation | PRO-001815 | CS-07149 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 101644-203282 | Works to facilitate the use of Aberthaw 275kV substation’s ex-generator bay for the User’s connection | 30/06/2029
|  | CS-07150 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 101645-203282 | Extension of the future consolidated South Wales Operational Tripping Scheme (functioning as a commercial operational tripping scheme for this User) | 30/06/2029
|  | CS-07151 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 100424-200970 | Reconductor the Bramley – Melksham 400kV circuits 1 and 2 to achieve a pre-fault summer rating of 1990MVA | 30/06/2029
|  | CS-07152 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 020903-020903 | Uprating/replacement of the Cowley – Walham and Cowley - Minety 400kV circuits cables sections to achieve 1193MVA or greater prefault Summer rating. | 30/06/2029
|  | CS-07153 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 033769-033769 | Reconductor Hinkley Point – Taunton circuits 1 and 2 to achieve 2680MVA pre-fault summer rating. | 30/06/2029
|  | CS-07154 | CYP SOLAR LIMITED | Aberthaw 275kV Substation | 101562-203112 | Reconductor Taunton - Exeter circuits 1 and 2 to achieve 2680MVA pre-fault summer rating. | 30/06/2029
Achany Extension Wind Farm | PRO-001555 | CS-06644 | SSE GENERATION LIMITED | ACHANY EXTENSION WIND FARM 132/33KV Substation | Achany Extension Enabling Works | Installation of an indoor type 132kV line disconnector (113) and 132kV circuit breaker (110) on the 132kV side of the 132/33kV transformer at the wind farm site. The line disconnector (113) will connect to the incoming ~17.5km, 132kV Trident wood pole overhead line 132kV circuit (with a minimum pre-fault summer rating of 120MVA) from Shin substation. The 132kV OHL will be connected to Shin substation via a new fully equipped 132kV double busbar feeder bay, comprising 132kV line disconnector (303), 132kV feeder circuit breaker (305) and 132kV double busbar selection disconnectors (304/306) and associated protection equipment. | 01/04/2027
|  | CS-06645 | SSE GENERATION LIMITED | ACHANY EXTENSION WIND FARM 132/33KV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 01/04/2027
|  | CS-06646 | SSE GENERATION LIMITED | ACHANY EXTENSION WIND FARM 132/33KV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 01/04/2027
Achrugan Wind Farm | PRO-002267 | CS-08254 | Statkraft Windco 1 Limited | Achrugan 132kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/07/2029
|  | CS-08255 | Statkraft Windco 1 Limited | Achrugan 132kV Substation | SHET-RI-106b | Connagil 2nd SGT – At Connagil substation, install a 2nd 275/132kV 120/240MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit. (SHET-RI-106b) | 31/07/2029
|  | CS-08256 | Statkraft Windco 1 Limited | Achrugan 132kV Substation | SHET-RI-191 | Strathy Switching Collector Station 132kV - Install 12km approximately of new 275kV double circuit overhead line between Connagill 275/132kV substation and a new 132kV switching collector station at Strathy North Wind Farm substation. The OHL double circuit will be built on steel lattice towers. This reinforcement is dependent upon TORI-106b Connagill 2nd SGT, looking at installing a new 480MVA transformer at Connagill substation (SGT1). If the works of this TORI are progressed, TORI-168 need to be cancelled and the offers issued to the following wind farms need to be amended as follows: -Armadale and Strathy South wind farms to update the TCA, One-off works and sole use works. -Kirkton wind farm to update the TCA and sole use works as per the new network design and double check the protection system configuration if additional devices are needed.(SHET-RI-191) | 31/07/2029
|  | CS-08253 | Statkraft Windco 1 Limited | Achrugan 132kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/07/2029
Ackron Wind Farm | PRO-001446 | CS-06710 | ACKRON WIND FARM LTD | Dounreay GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/08/2028
|  | CS-06711 | ACKRON WIND FARM LTD | Dounreay GSP | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/08/2028
AGS Calderside Battery Energy Storage System | PRO-002752 | CS-09236 | Advance Grid Solutions Ltd | Calderside 275kV Substation | AGS Calderside Battery Energy Storage System H1 | 1. Extension of Strathaven 275kV compound to accommodate a new 275kV feeder bay 2. Installation of one new 275kV double busbar switchgear (circuit breaker and associated double busbar disconnectors) 3. Installation of one 275kV line isolator at Strathaven 275kV substation 4. Installation of approx. 4.77km of 275kV UGC from Strathaven 275kV substation to AGS Calderside BESS 275kV substation 5. Install one 275kV line disconnector at the AGS Calderside BESS site | 31/10/2028
|  | CS-09237 | Advance Grid Solutions Ltd | Calderside 275kV Substation | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 31/10/2028
AGS Harestonhill BESS | PRO-003656 | CS-09772 | Advance Grid Solutions Ltd | Coylton GSP | SPT-RI-3406 | 4. Blacklaw 400kV Collector Substation - To establish a new 400kV collector substation, fed from Wishaw 400kV substation via a single 400kV circuit. The collector substation is to be named Blacklaw 400kV collector substation. The project involves establishing a new 400kV bay at Wishaw 400kV GIS substation, installing approx. 300m of 400kV UGC to the Blacklaw 400kV collector site. | 31/10/2030
|  | CS-09773 | Advance Grid Solutions Ltd | Coylton GSP | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 31/10/2030
Al Boum Photo (Norton) | PRO-001651 | CS-04897 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101333-202653 | Establish a new 400kV substation, provisionally referred to as Norton East 400kV, to the East of the existing Norton 400kV substation. Connect the new substation to the transmission system via a turn in of the existing Norton – Saltholme 400kV circuit to form a new Norton – Norton East 400kV and Norton East – Saltholme 400kV circuit | 31/10/2031
|  | CS-04898 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101552-203093 | Busbar extension at Norton East 400kV to provide space for the User’s generator bay | 31/10/2031
|  | CS-04899 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 31/10/2031
|  | CS-04900 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101093-202181 | Establish a new 400kV double circuit route between Creyke Beck 400kV and High Marnham 400kV substation including all associated substation works | 31/10/2031
|  | CS-04901 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101554-203095 | Reconductor the new High Marham - Staythorpe 400 kV circuit with 2x620mm2 GZTACSR conductor | 31/10/2031
|  | CS-04902 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-04903 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 31/10/2031
|  | CS-04904 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm2 conductor | 31/10/2031
|  | CS-04905 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 31/10/2031
|  | CS-04906 | AL BOUM PHOTO LTD | Norton 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 31/10/2031
|  | CS-04907 | AL BOUM PHOTO LTD | Norton 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 31/10/2031
|  | CS-04908 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm2 cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm2 cable. | 31/10/2031
|  | CS-04909 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101576-203163 | Uprate the Norton - Osbaldwick 1 and 2 400kV circuits | 31/10/2031
|  | CS-04910 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-04911 | AL BOUM PHOTO LTD | Norton 400kV Substation | 100818-201654 | Establish a new 400kV circuit between Creyke Beck and Grimsby West 400kV substations | 31/10/2031
|  | CS-04912 | AL BOUM PHOTO LTD | Norton 400kV Substation | 020640-020640 | Reconductor the 2x500mm2 sections of the Norton – Osbaldwick 1 400kV circuit with 2x700mm2 conductor strung for operation at 90°C | 31/10/2031
|  | CS-04913 | AL BOUM PHOTO LTD | Norton 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a post-fault winter rating of 3100MVA | 31/10/2031
Alcemi Bathgate No 2 | PRO-004011 | CS-09181 | ALCEMI STORAGE DEVELOPMENTS 8 LTD | Bathgate 400kV Substation | SPT-RI-3002 | Harburn 400kV Substation- Establish a new 400kV double busbar substation, indicatively named Harburn substation. The location of the SPT’s new 400kV substation is currently under review, with an initial view that it will tie into the existing XJ Route (STHA-TORN / WISH-SMEA/FALL) as well as facilitate a turn in of the XM Route (Kincardine-Currie circuit) following uprating as part of the HND process | 31/10/2030
|  | CS-09180 | ALCEMI STORAGE DEVELOPMENTS 8 LTD | Bathgate 400kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 31/10/2030
Alcemi Bramford Battery Energy Storage Facility | PRO-001416 | CS-07210 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 30/10/2030
|  | CS-07211 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 101722-10003191 | At Norwich Main 400kV: Replace circuit breakers X130 and X1030. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 30/10/2030
|  | CS-07212 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 30/10/2030
|  | CS-07213 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400 kV with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3100 MVA. | 30/10/2030
|  | CS-07214 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 30/10/2030
|  | CS-07215 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 100875-201758 | Build a new 400kV substation for the connection of North Falls, Five Estuaries and Tarchon. Part of the South East Anglia Enabling Works Bramford - Tilbury new 400kV OHL route. | 30/10/2030
|  | CS-07216 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 100875-202039 | Build a new 400 kV double circuit between East Anglia Coastal 400 kV and Tilbury 400 kV substations with a minimum rating of 3000 MVA winter postfault. | 30/10/2030
|  | CS-07217 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 100875-202041 | At Tilbury 400kV Substation: Extension of busbars for the provision of 2 feeder bays for the CLAC-TILB OHL | 30/10/2030
|  | CS-07218 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 30/10/2030
|  | CS-07219 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 100875-201761 | Build a new 400 kV double circuit between Bramford 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter post-fault. | 30/10/2030
|  | CS-07202 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 101721-203430 | Extension of Bramford 400kV substation double busbars and establishing separate compound, to provide space for customer bay installation, including a circuit transfer from the existing Bramford 400kV substation, 2 bus sections and a bus coupler. | 30/10/2030
|  | CS-07203 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 100875-202040 | At Bramford 400kV GIS Substation: Extend busbars in the North and South for the provision of 2 feeder bays for the BRFO-CLAC OHL | 30/10/2030
|  | CS-07204 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 101723-10003192 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 30/10/2030
|  | CS-07205 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 30/10/2030
|  | CS-07206 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 30/10/2030
|  | CS-07207 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 101294-202560 | At Norwich Main 400kV: Replace circuit breakers X120, X230, X210, X410 and X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 30/10/2030
|  | CS-07208 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3820 MVA | 30/10/2030
|  | CS-07209 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 30/10/2030
Alcemi Coalburn Battery Energy Storage Facility | PRO-001459 | CS-06655 | ALCEMI STORAGE DEVELOPMENTS 4 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 31/10/2025
|  | CS-06656 | ALCEMI STORAGE DEVELOPMENTS 4 LIMITED | Coalburn 400kV GIS Substation | Alcemi Coalburn 1 (H1) | 1. Installation of a new 400kV double busbar bay at Coalburn including a 400kV circuit breaker and associated equipment. 2. Installation of a new 400kV cable circuit (approx. 2.5km) between Coalburn 400kV substation and the User’s site. 3. Installation of a 400kV line disconnector at the User’s site. | 31/10/2025
Alcemi Devilla Battery Energy Storage Facility | PRO-001453 | CS-06688 | ALCEMI STORAGE DEVELOPMENTS 3 LIMITED | Longannet 275kV Substation | SPT-RI-1880 | Longannet to Westfield / Mosmorran 275kV circuit uprate - It is proposed to uprate the existing Longannet – Westfield – Mosmorran circuits (both north and south) by reconductoring to accommodate the generation in the area. The following circuits shall be reconductored: Reconductor ~26.5km of the overhead line (on both sides of the towers) between YJ001 to YJ075 with twin Rubus 85C (anticipated; subject to further verification); Reconductor ~3km of the overhead line (on both sides of the towers) between YJ075 to YJ084 with twin Totara 85C (anticipated; subject to further verification); Reconductor ~5.5km of overhead line (on both sides of the towers) between YV001 to YV015 with twin Totara 85C (anticipated; subject to further verification). | 30/10/2027
|  | CS-06689 | ALCEMI STORAGE DEVELOPMENTS 3 LIMITED | Longannet 275kV Substation | Alcemi Devilla H1 Works | At a location close to Longannet substation, on YG Route, establish a cable sealing end and install ~4km of 275kV cable circuit (required 554MVA) by tee connect onto YG Route to the Alcemi Devilla site. 2 At the Alcemi Devilla site, install one 275kV disconnector. 3 Provision of communications, alarms, indications and metering from the User site | 30/10/2027
|  | CS-06687 | ALCEMI STORAGE DEVELOPMENTS 3 LIMITED | Longannet 275kV Substation | SPT-RI-1879 | Culross 275kV substation turned in Longannet to Mosmorran circuit - A new substation will be established on the Longannet – Mosmorran 275kV circuit (YJ Route) approximately between YJ010 and YJ011. The YJ route (south circuit) will be turned in to the new substation with a 275kV circuit breaker on each side which will be connected to a new 275kV busbar. | 30/10/2027
Alcemi Score 2 Battery Energy Storage Facility | PRO-001790 | CS-07158 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Peterhead GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2029
|  | CS-07159 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Peterhead GSP | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2029
|  | CS-07160 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Peterhead GSP | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2029
|  | CS-07161 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Peterhead GSP | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2029
|  | CS-07162 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Peterhead GSP | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2029
|  | CS-07163 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Peterhead GSP | SHET-RI-025d | North East Reinforcement | 31/10/2029
|  | CS-07164 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Peterhead GSP | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2029
|  | CS-07165 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Peterhead GSP | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2029
Alcemi Score Battery Energy Storage Facility | PRO-001575 | CS-04310 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | Alcemi Score H1 Works | Installation of a 400kV disconnector at the User’s site, on the Network side of the circuit breaker mentioned above. | 31/10/2029
|  | CS-04311 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2029
|  | CS-04312 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2029
|  | CS-04313 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2029
|  | CS-04314 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2029
|  | CS-04315 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-025d | North East Reinforcement | 31/10/2029
|  | CS-04316 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2029
|  | CS-04317 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2029
|  | CS-04318 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2029
|  | CS-04319 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2029
|  | CS-04320 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2029
|  | CS-04321 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2029
|  | CS-04322 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-165 | Alcemi substation 400kV Switchgear - Overhead line works to bring the 400kV circuit to ground, including any required modifications. Design and installation of one 400kV circuit breaker with three 400kV disconnectors and associated protection and control equipment for the circuit. | 31/10/2029
|  | CS-04323 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2029
|  | CS-04324 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2029
|  | CS-04325 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2029
|  | CS-04326 | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2029
Allt an Tuir Renewable Energy Park | PRO-001819 | CS-07268 | ALLT AN TUIR RENEWABLE ENERGY PARK LIMITED | Shin GSP | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 30/09/2027
|  | CS-07269 | ALLT AN TUIR RENEWABLE ENERGY PARK LIMITED | Shin GSP |  | FALSE | 30/09/2027
Alverdiscott | PRO-001136 | CS-04788 | PIVOTED POWER LLP | Alverdiscott 400kV Substation | NGET-R1-100248-200688 (INFRA) | 1. Install earthing transformer on 13 kV tertiary connection 2. Install 13 kV cable from tertiary connection to motorised disconnector 3. Install 13 kV disconnector and associated earthing switches connecting tertiary to connection assets for Users connection | 31/10/2029
|  | CS-04789 | PIVOTED POWER LLP | Alverdiscott 400kV Substation | NGET-RI-30752 | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. | 31/10/2029
|  | CS-04790 | PIVOTED POWER LLP | Alverdiscott 400kV Substation | NGET-RI-31671-2 | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. | 31/10/2029
| PRO-001344 | CS-04773 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 01/11/2027
|  | CS-04774 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 01/11/2027
|  | CS-04775 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 &amp; 2 Circuits to provide a post fault winter rating of 3140MVA. | 01/11/2027
|  | CS-04776 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 101010-202014 | Works to enable generation connection of 1.8GW for Xlinks at Alverdiscott 400kV substation. | 01/11/2027
|  | CS-04777 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 020903-020903 | Uprating of the Cowley - Minety 400kV circuit and the Cowley - Minety 400kV cables to achieve 950MVA pre-fault summer rating. | 01/11/2027
|  | CS-04778 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 101051-202109 | Uprating of the Cowley - Walham 400kV OHL sections only to achieve a summer pre-fault summer rating of 2000MVA. | 01/11/2027
|  | CS-04780 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 100889-201781 | Hotwire Bramley - Melksham 1 &amp; 2 Circuits from 50C to 75C | 01/11/2027
|  | CS-04787 | XLINKS 1 LTD | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1+2 circuits to achieve a Pre-fault summer rating of 1680MVA | 01/11/2027
Alyth | PRO-001978 | CS-07712 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 31/10/2029
|  | CS-07719 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-025d | North East Reinforcement | 31/10/2029
|  | CS-07728 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2029
|  | CS-07713 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2029
|  | CS-07714 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 31/10/2029
|  | CS-07726 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2029
|  | CS-07715 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50oC operation to 275kV 65oC operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65oC,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 31/10/2029
|  | CS-07727 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2029
|  | CS-07716 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 31/10/2029
|  | CS-07717 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2029
|  | CS-07720 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2029
|  | CS-07722 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2029
|  | CS-07724 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-117 | Tealing 275kV Busbar Upgrade – At Tealing substation, upgrade the 275kV busbar to a rating of 4000A, and install a new 275kV bus coupler circuit breaker on the east side of the busbar. | 31/10/2029
|  | CS-07725 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2029
|  | CS-07718 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2029
|  | CS-07721 | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2029
Alyth BESS Station | PRO-002466 | CS-09549 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-09560 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-09555 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-09548 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-09554 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-09558 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-09556 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-117 | Tealing 275kV Busbar Upgrade – At Tealing substation, upgrade the 275kV busbar to a rating of 4000A, and install a new 275kV bus coupler circuit breaker on the east side of the busbar. | 31/10/2033
|  | CS-09559 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-09557 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-09552 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-09547 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-09550 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-09551 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-09553 | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
AMP Eccles BESS | PRO-003836 | CS-09604 | Eccles Grid Stability Limited | Eccles 132kV Substation | SPT-RI-2080 | Dunlaw Extension to Galashiels Reinforcements – The works in this reinforcement entails the construction of a new 132kV overhead line (OHL) between Dunlaw Extension 132kV substation and Galashiels 132kV substation. The new OHL will be built on L7 steel lattice towers and strung with twin UPAS conductor. The new OHL will be tee-ed to the proposed Galashiels North 400kV substation. At Galashiels North 400kV two 400/132kV 360MVA transformer will be installed to establish connectivity to the new OHL. Two 400kV bay will be added to the 400kV substation to connect the transformers and two 132kV circuit breakers will be installed to connect the transformers to the new OHL. | 31/10/2029
|  | CS-09605 | Eccles Grid Stability Limited | Eccles 132kV Substation | AMP Eccles | 1. A 132kV disconnector at Eccles 132kV on the Relevant Transmission Licensee’s side of the new 132kV metering circuit breaker. 2. Relevant civil works necessary to accommodate the new 132kV disconnector at Eccles 132kV. | 31/10/2029
|  | CS-09602 | Eccles Grid Stability Limited | Eccles 132kV Substation | SPT-RI-151b | In order to provide GBSQSS compliant connections for additional generation requiring to export from Hawick/Galashiels to Eccles, it is proposed to construct a new 132kV double circuit tower line between Galashiels and Eccles, and remove the existing U and AT Routes. | 31/10/2029
|  | CS-09603 | Eccles Grid Stability Limited | Eccles 132kV Substation | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 31/10/2029
Annan Road BESS | PRO-004059 | CS-09793 | SP Distribution plc | Dumfries GSP | SPT-RI-298 | Chapelcross to Gretna OHL Reinforcement | 28/04/2028
|  | CS-09791 | SP Distribution plc | Dumfries GSP | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 28/04/2028
|  | CS-09792 | SP Distribution plc | Dumfries GSP | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 28/04/2028
Aquind Interconnector | PRO-000285 | CS-05455 | AQUIND LIMITED | Lovedean 400kV Substation | 31832-3 | Thermal reinforcement to the South Coast | 30/06/2027
|  | CS-05456 | AQUIND LIMITED | Lovedean 400kV Substation | 31671-2 | Re-conductoring Fleet - Lovedean 1&2 circuits | 30/06/2027
|  | CS-05457 | AQUIND LIMITED | Lovedean 400kV Substation | 33585 | Extend Lovedean 400KV substation to the East and West including connection into Sellindge OTS system | 30/06/2027
|  | CS-05458 | AQUIND LIMITED | Lovedean 400kV Substation | 30752 | Build and install a South West Operational Tripping Scheme (OTS) | 30/06/2027
|  | CS-05459 | AQUIND LIMITED | Lovedean 400kV Substation | 31671-1 | Re-conductoring Bramley - Fleet 1&2 circuits | 30/06/2027
Arbroath Battery Substation | PRO-000950 | CS-04270 | ARBROATH LIMITED | Arbroath GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 21/02/2022
|  | CS-04271 | ARBROATH LIMITED | Arbroath GSP | Arbroath Enabling | At Arbroath 132/33kV GSP substation, install two 90MVA 132/33kV transformers within the existing substation. Install protection, control, metering and ancillary equipment. The new equipment will be installed to meet current Fire Separation Standards. | 21/02/2022
|  | CS-04272 | ARBROATH LIMITED | Arbroath GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 21/02/2022
Ardleigh Solar & BESS | PRO-002644 | CS-09357 | Nembus BESS Limited | Hadleigh 400kV Substation | 100875-201761 | Build a new 400 kV double circuit between Bramford 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter post-fault. | 31/10/2032
|  | CS-09359 | Nembus BESS Limited | Hadleigh 400kV Substation | 101786-203721 | At Pelham 400 kV Substation: Install 3000MVA QBs on the (Pelham to Rye House 1&2 circuits (PELH4-1 - RYEH4A and PELH4-2 - RYEH4B circuits) | 31/10/2032
|  | CS-09340 | Nembus BESS Limited | Hadleigh 400kV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400 kV with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3100 MVA. | 31/10/2032
|  | CS-09343 | Nembus BESS Limited | Hadleigh 400kV Substation | 101247-202487 | The circuits running from Leighton Buzzard to Sundon 1&2 (LEIB4A-SUND4- 1) and LEIB4B-SUND4-2 will also be reconductored with 4 x 400mm2 conductor rating 2870MVA, 75˚C for winter intact condition. | 31/10/2032
|  | CS-09349 | Nembus BESS Limited | Hadleigh 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 31/10/2032
|  | CS-09363 | Nembus BESS Limited | Hadleigh 400kV Substation | 101883-203859 | Uprating of the Coryton South – Rayleigh Main (A68A) 400kV circuit cables to achieve 3002MVA pre-fault summer rating | 31/10/2032
|  | CS-09362 | Nembus BESS Limited | Hadleigh 400kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 31/10/2032
|  | CS-09345 | Nembus BESS Limited | Hadleigh 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm2 and 3M curlew 2x490mm2 @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm2 conductor | 31/10/2032
|  | CS-09348 | Nembus BESS Limited | Hadleigh 400kV Substation | 100468-201037 | The circuits running from Cowley to East Claydon (COWL4-ECLA4-1) and Cowley to Leighton Buzzard (COWL4-LEIB4A-1) will also be reconductored with 4 x 400mm2 conductor rating 2870 MVA, 75˚C for winter intact condition | 31/10/2032
|  | CS-09351 | Nembus BESS Limited | Hadleigh 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 31/10/2032
|  | CS-09336 | Nembus BESS Limited | Hadleigh 400kV Substation | 102774-205610 | Construction of a new 400kV AIS double busbar 400kV substation (Hadleigh 400kV) between Bramford 400kV – Braintree 400kV substations, comprising of 2 feeder bays and 1 bus coupler bay | 31/10/2032
|  | CS-09355 | Nembus BESS Limited | Hadleigh 400kV Substation | 100875-201758 | Build a new 400kV substation for the connection of North Falls, Five Estuaries and Tarchon. Part of the South East Anglia Enabling Works Bramford - Tilbury new 400kV OHL route. | 31/10/2032
|  | CS-09361 | Nembus BESS Limited | Hadleigh 400kV Substation | 101956-204071 | Reconductor TILBURY4-TILBURY4B-1 (TILB4-TILB4B-1) 400kV circuit to achieve a higher MVA (2809) rating summer pre-fault. | 31/10/2032
|  | CS-09364 | Nembus BESS Limited | Hadleigh 400kV Substation | 101295-202561 | Power Control Technology on Tilbury to Kingsnorth 400kVA circuit (NOA) | 31/10/2032
|  | CS-09365 | Nembus BESS Limited | Hadleigh 400kV Substation | 101296-202563 | Power Control Technology on Tilbury to Grain 400kVA circuit (NOA) | 31/10/2032
|  | CS-09347 | Nembus BESS Limited | Hadleigh 400kV Substation | 101248-204325 | Add a new bus coupler and three new bays at Wymondley 400kV substation to facilitate the turn in of the existing Pelham to Sundon 400kV circuit at Wymondley 400kV substation. | 31/10/2032
|  | CS-09350 | Nembus BESS Limited | Hadleigh 400kV Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 31/10/2032
|  | CS-09353 | Nembus BESS Limited | Hadleigh 400kV Substation | 033461- 033461 | Post-completion of BTNO works, reconductor Bramford-Pelham 1 400kV circuits with 3 x700mm2 AAAC conductors to achieve a post-fault winter rating of 3100 MVA | 31/10/2032
|  | CS-09337 | Nembus BESS Limited | Hadleigh 400kV Substation | 102774-205612 | Extend Hadleigh 400kV substation main and reserve 1 busbar for the provision of one User bay. | 31/10/2032
|  | CS-09339 | Nembus BESS Limited | Hadleigh 400kV Substation | 102774-205611 | Provide a single turn in of the 400kV OHL circuit 1 or circuit 2 (TBC after completion of BTNO works) at tower 4YL024 between Bramford 400kV – Braintree 400kV substations to Hadleigh 400kV substation | 31/10/2032
|  | CS-09354 | Nembus BESS Limited | Hadleigh 400kV Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 31/10/2032
|  | CS-09356 | Nembus BESS Limited | Hadleigh 400kV Substation | 100875-202039 | Build a new 400 kV double circuit between East Anglia Coastal 400 kV and Tilbury 400 kV substations with a minimum rating of 3000 MVA winter postfault. | 31/10/2032
|  | CS-09358 | Nembus BESS Limited | Hadleigh 400kV Substation | 031867-200324 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 31/10/2032
|  | CS-09360 | Nembus BESS Limited | Hadleigh 400kV Substation | 101955-204070 | Reconductor TILBURY2-WARLEY2-1 (TILB2-WARL2-1) 400kV circuit to achieve a higher MVA (1049) rating summer pre-fault. | 31/10/2032
|  | CS-09352 | Nembus BESS Limited | Hadleigh 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 31/10/2032
|  | CS-09341 | Nembus BESS Limited | Hadleigh 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 31/10/2032
|  | CS-09342 | Nembus BESS Limited | Hadleigh 400kV Substation | 100952-201899 | Reconductor EAST CLAYDON-LEIGHTON BUZZARD (ECLA4- LEIB4B-1) 400kV circuit to achieve a minimum rating of 2450MVA summer pre-fault rating | 31/10/2032
|  | CS-09344 | Nembus BESS Limited | Hadleigh 400kV Substation | 033750-033750 | Uprate the circuit bay Busbar, CT and Circuit Breaker attached to existing A654 circuit (BRFO-PELH) and uprate the circuit bay Busbar, CT, Circuit Breaker, disconnector and main protection system on the newly formed second Bramford – Pelham circuit (currently part of A646 BRFO-BRAI circuit) to achieve a post fault winter rating of 3820MVA | 31/10/2032
|  | CS-09346 | Nembus BESS Limited | Hadleigh 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400kV circuits with 3x700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. | 31/10/2032
|  | CS-09338 | Nembus BESS Limited | Hadleigh 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 31/10/2032
Ardoch Farm Battery Storage | PRO-002431 | CS-08935 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Kilmorack GSP |  | FALSE | 30/04/2026
Arecleoch | PRO-000012 | CS-06707 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132kV Substation | Arecleoch - H1 Works | At Arecleoch Repowering substation install two disconnectors on the HV side of the transformers. At Arecleoch Repowering substation establish a 275kV busbar to which the two disconnectors and a 275kV circuit breaker, to connect the 275kV underground cable, are connected. Install around 9.5km of 275kV underground cable circuit to connect the wind farm substation to Mark Hill substation, continuous summer rating 250MVA. At Arecleoch Repowering substation install a second 275kV CB on the underground circuit to which a 60MVar reactor is connected. At Mark Hill extend the substation to install a 275kV circuit breaker to which the underground 275kV circuit will connect. | 15/06/2032
|  | CS-06708 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 15/06/2032
|  | CS-06709 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 15/06/2032
Arecleoch Windfarm Extension | PRO-001111 | CS-05460 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132kV Substation | Areceloch Ext H1 Cable | Installation of a 132kV cable system from Mark Hill 132kV circuit breaker to an appropriate location where the 132kV wood pole overhead line will be constructed. | 01/08/2025
|  | CS-05461 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132kV Substation | SPT-RI-282 | Markhill SGT4 | 01/08/2025
|  | CS-05462 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132kV Substation | Areceloch Ext H1 OHL | Installation of approximately 5km of 132kV wood pole overhead line between Mark Hill and Arecleoch Extension 132kV Substation. | 01/08/2025
|  | CS-05463 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132kV Substation | Arecleoch Ext H1 SS | At Mark Hill Substation install a new 132kV switch bay and associated equipment and apparatus | 01/08/2025
Armadale Wind Farm | PRO-000557 | CS-06222 | WIND DEVELOPMENT HOLDINGS LIMITED | Armadale 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 01/08/2027
|  | CS-06223 | WIND DEVELOPMENT HOLDINGS LIMITED | Armadale 132/33kV Substation | Armadale WF H1 Sole Enabling Works | Construction of a 15km single 132kV circuit from Connagill 275/132kV substation, comprising 15km 132kV underground cable trident wood pole overhead line (OHL), terminating on an indoor 132kV disconnector installed within the Relevant Transmission Licensee’s building at Armadale 132/33kV substation. The 132kV Circuit will be connected to Connagill 132/33kV Substation via new fully equipped 132kV feeder circuit bay, including all necessary protection and control. | 01/08/2027
|  | CS-06219 | WIND DEVELOPMENT HOLDINGS LIMITED | Armadale 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 01/08/2027
|  | CS-06220 | WIND DEVELOPMENT HOLDINGS LIMITED | Armadale 132/33kV Substation | SHET-RI-106b | Connagil 2nd SGT – At Connagil substation, install a 2nd 275/132kV 120/240MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit. (SHET-RI-106b) | 01/08/2027
|  | CS-06221 | WIND DEVELOPMENT HOLDINGS LIMITED | Armadale 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 01/08/2027
Arresgill Energy Storage 1 | PRO-003246 | CS-09620 | Arresgill Energy Storage 1 Limited | Arresgill 132kV Substation | SPT-RI-2320 | 0 | 31/10/2031
|  | CS-09619 | Arresgill Energy Storage 1 Limited | Arresgill 132kV Substation | SPT-RI-231 | 0 | 31/10/2031
|  | CS-09621 | Arresgill Energy Storage 1 Limited | Arresgill 132kV Substation | SPT-RI-3191 - Arresgill 132/33kV Substation | The scope of this TORI shall consist of the installation of a new 400kV double busbar feeder bay and associated switchgear (circuit breaker and DBB disconnectors) and a 400/132kV 240MVA Super Grid Transformer at Wyseby Hill substation. From here a new 132kV circuit shall be installed out to the new collector substation called Arresgill 132/33kV substation. Two new 132/33kV 120MVA Grid Transformers will be installed at Arresgill 132/33kV substation with associated 132kV circuit breakers (HV side of GT’s) and 33kV indoor circuit breakers (LV side of GT’s) at Arresgill substation. Establish two 33kV switchboards (‘A’ and ‘B’ board) at Arresgill substation, this shall provide a connection to two separate 33kV circuit breaker bays covered off under the appropriate connection offers. | 31/10/2031
Arresgill Wind Farm | PRO-002409 | CS-08222 | ARRESGILL ENERGY LIMITED | Arresgill 132kV Substation | SPT-RI-231 | 0 | 31/10/2031
|  | CS-08223 | ARRESGILL ENERGY LIMITED | Arresgill 132kV Substation | SPT-RI-2320 | 0 | 31/10/2031
Artfield Forest Windfarm | PRO-001310 | CS-05464 | ARTFIELD FOREST WIND FARM LTD | Newton Stewart GSP | SPT-RI-198 | At Newton Stewart 132/33kV substation, a second 132/33kV transformer will be installed as part of a separate project in order to accommodate contracted generation on a firm basis. To enable the transformer installation, substation works are required involving a new 132kV line isolator to connect the second grid transformer onto the existing T2 33kV circuit breaker. | 01/05/2026
|  | CS-05465 | ARTFIELD FOREST WIND FARM LTD | Newton Stewart GSP | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 01/05/2026
|  | CS-05466 | ARTFIELD FOREST WIND FARM LTD | Newton Stewart GSP | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 01/05/2026
|  | CS-05467 | ARTFIELD FOREST WIND FARM LTD | Newton Stewart GSP | SPT-RI-223 | Reconductor the existing circuits between Glenlee and Newton Stewart with High Temperature Low Sag conductors. | 01/05/2026
|  | CS-05468 | ARTFIELD FOREST WIND FARM LTD | Newton Stewart GSP | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 01/05/2026
|  | CS-05469 | ARTFIELD FOREST WIND FARM LTD | Newton Stewart GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 01/05/2026
|  | CS-05470 | ARTFIELD FOREST WIND FARM LTD | Newton Stewart GSP | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 01/05/2026
Artfield Forest Wind Farm | PRO-003578 | CS-08531 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 28/06/2030
|  | CS-08529 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | Artfield Forest Wind Farm H1 Works | 1. At an appropriate location on BT Route (anticipated to be around BT052-053), establish a new 132kV substation and installing a 132kV circuit breaker and associated line disconnectors to tee onto the overhead line. 2. Install a new steel tower and associate downleads. 3. Install approx. 7km of 132kV OHL (minimum of 90MVA required) to Artfield Forest wind farm site. 4. At the wind farm site, install one 132kV disconnector. | 28/06/2030
|  | CS-08532 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-223 | Reconductor the existing circuits between Glenlee and Newton Stewart with High Temperature Low Sag conductors. | 28/06/2030
|  | CS-08534 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 28/06/2030
|  | CS-08535 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-2802 | Artfield Tee – Newton Stewart 132kV OHL circuit uprate - In order to alleviate overloads on the 132kV circuit between the proposed tee location and Newton Stewart (on BT Route No.1 side) associated with the connection of the Artfield Forest Windfarm, it is required to uprate the stretch of circuit. It is proposed to uprate the stretch of circuit with 250mm2 AAAC (Sycamore), which will provide sufficient headroom to remove any intact overloads seen on the system. (SPT-RI-2802) | 28/06/2030
|  | CS-08530 | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 28/06/2030
ARVEN OFFSHORE WIND FARM | PRO-003288 | CS-09485 | ARVEN OFFSHORE WIND FARM LIMITED | Arven 400/66kV Offshore Substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 31/10/2033
|  | CS-09483 | ARVEN OFFSHORE WIND FARM LIMITED | Arven 400/66kV Offshore Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-09482 | ARVEN OFFSHORE WIND FARM LIMITED | Arven 400/66kV Offshore Substation | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 31/10/2033
|  | CS-09481 | ARVEN OFFSHORE WIND FARM LIMITED | Arven 400/66kV Offshore Substation | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 31/10/2033
|  | CS-09484 | ARVEN OFFSHORE WIND FARM LIMITED | Arven 400/66kV Offshore Substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50oC operation to 275kV 65oC operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65oC,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 31/10/2033
Auchentiber Farm | PRO-003601 | CS-08544 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 17/10/2029
|  | CS-08545 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 17/10/2029
|  | CS-08546 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-2268 | BZ Route No.2 Uprating - Generation connections into the Devol Moor – Erskine 132kV circuit have identified the need to uprate the No.2 side of BZ Route between Erskine and Braehead Park. It has been noted through system studies that an outage on the Erskine to Braehead circuit (BZ No.1) could result in overloads on the No.2 side. In order to alleviate these overloads, it is required to uprate the OHL and cable sections of the circuit. It is proposed to install 1x 280mm2 AAAC “Sycamore” conductor on the OHL sections operating at 75℃ with similarly rated cable sections | 17/10/2029
|  | CS-08549 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-2833 | Devol Moor 400kV GIS Substation - At Devol Moor 400kV it is proposed to establish a new indoor GIS Double Busbar substation. The building is proposed to be sized to accommodate 14 bays. The initial GIS substation assets to be installed include the followings (subject to review):  5x 400kV Feeder Bays and associated switchgear; SGT1, SGT2, HUNE, WIYH and High Mathernock BESS  1x 400kV Bus Coupler  1x 400kV Bus Section  Space to be included with building to accommodate future connections  Removal of redundant equipment at existing 400kV Devol Moor substation. | 17/10/2029
|  | CS-08547 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-2311 | G Route Modernisation - The existing G Route 132kV Devol Moor to Erskine overhead line (OHL) is predominantly situated close to the coastline and is approximately 16km in length supported on 50 lattice towers (PL-1 design) built in 1929 as a single circuit. The majority of the conductors (175mm2 Lynx ACSR) and earthwire (70mm2 Horse ASCR) were replaced in 1960. The route has been identified as at end of life and a result its replacement with a new 132kV OHL circuit is proposed. The replacement scheme would entail the construction of a new 132kV single circuit wood pole overhead line being Devol Moor substation and Erskine substation. The approximate length of the circuit would be 17km and shall comprise of 250mm2 Sycamore AAAC and OPPC Sycamore equivalent phase wire (middle phase) incorporating a fibre optic cable for communications and protection purposes. They will have the overall effect on reducing the visual impact along the route and overcome environmental and landowner issues that currently prevail on the existing G Route | 17/10/2029
|  | CS-08548 | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 17/10/2029
Auchnasavil Battery Storage | PRO-002127 | CS-07558 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2032
|  | CS-07559 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 31/10/2032
|  | CS-07562 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SPT-RI-028 | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | 31/10/2032
|  | CS-07554 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | Intertrip Scheme - Auchnasavil | An intertrip scheme will be installed to facilitate the non-firm connection. The intertrip scheme requires the provision of signals at Carradale 132/33kV GSP Substation, to the host Distribution Network Operator, should either (or both) 33kV metering circuit breakers (3T0 or 4T0) at Carradale Grid Supply Point be opened, resulting in the loss of GT3 or GT4. | 31/10/2032
|  | CS-07561 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 31/10/2032
|  | CS-07563 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 31/10/2032
|  | CS-07555 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2032
|  | CS-07557 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 31/10/2032
|  | CS-07556 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2032
|  | CS-07564 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SPT-RI-2319 | Carradale – Kilmarnock South subsea cable - Installation of 2 x 240MVA 220kV subsea cable circuits from Carradale (SHE Transmission) to the South of Troon. Installation of two underground cable circuits from the South of Troon to Kilmarnock South and two associated 400/220kV transformer at Kilmarnock South (SP Transmmission). | 31/10/2032
|  | CS-07560 | Auchnasavil Battery Storage Ltd | Carradale 1 GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 31/10/2032
Auchteraw Energy Storage | PRO-001658 | CS-04400 | FIELD AUCHTERAW LTD. | Fort Augustus GSP | Replacement of the existing 15MVA transformer to a 90MVA transformer | The replacement of the existing 15MVA 132/33kV Transformer with a redeployed 90MVA 132/33kV Transformer at the GSP. The works shall include the foundation and associated compound works to facilitate the new equipment. A new 33kV switchboard will be installed to connect to the Host DNO’s equipment. | 31/12/2022
|  | CS-04401 | FIELD AUCHTERAW LTD. | Fort Augustus GSP | Installation of a 132kV Transformer Circuit Breaker and Disconnector at Fort Aug | The installation of a 132kV Transformer Circuit Breaker and Disconnector at Fort Augustus GSP. | 31/12/2022
Aultmore Wind Farm (2023) | PRO-003975 | CS-09164 | VATTENFALL WIND POWER LTD | Aultmore Wind Farm 132/33kV Substation | SHET-RI-221 | 3. Macduff to Blackhillock 132kV Works – Establish a new 132 kV tee point of the Macduff to Blackhillock 132kV HMN circuit. Upgrade 4.7km of 132kV OHL on the Macduff to Blackhillock 132kV HMN circuit to a minimum summer pre-fault capacity of 245MVA. Upgrade 3.3km of 132kV underground cable on the Macduff to Blackhillock 132kV HMN circuit to a minimum summer pre-fault capacity of 245MVA. | 30/09/2030
|  | CS-09165 | VATTENFALL WIND POWER LTD | Aultmore Wind Farm 132/33kV Substation | Aultmore WF (2023) enabling works | 1. Installation of a 132kV circuit breaker and 132kV disconnector at the new Aultmore Wind Farm 132/33kV substation, including the 132kV cabling and works to connect the 132/33kV 120MVA grid transformer. Approximately 5.8km of 132kV single circuit overhead line will be required as part of this connection. Installation of a further 132kV circuit breaker and 132kV disconnector will be required at a new substation compound located between the Macduff to Blackhillock 132kV circuits | 30/09/2030
|  | CS-09163 | VATTENFALL WIND POWER LTD | Aultmore Wind Farm 132/33kV Substation | SHET-RI-079 | Additional 275/132kV SGT’s at Blackhillock - Reinforce the transmission network at Blackhillock substation by installing two additional new 275/132kV Supergrid Transformers. The transformers are to be rated at 360MVA. (SHETL- RI-079) | 30/09/2030
Aurora Offshore Windfarm | PRO-001774 | CS-04973 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101604-203228 | Infrastructure works for the generation connection of Aurora Offshore Wind Farm. | 31/10/2031
|  | CS-04974 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101604-203229 | Extension of the South West OTS to incorporate the Aurora Offshore Wind Farm. | 31/10/2031
|  | CS-04975 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 31/10/2031
|  | CS-04976 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Hinkley Point - Exeter 400kV circuits to achieve a 3100MVA post fault winter rating. Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating | 31/10/2031
|  | CS-04977 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 020903-020903 | Uprating of the Cowley - Walham 400kV circuit cables to achieve 1500MVA post-fault summer rating. | 31/10/2031
|  | CS-04978 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 31/10/2031
|  | CS-04979 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 31/10/2031
|  | CS-04980 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault Summer rating of 1650MVA. | 31/10/2031
|  | CS-04981 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-04982 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 31/10/2031
|  | CS-04983 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101619-203253 | Reconductoring of the Landulph – Langage 2 circuit to achieve a post-fault Summer rating of 2150MVA. | 31/10/2031
|  | CS-04984 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101620-203254 | Reconductoring of the Landulph – Indian Queens 2 circuit to achieve a post-fault Summer rating of 2300MVA. | 31/10/2031
|  | CS-04985 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 31/10/2031
|  | CS-04986 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-04987 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 31/10/2031
|  | CS-04988 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 31/10/2031
|  | CS-04989 | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 31/10/2031
Awel Y Mor Extension | PRO-000529 | CS-05471 | AWEL Y MOR OFFSHORE WIND FARM LIMITED | Bodelwyddan 400kV Substation | 100570-201193 | Extension of the GIS busbar at Bodelwyddan 400kV GIS substation to allow for the connection of the User’s generator bay and the double turn in of the existing CONQ4-BODE/PENT4- 1 & 2 teed circuits. | 01/04/2027
|  | CS-05472 | AWEL Y MOR OFFSHORE WIND FARM LIMITED | Bodelwyddan 400kV Substation | 100570-201374 | 2. Double turn-in of PENT-BODE-CONQ 1 & 2 circuits - PENT end of circuit 2 to utilise existing OHL between T and BODE s/s (GM line). New OHL to carry CONQ end of (PENT-BODECONQ) circuit 2 turn in, and circuit 1 T. Building of 2 new bays to accommodate additional circuits | 01/04/2027
|  | CS-05473 | AWEL Y MOR OFFSHORE WIND FARM LIMITED | Bodelwyddan 400kV Substation | 032018-032018 | Reconductor the existing Quad Zebra CONQ legs of PENT-BODE-CONQ 1 & 2 Circuits to meet the post fault requirement of 2570MVA | 01/04/2027
Axminster | PRO-001017 | CS-04803 | HB825AXM LTD | Axminster 400kV Substation | 101382-202707 | Expand Axminster 400kV into a 4 Switch Mesh Turn in the Exter - Chickerell onto the Mesh Expansion of Axminster 132kV Install Bus Section Breaker 120 at Axminster 132kV Installation of the 3rd SGT feeding Axminster 132kV | 31/10/2024
|  | CS-04805 | HB825AXM LTD | Axminster 400kV Substation | 101562-203112 | Reconductor Taunton - Exeter circuits 1 and 2 to achieve 2680MVA pre-fault summer rating. | 31/10/2024
|  | CS-04806 | HB825AXM LTD | Axminster 400kV Substation | 100805-201625 | 1. Extend Axminster 132kV substation boundary 2. Extend Axminster 132kV main and reserve busbars to provide space for User’s generator bay 3. Works required to connect the User to the Category 2 Melksham Operational Tripping Scheme as described in appendix F3 of the Bilateral Connection Agreement. | 31/10/2024
|  | CS-04807 | HB825AXM LTD | Axminster 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 31/10/2024
|  | CS-04808 | HB825AXM LTD | Axminster 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 &amp; 2 Circuits to provide a post fault winter rating of 3140MVA. | 31/10/2024
|  | CS-04809 | HB825AXM LTD | Axminster 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 &amp; 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 31/10/2024
|  | CS-04810 | HB825AXM LTD | Axminster 400kV Substation | 033769-033769 | Reconductor Hinkley Point – Taunton circuits 1 and 2 to achieve 2680MVA pre-fault summer rating. | 31/10/2024
|  | CS-04801 | HB825AXM LTD | Axminster 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 1990MVA | 31/10/2024
| PRO-001143 | CS-05474 | PIVOTED POWER LLP | Axminster 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 31/10/2027
|  | CS-05475 | PIVOTED POWER LLP | Axminster 400kV Substation | 033773-033773 | Thermal uprating of Bramley - Fleet OHL circuits to increase capacity. | 31/10/2027
|  | CS-05476 | PIVOTED POWER LLP | Axminster 400kV Substation | 100298-200724 | Re-conductor Fleet - Lovedean OHL circuits to increase capacity. | 31/10/2027
|  | CS-05477 | PIVOTED POWER LLP | Axminster 400kV Substation | 100757-202247 | 1. Substation boundary extension to accommodate the User’s Connection Assets. 2. Install a tertiary cable box or bushing on SGT1. 3. Install a 13kV cable (if required) from tertiary cable box or bushing to earthing transformer. 4. Install an earthing transformer. 5. Install 13kV Disconnector connecting the tertiary connection to Connection Assets. 6. Works required to connect the User to the Melksham Operational Tripping Scheme as described in F3. 7. Works required to connect User to Category 2 intertripping scheme as outline in Appendix F3. | 31/10/2027
| PRO-001740 | CS-04791 | CSE25 LIMITED | Axminster 400kV Substation | 101617-203250 | 1. Extend Axminster 132kV substation boundary 2. Extend Axminster 132kV main and reserve busbars to provide space for User’s generator bay 3. Works required to connect the User to the Category Melksham Operational Tripping Scheme as described in Appendix F3 of the Bilateral Connection Agreement. 4. Auto close scheme following the loss of an SGT during an outage of another SGT on he same section | 31/10/2028
|  | CS-04792 | CSE25 LIMITED | Axminster 400kV Substation | 101382-202707 | Expand Axminster 400kV into a 4 Switch Mesh Turn in the Exter - Chickerell onto the Mesh Expansion of Axminster 132kV Install Bus Section Breaker 120 at Axminster 132kV Installation of the 3rd SGT feeding Axminster 132kV | 31/10/2028
|  | CS-04793 | CSE25 LIMITED | Axminster 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 31/10/2028
|  | CS-04794 | CSE25 LIMITED | Axminster 400kV Substation | 033769-033769 | Reconductor the Taunton - Hinkley Point - Exeter 400kV circuits to achieve a 3100MVA post fault winter rating. Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating | 31/10/2028
|  | CS-04795 | CSE25 LIMITED | Axminster 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 &amp; 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 31/10/2028
|  | CS-04796 | CSE25 LIMITED | Axminster 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 &amp; 2 Circuits to provide a post fault winter rating of 3140MVA. | 31/10/2028
|  | CS-04797 | CSE25 LIMITED | Axminster 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 1990MVA | 31/10/2028
|  | CS-04798 | CSE25 LIMITED | Axminster 400kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 31/10/2028
Axminster - New Connection | PRO-001356 | CS-04802 | ENSO GREEN HOLDINGS B LIMITED | Axminster 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 30/06/2025
|  | CS-04804 | ENSO GREEN HOLDINGS B LIMITED | Axminster 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 &amp; 2 Circuits to provide a post fault winter rating of 3140MVA. | 30/06/2025
|  | CS-04799 | ENSO GREEN HOLDINGS B LIMITED | Axminster 400kV Substation | 101059-202122 | 1. Extend Axminster 132kV substation to accommodate new bay connection 2. Substation control modification and bus bar protection. 3. Works required to connect the User to the Melksham Operational Tripping Scheme as described in F3. 4. Works required to connect User to Category 2 intertripping scheme as outline in Appendix F3. | 30/06/2025
|  | CS-04800 | ENSO GREEN HOLDINGS B LIMITED | Axminster 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 &amp; 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 30/06/2025
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | PRO-002100 | CS-08944 | AYRE OFFSHORE WIND FARM LIMITED | Dounreay 400kV | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-08952 | AYRE OFFSHORE WIND FARM LIMITED | Dounreay 400kV | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 31/10/2033
|  | CS-08953 | AYRE OFFSHORE WIND FARM LIMITED | Dounreay 400kV | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-08948 | AYRE OFFSHORE WIND FARM LIMITED | Dounreay 400kV | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 31/10/2033
|  | CS-08945 | AYRE OFFSHORE WIND FARM LIMITED | Dounreay 400kV | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-08950 | AYRE OFFSHORE WIND FARM LIMITED | Dounreay 400kV | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-08946 | AYRE OFFSHORE WIND FARM LIMITED | Dounreay 400kV | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-08949 | AYRE OFFSHORE WIND FARM LIMITED | Dounreay 400kV | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-08951 | AYRE OFFSHORE WIND FARM LIMITED | Dounreay 400kV | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-08947 | AYRE OFFSHORE WIND FARM LIMITED | Dounreay 400kV | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
Ayrshire Grid Services Facility | PRO-001090 | CS-04633 | FLEXIBLEGRIDPOWER LTD | Hunterston East 400kV substation | SPT-RI-1566 | Hunterston East to Ayrshire Grid 400kV switchgear and cable works - It is proposed to extend the GIS double busbar and install a new 400kV switchbay at Hunterston East 400kV GIS substation, install approximately 900m of 400kV underground cable from the Hunterston East 400kV GIS substation to a new collector substation (Ayrshire Grid 400kV collector substation). At the collector substation, a new outdoor 400kV busbar and three isolators shall be installed. | 29/03/2024
Baillie Greener Grid Park | PRO-001701 | CS-04970 | STATKRAFT UK LTD | Baillie 275KV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2026
|  | CS-04971 | STATKRAFT UK LTD | Baillie 275KV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/10/2026
|  | CS-04972 | STATKRAFT UK LTD | Baillie 275KV Substation | Baillie Greener Grid - Enabling Works | 1. 275kV single busbar within the Baillie 275kV substation 2. The works will include the construction of 250m 275kV OHL from the Dounreay side of circuit UT2 to loop-in to the new Baillie 275kV substation 3. The works also include the construction of 250m 275kV OHL from the Thurso side of circuit UT2 to loop-in to the new Baillie 275kV substation. | 31/10/2026
Balliemeanoch PSH | PRO-001901 | CS-08071 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 31/10/2034
|  | CS-08076 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SPT-RI-028 | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | 31/10/2034
|  | CS-08077 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 31/10/2034
|  | CS-08078 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SPT-RI-2347 | Windyhill/Inveranan/Dalmally/Creag Dhubh 275kV Intertripping Scheme - Install new load management schemes at the following locations: Dalmally 275kV, Inverarnan 275kV and Windyhill 275kV. Measure digital and analogue signals of the 275kV circuits between Windyhill – Creag Dhubh, Windyhill – Inverarnan, Inverarnan – Dalmally and Creag Dhubh – Dalmally. These signals shall be shared to SHE Transmission at Creag Dhubh 275kV substation. Relevant signal and communication interface between SP Transmission and SHE Transmission shall be carried out. | 31/10/2034
|  | CS-08075 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bipole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 31/10/2034
|  | CS-08079 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | Balliemeanoch PSH - 275kV double busbar bay | Installation of a new 275kV double busbar bay at Creag Dhubh 275kV substation, connected to a new 275kV circuit comprised of 7.5km of 275kV tower line and 3km of 275kV cable to the new Balliemeanoch 275kV substation. At the Balliemeanoch 275kV substation, terminate the new 275kV circuit on 1x 275kV line disconnector (L17). | 31/10/2034
|  | CS-08073 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 31/10/2034
|  | CS-08074 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 31/10/2034
|  | CS-08070 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2034
|  | CS-08069 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2034
|  | CS-08072 | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2034
Ballygroggan Wind Farm | PRO-003733 | CS-09714 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 31/10/2034
|  | CS-09715 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2034
|  | CS-09718 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 31/10/2034
|  | CS-09719 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bipole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 31/10/2034
|  | CS-09721 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | Ballygroggan 132kV Feeder Bay | The works include the installation of a new 132kV feeder bay, consisting of 2x 132kV disconnectors and 1x 132kV circuit breaker, located at the future Greenland 132kV substation. | 31/10/2034
|  | CS-09713 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | SHET-RI-034 | Inverarnan 132kV QBs - Install 2 x 132kV 240MVA QBs at Inverarnan substation in series with the two 275/132kV SGTs connected to the Dalmally – Windyhill 275kV line. (SHET-RI-034) | 31/10/2034
|  | CS-09720 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | SHET-RI-253 | Carradale - Greenland 132kV Single Circuit OHL | 31/10/2034
|  | CS-09723 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | Ballygroggan - Disconnector | This circuit will terminate onto a new 132kV line disconnector switch located at the Ballygroggan 132/33kV substation | 31/10/2034
|  | CS-09712 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | SHET-RI-013 and SPT-RI-028 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existing Inveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers. Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. Reconfigure Dalmally 275kV substation to a double busbar arrangement to allow the extension of the substation to develop new bays for the connection of renewable generation. (SHET-RI-013 and SPT-RI-028) | 31/10/2034
|  | CS-09717 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 31/10/2034
|  | CS-09722 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | Ballygroggan - 132kV Circuit | The works also include establishment of a new 132kV single circuit connection between Greenland 132kV substation and the new Ballygroggan 132/33kV substation. This will comprise approximately 14km of 132kV wood pole overhead line. | 31/10/2034
|  | CS-09716 | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation | SHET-RI-130a | North Argyll – Craig Murrail 275kV Operation - Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Creag Dhubh substation (established as part of SHET-RI-013) to Craig Murrail Substation. This will require the upgrade of substations on this circuit for 275kV operation | 31/10/2034
Balmeanach Wind Farm | PRO-001438 | CS-06690 | WIND 2 PROJECT 1 LIMITED | Edinbane GSP | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 31/07/2027
|  | CS-06691 | WIND 2 PROJECT 1 LIMITED | Edinbane GSP | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 31/07/2027
|  | CS-06692 | WIND 2 PROJECT 1 LIMITED | Edinbane GSP | SHET-RI-135 | 4. Broadford – Edinbane Reinforcement (SHET-RI-135) | 31/07/2027
|  | CS-06693 | WIND 2 PROJECT 1 LIMITED | Edinbane GSP | Balmeanach Item 1 | Installation of 132kV Disconnector and Circuit breaker, housed indoors with GT2, in addition to 132kV cabling and busbar works to connect new transformer (GT2) | 31/07/2027
|  | CS-06694 | WIND 2 PROJECT 1 LIMITED | Edinbane GSP | Balmeanach Item 2 | Replace the existing 33kV Transformer Circuit Breaker 1T0 located within Dunvegan 132/33kV GSP substation compound with the equivalent new equipment rated appropriately. | 31/07/2027
|  | CS-06695 | WIND 2 PROJECT 1 LIMITED | Edinbane GSP | Balmeanach Item 3 | Install a new 120MVA transformer and associated switchgear at Dunvegan GSP, extending the 132kV busbar appropriately. Supply and install circuit breaker 2T0, in a location to be provided by the User. | 31/07/2027
Balnacraig Battery Storage | PRO-002244 | CS-08110 | BALNACRAIG BATTERY STORAGE LIMITED | Alness GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/03/2024
Balvedavist 162 Battery Storage | PRO-002024 | CS-07954 | Sun4net Ltd | Mybster 132/33kV Substation | no Scheme | 0 | 31/07/2027
|  | CS-07955 | Sun4net Ltd | Mybster 132/33kV Substation | 132kV Disconnector | Installation of a new 132kV disconnector (704) at Spittal 132kV substation. | 31/07/2027
|  | CS-07949 | Sun4net Ltd | Mybster 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/07/2027
|  | CS-07956 | Sun4net Ltd | Mybster 132/33kV Substation | Protection and telecommunication equipment | Modification of the protection and telecommunication equipment at Spittal 132kV substation. | 31/07/2027
|  | CS-07953 | Sun4net Ltd | Mybster 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/07/2027
Balwyllo BESS | PRO-002352 | CS-08573 | BALWYLLO BESS LIMITED | Bridge of Dun GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 30/06/2032
|  | CS-08572 | BALWYLLO BESS LIMITED | Bridge of Dun GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 30/06/2032
Bankend Rig Extension Wind Farm | PRO-000755 | CS-05383 | SP Distribution plc | Kilmarnock South GSP | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 31/10/2022
Bankend Rig III Wind Farm | PRO-003451 | CS-08400 | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation | SPT-RI-2827 | Redshaw to Hagshaw Tee 132kV Circuit - Construct a new 132kV double busbar bay at Redshaw 132kV substation and from here install a new 132kV cable/OHL circuit to an appropriate point at which a tee off shall be established for the Bankend Rig III Collector substation and Hagshaw Hill Ph3 WF connections. | 30/04/2030
|  | CS-08397 | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 30/04/2030
|  | CS-08399 | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation | SPT-RI-2826 | Hagshaw Tee to Bankend Rig III Collector Substation -Install a new 132kV trident wood pole circuit between the tee off with Hagshaw Hill Ph3 Wind Farm and the Bankend Rig III collector. The circuit capacity required for this overhead line circuit is 126MVA. The chosen conductor system for the desktop exercise is AAAC UPAS conductor. The circuit length is approximately 18km. At the Hawkwood substation a new 132/33kV substation shall be created with a 132kV circuit breaker and line disconnector being installed alongside a 132/33kV 120MVA transformer . A 33kV 3 Panel board shall be installed with one feeder being captured under this TORI and the remaining two being allocated to Hawkwood WF and Hawkwood Wind Farm. | 30/04/2030
|  | CS-08396 | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 30/04/2030
|  | CS-08398 | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation | SPT-RI-2139 | Redshaw 400/132kV SGT2 - a new 360MVA 400/132kV supergrid transformer and associated 400kV and 132kV circuit breakers will be installed. This will increase the thermal capacity of Redshaw 132kV substation. | 30/04/2030
Bankhead BESS | PRO-003236 | CS-09473 | GPC Battery Ltd | Eccles 400kV Substation | SPT-RI-131 | ZT route overhead line uprating works (Branxton- Eccles) | 30/10/2036
|  | CS-09474 | GPC Battery Ltd | Eccles 400kV Substation | SPT-RI-3232 | Bankhead 400kV Substation and 400kV OHL Works - To facilitate the connection of a Battery Storage connection a new 400kV substation will be need to be created and looped into one side of the existing ZA 400kV OHL Route. The 400kV OHL works as well as the creation of this new substation will be established under SPT-RI-3232 which this new Battery Storage connection shall be contingent upon | 30/10/2036
Barking BESS | PRO-003518 | CS-08448 | O&G SOLAR (SPV 52) LIMITED | Barking 275kV Substation | 102416 - 204944 | 1. Extend the Substation compound at Barking to accommodate the new SGT. This may require the purchase of additional land and Substation extension. 2. Install and commission a new 275kV Supergrid Transformer (SGT) bay at Barking 275kV substation. This equipment will include the HV side SGT bay disconnectors and circuit breakers. 3. Install 275kV cabling from the new 275kV bay at Barking 275kV to the new SGT. 4. Install and commission a new 120MVA rated 275/33kV SGT 5. Install 33kV cabling from the LV side of the SGTs to the relevant bay at Barking West 33kV substation. 6. At Barking West 33kV substation, modify the current arrangement of SGT 8 to create a 33kV Bay for the new SGT. This equipment will include the LV side SGT bay disconnectors, circuit breakers and busbar selector disconnectors. 7. Install CTs in the Users Generator Bay at Barking West 33kV and link these to the Busbar Protection. Note these will not be for Metering purposes. | 31/10/2028
Barr River Hydro | PRO-001001 | CS-06177 | Scottish Hydro Electric Power Distribution Plc | Fort William GSP | SHET-RI-045a | 3. Fort Augustus–Fort William 132kV OHL Upgrade Phase 1 - Reconductor the 132kV double circuit OHL between Fort Augustus and Fort William (FFW). The 132kV double circuit OHL (FFW) is to be reconductored with a higher capacity conductor. This will have a minimum summer pre-fault rating of 208MVA per circuit. Transfer the connection of Invergarry power station from FFE circuit of the OHL between Fort Augustus and Fort William to the FFW circuit. Temporarily transfer the connection of the Kinlochleven (FV1) 132kV circuit to FFW for the duration of the FFE reconductoring work. (SHET-RI-045a) | 31/05/2021
|  | CS-06178 | Scottish Hydro Electric Power Distribution Plc | Fort William GSP | SHET-RI-045b | 1. Fort Augustus–Fort William 132kV OHL Upgrade Phase 2 - Reconductor one side of the 132kV double circuit OHL between Fort Augustus and Fort William (FFE). The 132kV circuit OHL (FFE) is to be reconductored with a higher capacity conductor. This will have a minimum summer pre-fault rating of 208MVA per circuit. Replace the existing 132kV cables on FFE & FFW into Fort Augustus with new 132kV cables rated suitably for the increased capacity of the new OHL conductor. Reinstate the permanent connection of the 132kV Kinlochleven circuit (FV1) to FFE following the completion of FFE reconductoring work. (SHET-RI-045b) | 31/05/2021
Bearsden BESS | PRO-004404 | CS-09504 | BEARSDEN BESS LTD | Windy Hill Grid 132kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 31/10/2028
|  | CS-09506 | BEARSDEN BESS LTD | Windy Hill Grid 132kV Substation | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 31/10/2028
|  | CS-09505 | BEARSDEN BESS LTD | Windy Hill Grid 132kV Substation | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 31/10/2028
Beatrice Sync Comp | PRO-001757 | CS-04603 | TINZ PROGRAMME 1 PROJECTCO 3 LIMITED | Beatrice 400kV Substation | TINZ Beatrice H1 works | 1. Construct a busbar extension to the Beatrice SGT2 / 400kV Harmonic Filter 2 circuit, adjacent to the existing 400kV Harmonic Filter 2 connections. 2. Support insulators, gantry and connections to the 0MW User’s 400kV disconnector. | 31/05/2024
Beaw Field Wind Farm | PRO-000026 | CS-05479 | BEAW FIELD SHETLAND LIMITED | Beaw Field 132/33kV Substation | SHET-RI-053 | Shetland 600MW HVDC Link and Kergord 132kV Substation ‒ Construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Noss Head in Caithness. The HVDC switching station works will be part of SHET-RI-062 and will integrate with the Caithness-Moray Transmission Reinforcement (part of SHET-RI-031). The HVDC link includes a 600MW HVDC converter station and 132kV Substation at Kergord in Shetland. The new 132kV Substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of subsea cable between Shetland and the HVDC switching station in Caithness. (SHET-RI-053) | 30/11/2028
|  | CS-06456 | BEAW FIELD SHETLAND LIMITED | Beaw Field 132/33kV Substation | SHET-RI-116 | Kergord - Yell 132kV Connection - on Shetland install a new 132kV single circuit between the Kergord 132kV substation (established as part of SHET-RI-053) and a new tee point on Yell, to enable the connection of renewable generation. (SHET-RI-116) | 30/11/2028
|  | CS-06459 | BEAW FIELD SHETLAND LIMITED | Beaw Field 132/33kV Substation | Beaw Field H1 | 1. Installation of a new 132kV circuit breaker (205) and line disconnector (203) connected within the South Yell Switching Station (constructed under TORI SHET-RI-116). 2. Installation of a line disconnector (103) at 132 kV Beaw Field Substation. 3. Establish approximately 1.1 km of 132 kV Underground Cable from the proposed South Yell Switching Station to the 132kV Beaw Field substation on the Isle of Yell. | 30/11/2028
Beinn Mheadhonach | PRO-001506 | CS-07043 | Wind Harvest Limited | Dunvegan GSP | Beinn Mheadhonach H1 Edinbane | Establish a new 132/33kV Edinbane Grid Supply Point, GSP Substation to be located in a building at Edinbane Collector Switching Station. | 16/04/2028
|  | CS-06484 | Wind Harvest Limited | Dunvegan GSP | SHET-RI-135 | 4. Broadford – Edinbane Reinforcement (SHET-RI-135) | 16/04/2028
|  | CS-06485 | Wind Harvest Limited | Dunvegan GSP | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 16/04/2028
|  | CS-06486 | Wind Harvest Limited | Dunvegan GSP | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 16/04/2028
|  | CS-06487 | Wind Harvest Limited | Dunvegan GSP | Beinn Mheadhonach H1 | Install a new 132kV double busbar GIS feeder bay at the new 132kV Edinbane switching station, complete with 132kV busbar selector disconnectors, 132kV line circuit breaker and 132kV line disconnector. Install a new 132/33kV 120MVA rated Transformer unit to be located within the proposed Edinbane GSP Substation building. Install a 33kV transformer metering circuit breaker and transformer isolator within a new 33kV switch room to be located within the substation building. | 16/04/2028
Beinn Pumped Hydro Storage | PRO-001935 | CS-07400 | STATERA ENERGY LIMITED | Fasnakyle GSP | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 31/10/2029
|  | CS-07401 | STATERA ENERGY LIMITED | Fasnakyle GSP | SPT-RI-1560 | It is proposed to uprate the existing Denny-Braco West 275kV circuit to 400kV operation by transferring the circuit from its current bay in Denny 275kV substation to a new bay in Denny 400kV substation. | 31/10/2029
|  | CS-07402 | STATERA ENERGY LIMITED | Fasnakyle GSP | Beinn PHS H1 Works | 0 | 31/10/2029
Beinn Tharsuinn Extension | PRO-001035 | CS-05481 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn Tharsuinn Extension 132/33kV Substation | Beinn Tharsuinn Extension H1 Works | The sole use enabling works will include the installation of a 132kV circuit switcher (115) on the 132kV side of the 132/33kV transformer at the wind farm site. The circuit switcher (115) will connect to the incoming 132kV circuit constructed (with a minimum pre-fault summer rating of 120MVA) from Fyrish 275/132kV substation. The 132kV circuit will be connected to Fyrish 275/132kV substation via a spare 132kV bay comprising 132kV line disconnector (903), 132kV feeder circuit (905) breaker and a 132kV double busbar disconnectors (904/906). | 31/10/2029
|  | CS-05482 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn Tharsuinn Extension 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2029
Bellrock Offshore Wind Farm | PRO-001496 | CS-06696 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation | Lyra Item 1 | 1. Install 400kV plant and apparatus at Cousland 400kV Substation which will form the connection to the Lyra Offshore Transmission Interface Point, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers. | 31/10/2033
|  | CS-06697 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation | SPT-RI-1791 | Cockenzie to Eccles (ZA route) Uprating. - The project will uprate the 400kV double circuit between Cockenzie 400kV substation and Eccles 400kV substation from twin Totara to triple Totara operating at 90℃. | 31/10/2033
|  | CS-06698 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 31/10/2033
|  | CS-06699 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 31/10/2033
|  | CS-06700 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 31/10/2033
|  | CS-06701 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 31/10/2033
|  | CS-06702 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation | SPT-RI-1795 | This project will construct a new 400kV double circuit over the boundary from the South East of Scotland and the North West of England | 31/10/2033
|  | CS-06703 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation | SPT-RI-1796 | Cousland 400kV GIS Substation - A new 400kV double busbar substation, utilising Gas Insulated Switchgear (GIS), will be established south of Cockenzie in the Cousland area in the vicinity of the Torness/Fallago to Smeaton/Wishaw 400kV double circuit (ZS route) and Cockenzie to Eccles 400kV double circuit (ZA Route) crossing. Both the ZA and the ZS routes will be turned into the new substation. | 31/10/2033
|  | CS-06704 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation | SPT-RI-1873 | Second East Coast HVDC Link - Installation of a 2 GW HVDC subsea link between the East Lothian area in South East Scotland, and the South Humber area in North East England | 31/10/2033
|  | CS-06705 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation | SPT-RI-267 | Eccles 400kV Shunt Compensation - In order maintain to post-fault voltages within statutory limits, the installation of voltage control in the east of the network is required. As such, dynamic shunt compensation will be installed at Eccles 400kV substation with associated switchgear. | 31/10/2033
Benbrack Wind Farm | PRO-000032 | CS-06409 | Benbrack Wind Farm Limited | Benbrack Wind Farm 132/33kV Substation | Benbrack H1 Enabling Works | 1. Install a 132kV line disconnector at Benbrack substation. 2. Install a ~2km 132kV overhead line (Poplar 124MVA) to a tee on the New Cumnock – Blackcraig 132kV circuit. | 30/01/2025
|  | CS-06410 | Benbrack Wind Farm Limited | Benbrack Wind Farm 132/33kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 30/01/2025
|  | CS-06411 | Benbrack Wind Farm Limited | Benbrack Wind Farm 132/33kV Substation | SPT-RI-111 | The Kendoon to Maybole T 132kV single circuit will be reconfigured to form two new circuits, a circuit from Kendoon to New Cumnock, and a circuit from New Cumnock to Margree windfarm substation. | 30/01/2025
|  | CS-06412 | Benbrack Wind Farm Limited | Benbrack Wind Farm 132/33kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/01/2025
|  | CS-06413 | Benbrack Wind Farm Limited | Benbrack Wind Farm 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/01/2025
|  | CS-06414 | Benbrack Wind Farm Limited | Benbrack Wind Farm 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/01/2025
Bendle Farm | PRO-002243 | CS-09829 | Balance Power Ltd | Gretna 400kV Substation | SPT-RI-231 OHL | 0 | 31/10/2031
|  | CS-09827 | Balance Power Ltd | Gretna 400kV Substation | Bendle Farm H1 OHL | 0 | 31/10/2031
|  | CS-09826 | Balance Power Ltd | Gretna 400kV Substation | Bendle FarmA1 SS | 0 | 31/10/2031
|  | CS-09830 | Balance Power Ltd | Gretna 400kV Substation | SPT-RI-2320 OHL | 0 | 31/10/2031
|  | CS-09828 | Balance Power Ltd | Gretna 400kV Substation | Bendle Farm H1 SS | 0 | 31/10/2031
|  | CS-09831 | Balance Power Ltd | Gretna 400kV Substation | SPT-RI-2320 SS | 0 | 31/10/2031
Bendsmoor BESS | PRO-003582 | CS-09638 | GPC Battery Ltd | Gretna 400kV Substation | SPT-RI-231 | 0 | 30/06/2032
Ben Sca | PRO-000907 | CS-03799 | BEN SCA WIND FARM LIMITED | Edinbane GSP | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 31/10/2026
|  | CS-03800 | BEN SCA WIND FARM LIMITED | Edinbane GSP | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 31/10/2026
|  | CS-04194 | BEN SCA WIND FARM LIMITED | Edinbane GSP | Ben Sca Item 1 | A new 132kV busbar will be created under TORI 61 and two new 132kV Circuit Switcher Bays (115 and 215) will be created to connect to this infrastructure. This will include the associated protection and control infrastructure. | 31/10/2026
|  | CS-04195 | BEN SCA WIND FARM LIMITED | Edinbane GSP | Ben Sca Item 2 | Replace the existing 33kV Transformer Circuit Breaker (1T0) located within Dunvegan 132/33kV GSP substation compound with the equivalent new equipment rated to a minimum of 1250A. | 31/10/2026
|  | CS-04196 | BEN SCA WIND FARM LIMITED | Edinbane GSP | Ben Sca Item 3 | Install an additional 60MVA 132/33kV transformer, a 33kV transformer Circuit Breaker (2T0) within Dunvegan 132/33kV substation, on suitable plinths; along with their associated cabling/metering/protection equipment. The circuit breakers (1T0 and 2T0) will be owned and operated by Relevant Transmission Licensee and will represent the commercial boundary between Relevant Transmission Licensee and the User. | 31/10/2026
Berkswell (Tertiary) | PRO-000516 | CS-04811 | ENSO GREEN HOLDINGS LIMITED | Berkswell 275kV Substation | 100953-201900 | 1. Install earthing transformer on 13kV tertiary connection 2. Install 13kV Cable from 13kV tertiary connection to the 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets for Users connection | 31/10/2025
Berkswell Energy Storage | PRO-001788 | CS-05313 | Penso Power Limited | Berkswell 275kV Substation | 101395-202733 | 1. At Berkswell 275KV site, Mesh corner 4 extension to facilitate the transmission works 2. Installation of 275KV disconnector. | 31/10/2026
Berwick Bank Offshore Wind Farm A | PRO-002627 | CS-08403 | BERWICK BANK A LIMITED | Berwick Bank A 275/66kV Offshore Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 27/11/2027
|  | CS-08401 | BERWICK BANK A LIMITED | Berwick Bank A 275/66kV Offshore Substation | Berwick Bank A H1 SS Works | Installation of two 400kV Gas Insulated Switchgear (GIS) bays, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers which will form the transmission interface points for the Berwick Bank “A” Offshore Wind Farm connection (Interfaces A1 and A2). Completion of all associated protection and control works Provision of communications, alarms and indications, as described in Appendix F and Appendix OF of the Bilateral Connection Agreement. All associated miscellaneous and minor works, including provision of Category 2 Intertripping Scheme and Category 4 Intertripping Scheme, as defined in the Grid Code. | 27/11/2027
|  | CS-08402 | BERWICK BANK A LIMITED | Berwick Bank A 275/66kV Offshore Substation | SPT-RI-124 | 400kV GIS substation in Torness Area - A new 23 Bay double busbar 400kV GIS substation will be installed at a site yet to be determined in the Torness Area of East Lothian. This new substation is currently named as “Branxton 400kV Substation”. (SPT-RI-124 | 27/11/2027
Berwick Bank Offshore Wind Farm B | PRO-002628 | CS-08404 | Berwick Bank B Limited | Berwick Bank B 275/66kV Offshore Substation | Berwick Bank B H1 SS Works | Installation of two 400kV Gas Insulated Switchgear (GIS) bays , including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers which will form the transmission interface points for the Berwick Bank “B” Offshore Wind Farm connection (Interfaces B1 and B2) Completion of all associated protection and control works Provision of communications, alarms and indications, as described in Appendix F and Appendix OF of the Bilateral Connection Agreement All associated miscellaneous and minor works, including provision of Category 2 Intertripping Scheme and Category 4 Intertripping Scheme, as defined in the Grid Code. | 27/11/2027
|  | CS-08407 | Berwick Bank B Limited | Berwick Bank B 275/66kV Offshore Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 27/11/2027
|  | CS-08406 | Berwick Bank B Limited | Berwick Bank B 275/66kV Offshore Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 27/11/2027
Berwick Bank Offshore Wind Farm C | PRO-000513 | CS-07077 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101370-202690 | At Blyth 400kV / 275kV substation: Install 2 new 1100MVA rated interbus transformers. | 30/11/2029
|  | CS-07078 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 30/11/2029
|  | CS-07079 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101539-203052 | At Tynemouth 275kV substation: Replace the line disconnectors, busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus (101539-203052) | 30/11/2029
|  | CS-07080 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 100927-201853 | 1. At Blyth 400kV Substation: Extend Main and Reserve bar section to accommodate a user bay, install 2 new section breakers in both Main and Reserve busbar and install a generator intertripping scheme. (100927-201853) | 30/11/2029
|  | CS-07081 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 100058-200133 | Tee in the Hartlepool - West Boldon circuit into Hawthorn Pit 275kV Substation (NOA WHTI) | 30/11/2029
|  | CS-07082 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101369-202689 | Reconductor the Blyth legs of the Blyth – Eccles – Stella West 1 and Blyth – Eccles – Stella West 2 circuits with GAP conductor and replace the cable sections of both circuits. | 30/11/2029
|  | CS-07083 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101385-202714 | At Blyth 275kV substation: Replace busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. | 30/11/2029
|  | CS-07084 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 30/11/2029
|  | CS-07085 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a post-fault winter rating of 3100MVA | 30/11/2029
|  | CS-07086 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101553-203094 | Turn in the Cottam-Staythorpe 400KV circuit at High Marnham 400KV | 30/11/2029
|  | CS-07087 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 030317-030317 | Rebuild the existing Hawthorn Pit 400kV compound as a full double busbar substation. Uprate the existing Hawthorn Pit - Norton 275kV to a 400kV circuit. (NOA E2DC) | 30/11/2029
|  | CS-07088 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101385-202713 | Reconductor the Blyth – Stella West 275kV circuits with 1x525mm2 Curlew conductor (101385- 202713) | 30/11/2029
|  | CS-07089 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101539-203053 | At South Shields 275kV substation: Replace the, line disconnectors, busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus (101539-203053) | 30/11/2029
|  | CS-07090 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101539-203054 | At West Boldon 275kV substation: Replace the line disconnectors, busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. (101539-203054) | 30/11/2029
|  | CS-07091 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101539-203055 | At Offerton 275kV substation: Replace the, line disconnectors, busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus (101539-203055) | 30/11/2029
|  | CS-07092 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101386-202715 | Reconductor the 2x700mm2 sections of the Lackenby-Thornton 1+2 circuit with 2x850mm2 conductor. Reconductor the 4x400mm2 sections with 2x850mm2 conductor. Uprate the cable section of this circuit. (2850MVA). | 30/11/2029
|  | CS-07093 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 020669-020669 | Lackenby – Norton 1 circuit reconductor the 2x570mm2 sections with 2x620mm2 GZTACSR conductor. Replace the cable section of the circuit. | 30/11/2029
|  | CS-07094 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101540-203056 | Reconductor the Blyth – Tynemouth 275kV circuit with 1x525mm2 Curlew conductor (101540- 203056) | 30/11/2029
|  | CS-07095 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101540-203057 | Reconductor the Blyth – South Shields - Tynemouth 275kV circuits with 1x525mm2 Curlew conductor (101540-203057) | 30/11/2029
|  | CS-07096 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101540-203058 | Reconductor the Tynemouth – West Boldon 275kV circuit with 1x525mm2 Curlew conductor (101540-203058) | 30/11/2029
|  | CS-07097 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101540-203059 | Reconductor the South Shields – West Boldon 275kV circuit with 1x525mm2 Curlew conductor. | 30/11/2029
|  | CS-07098 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101430-202806 | Reconductor the Offerton - West Boldon 275kV circuit with 1x525mm2 Curlew conductor (101430- 202806) | 30/11/2029
|  | CS-07099 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 033463-033463 | Uprate the Norton - Osbaldwick 1 OHL circuit to achieve at least a post-fault Winter rating of 2550MVA. | 30/11/2029
|  | CS-07100 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101430-202807 | Reconductor the Hawthorn Pit – Offerton circuit with 1x525mm2 Curlew conductor (101430- 202807) | 30/11/2029
|  | CS-07101 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101430-202808 | Reconductor the Hawthorn Pit – West Boldon circuit with 1x525mm2 Curlew conductor (101430- 202808) | 30/11/2029
|  | CS-07102 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101373-202693 | Reconductor the 2x400mm2 section of the Hartlepool – Hawthorn Pit circuit with 2x570 mm2 conductor (101373-202693) | 30/11/2029
|  | CS-07103 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 033703-033703 | Reconductor Harker - Fourstones - Stella West circuits with 1x525mm2 Curlew conductor (033703-033703) | 30/11/2029
|  | CS-07104 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 30/11/2029
|  | CS-07105 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101325-202642 | At Thornton 400kV: Establish an additional section switch in place of X224 or X228 and add another section switch in place of X428 or X424. Replace circuit breaker X405 and X805 (In Lackenby - Thornton circuits with 63kA rated breakers. (101325-202642) | 30/11/2029
|  | CS-07106 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 100110-200299 | Install three new 225MVAr MSCs at Norton, Osbaldwick and Stella West 400kV substations. (NOA NEMS). | 30/11/2029
|  | CS-07107 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 30/11/2029
|  | CS-07108 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 30/11/2029
|  | CS-07109 | BERWICK BANK C LIMITED | Blyth 400kV Substation | Berwick Bank Offshore Wind Farm C H1 Enabling Works | Reconfiguration and/ or replacement of Main Protections at Eccles 400kV Substation on the Eccles – Stella West/ Blyth 400kV circuits. • The final scope of protection and control works will be subject to detailed engineering design and studies, the scope of which shall include ‘hardware-in-the-loop’ transient testing, to be performed by real time simulation using relays provided by the Relevant Transmission Licensees, and with a suitable and sufficient representation of the OTSDUW User’s DC Converters and system, their controls, reactive compensation and filter equipment to be provided by the OTSDUW User. | 30/11/2029
|  | CS-07110 | BERWICK BANK C LIMITED | Blyth 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 30/11/2029
|  | CS-07111 | BERWICK BANK C LIMITED | Blyth 400kV Substation | Berwick Bank Offshore Wind Farm C H1 Enabling Works | Modification of Series Compensation Equipment at Eccles 400kV Substation on the Eccles – Stella West/ Blyth 400kV circuits as required. • The final scope of series compensation related works will be subject to a detailed engineering design and studies to be completed by the Series Compensation Equipment original equipment manufacturer | 30/11/2029
BESS Cilfynydd | PRO-002008 | CS-07950 | CSWE 2 LIMITED | Cilfynydd 400kV Substation | 101841-203779 | Double Busbar extension Cilfynydd 400kV Substation to provide space for the User’s generation bay. | 12/07/2029
|  | CS-07951 | CSWE 2 LIMITED | Cilfynydd 400kV Substation | 020903-020903 | Uprating of the Cowley – Walham / Cowley – Minety 400kV circuit cables to achieve 1700MVA post-fault summer rating | 12/07/2029
|  | CS-07952 | CSWE 2 LIMITED | Cilfynydd 400kV Substation | 100424-200970 | Reconductor the Bramley – Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve at least a 2600MVA pre-fault summer rating / 2700MVA post-fault summer rating | 12/07/2029
BESS Harker | PRO-002010 | CS-07771 | CSWE 4 LIMITED | Harker 400kV Substation | 101268-202511 | The scope of this project is the rebuild of Harker substation and rationalisation to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. | 30/05/2031
|  | CS-07770 | CSWE 4 LIMITED | Harker 400kV Substation | 101843-203780 | Provision of spare 400kV GIS bay in the new build substation inclusive of required Protection and Control to form a compliant connection. | 30/05/2031
BESS North Farm | PRO-002060 | CS-08961 | CSWE 5 LIMITED | Chickerell 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 01/11/2031
|  | CS-08956 | CSWE 5 LIMITED | Chickerell 400kV Substation | 101894-203881 | Extend the Busbar at Chickerell 400kV to make provision for the User to connect their generator bay | 01/11/2031
|  | CS-08964 | CSWE 5 LIMITED | Chickerell 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 &amp; 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 01/11/2031
|  | CS-08958 | CSWE 5 LIMITED | Chickerell 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to triple Auriacuria 3 x 700mm2 at 90 degrees to achieve a summer pre-fault rating of 3000MVA | 01/11/2031
|  | CS-08965 | CSWE 5 LIMITED | Chickerell 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 2680MVA | 01/11/2031
|  | CS-08969 | CSWE 5 LIMITED | Chickerell 400kV Substation | 101894-203888 | Extension of the Melksham OTS for this connection. | 01/11/2031
|  | CS-08959 | CSWE 5 LIMITED | Chickerell 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 01/11/2031
|  | CS-08968 | CSWE 5 LIMITED | Chickerell 400kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault summer rating of 2680MVA | 01/11/2031
|  | CS-08957 | CSWE 5 LIMITED | Chickerell 400kV Substation | 101485-202932 | Installation of new circuit breaker to control MSC2 to maintain the substation operability | 01/11/2031
|  | CS-08960 | CSWE 5 LIMITED | Chickerell 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 01/11/2031
BESS Swan | PRO-002009 | CS-08374 | CSWE 3 LIMITED | Swansea North 400kV Substation | 101841-203778 | Installation of a new commercial Operational Tripping Scheme (via extension of the existing Pembroke OTS) | 31/10/2028
|  | CS-08373 | CSWE 3 LIMITED | Swansea North 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to achieve 2300MVA pre-fault summer rating | 31/10/2028
|  | CS-08372 | CSWE 3 LIMITED | Swansea North 400kV Substation | 020903-020903 | Uprating of the Cowley – Walham / Cowley – Minety 400kV circuit cables to achieve 1700MVA post-fault summer rating | 31/10/2028
|  | CS-08371 | CSWE 3 LIMITED | Swansea North 400kV Substation | 101836-203768 | Extension of 400kV busbar at Swansea North 400kV Substation for provision of one generator bay | 31/10/2028
Bettyhill Phase 2 Wind Farm | PRO-002001 | CS-08463 | Bettyhill 2 Wind Ltd | Bettyhill 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 01/11/2027
|  | CS-08462 | Bettyhill 2 Wind Ltd | Bettyhill 132/33kV Substation | SHET-RI-058 - Bettyhill 2 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement*- This project is to reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe (Cambusmore) 132kV double circuit with a higher capacity 275kV double circuit OHL The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 01/11/2027
Bhlaraidh Extension Wind Farm | PRO-000383 | CS-05483 | SSE GENERATION LIMITED | Bhlaraidh 132/33kV Substation | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 01/04/2026
|  | CS-05484 | SSE GENERATION LIMITED | Bhlaraidh 132/33kV Substation | Bhlaraidh Extension Enabling | Construct a single circuit 132kV overhead trident line from the 132kV busbar, with a 132kV Circuit Switcher, at the Bhlaraidh Extension Windfarm Substation compound, for a distance of approximately 20 km, to within around 0.5km of the Fort Augustus 400/132kV Substation. The remaining 0.5km distance, to a termination at a new bay on the new 132kV double busbar at the Fort Augustus 400/132kV Substation, should be covered by underground 132kV cable; subject to obtaining the necessary wayleave and consent approvals. The 132kV line/cable will be built using conductors sufficiently rated to accommodate the Bhlaraidh Extension Windfarm | 01/04/2026
Bicker Drove | PRO-003874 | CS-08991 | CSWE 1 LIMITED | Navenby 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 30/05/2034
|  | CS-08994 | CSWE 1 LIMITED | Navenby 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 30/05/2034
|  | CS-08987 | CSWE 1 LIMITED | Navenby 400kV Substation | 101687-203363 | Establish a double turn in connection between the new 400kV substation and the West Burton – Bicker Fen 400kV circuit 1 and 2 | 30/05/2034
|  | CS-09006 | CSWE 1 LIMITED | Navenby 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post fault winter rating of 3420MVA | 30/05/2034
|  | CS-09002 | CSWE 1 LIMITED | Navenby 400kV Substation | 101663-203316 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pulling mode capable of injecting up to -8 ohms along the Bicker Fen – West Burton 1 (A685) 400kV circuit | 30/05/2034
|  | CS-08996 | CSWE 1 LIMITED | Navenby 400kV Substation | 100459-201024 | Reconductor the 2x500mm2 section of the High Marnham – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 30/05/2034
|  | CS-09004 | CSWE 1 LIMITED | Navenby 400kV Substation | 102056-204226 | At West Burton 400kV: 1. Replace CB X220 and X705 to 63kA nominal rating. 2. Replace CB X120 and X320 to 63kA nominal rating with higher X/R derating and higher CB rating. | 30/05/2034
|  | CS-09005 | CSWE 1 LIMITED | Navenby 400kV Substation | 101807-203697 | New EDN2 Chesterfield – Ratcliffe-on-Soar 400kV double circuit | 30/05/2034
|  | CS-08998 | CSWE 1 LIMITED | Navenby 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 30/05/2034
|  | CS-08986 | CSWE 1 LIMITED | Navenby 400kV Substation | 101687-203362 | Build a new Navenby 400kV Double Busbar Substation with 4 Feeder bays, and 1 Coupler Bay in the vicinity of tower 4ZM508. | 30/05/2034
|  | CS-09001 | CSWE 1 LIMITED | Navenby 400kV Substation | 100798-201612 | At Cottam 400kV Substation: Uprate feeder bay disconnector and circuit breaker on the Cottam - West Burton circuit to provide a post fault summer rating of 3060MVA | 30/05/2034
|  | CS-08997 | CSWE 1 LIMITED | Navenby 400kV Substation | 100590-201212 | Reconductor the 2x500mm2 sections of the Ratcliffe – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 30/05/2034
|  | CS-08989 | CSWE 1 LIMITED | Navenby 400kV Substation | 100944-201181 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 30/05/2034
|  | CS-09000 | CSWE 1 LIMITED | Navenby 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 30/05/2034
|  | CS-09003 | CSWE 1 LIMITED | Navenby 400kV Substation | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. New Circuit Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 30/05/2034
|  | CS-08995 | CSWE 1 LIMITED | Navenby 400kV Substation | 100451-201016 | Reconductor the 2x500mm2 sections of the High Marnham – West Burton 400kV circuit with 2x570mm2 conductor and replace the cable section. | 30/05/2034
|  | CS-08990 | CSWE 1 LIMITED | Navenby 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 30/05/2034
|  | CS-08992 | CSWE 1 LIMITED | Navenby 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 30/05/2034
|  | CS-08993 | CSWE 1 LIMITED | Navenby 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 30/05/2034
|  | CS-09007 | CSWE 1 LIMITED | Navenby 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 30/05/2034
|  | CS-08999 | CSWE 1 LIMITED | Navenby 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 30/05/2034
|  | CS-08988 | CSWE 1 LIMITED | Navenby 400kV Substation | 102433-204962 | Extension of the newly built Navenby 400kV substation busbars to accommodate the User’s bay | 30/05/2034
|  | CS-09008 | CSWE 1 LIMITED | Navenby 400kV Substation | 100450-201015 | Uprate the Cottam - Keadby 1 and 2 circuits to achieve a post fault winter rating of 3400MVA | 30/05/2034
Bicker Fen | PRO-001984 | CS-07233 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 101716-203424 | 1. Extend Bicker Fenn 400kV substation including 2 Section Breakers Main and Reserve, 1 coupler bay, feeder bay and make provision for the connection of the User’s generation bay. 2. Transpose West Burton Circuit 1 to newly built substation section | 01/06/2029
|  | CS-07234 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 101651-203292 | 1. Establishment of a new bay on the 400kV bars, including Busbar protection. | 01/06/2029
|  | CS-07235 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 01/06/2029
|  | CS-07236 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 01/06/2029
|  | CS-07237 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 01/06/2029
|  | CS-07238 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 01/06/2029
|  | CS-07239 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 01/06/2029
|  | CS-07240 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 01/06/2029
|  | CS-07241 | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 01/06/2029
Bicker Fen 1 Solar | PRO-001034 | CS-08356 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100892-201790 | 1. Installation of tertiary bushings on the 13kV side of SGT2 at the Connection Site.. 2. Installation of earthing transformer at the Connection Site 3. Installation of 13kV Disconnector at the Connection Site. 4. Installation of 13kV busbar to 13kV circuit breaker at the Connection Site. 5. Works at the Connection Site to facilitate Category 2 Operational Tripping Scheme (Extension of East Anglia OTS scheme) as described in Appendix F3 of Bilateral Connection Agreement. | 30/05/2025
|  | CS-08363 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100451-201016 | Reconductor the 2x500mm2 sections of the High Marnham – West Burton 400kV circuit with 2x570mm2 conductor and replace the cable section. | 30/05/2025
|  | CS-04812 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100891-201788 | 1. Extension of Bicker Fen 400kV substation. 2. Installation of tertiary cable box on the 13kV side of SGT1 at the Connection Site. 3. Installation of 13kV cable at the Connection Site. 4. installation of earthing transformer at the Connection Site. 5. Installation of 13kV Disconnector at the Connection Site. 6. Works at the Connection Site to facilitate Category 2 Operational Tripping Scheme (Extension of East Anglia OTS scheme) as described in TOF3. | 30/05/2025
|  | CS-08359 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 30/05/2025
|  | CS-08360 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 30/05/2025
|  | CS-08369 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 30/05/2025
|  | CS-08364 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100459-201024 | Reconductor the 2x500mm2 section of the High Marnham – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 30/05/2025
|  | CS-08367 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 30/05/2025
|  | CS-08368 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 30/05/2025
|  | CS-08357 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 30/05/2025
|  | CS-08358 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 30/05/2025
|  | CS-08366 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 30/05/2025
|  | CS-08361 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 30/05/2025
|  | CS-08362 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 30/05/2025
|  | CS-08365 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100590-201212 | Reconductor the 2x500mm2 sections of the Ratcliffe – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 30/05/2025
|  | CS-08370 | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 100798-201612 | At Cottam 400kV Substation: Uprate feeder bay disconnector and circuit breaker on the Cottam - West Burton circuit to provide a post fault summer rating of 3060MVA | 30/05/2025
Bicker Fen 2 Solar | PRO-001046 | CS-05297 | AGR SOLAR 3 LIMITED | Bicker Fen 400kV Substation | 100892-201790 | 1. Extension of Bicker Fen 400kV substation. 2. Installation of tertiary cable box on the 13kV side of SGT1 at the Connection Site. 3. Installation of 13kV cable at the Connection Site. 4. Installation of earthing transformer at the Connection Site. 5. Installation of 13kV Disconnector at the Connection Site. | 30/09/2025
Bilbo Farm | PRO-001301 | CS-09607 | LEL BILBO SOLAR LIMITED | Strichen GSP | SHET-RI-188 | St Fergus to New Deer 2 132kV Reinforcement – At New Deer 2 400kV Substation, establish a new 132kV busbar at New Deer 2 substation and install 2x240MVA 400/132kV transformers. Construct a new 132kV double circuit overhead line from New Deer 2 to St Fergus substation (Approx. 26 km). | 31/10/2024
|  | CS-09606 | LEL BILBO SOLAR LIMITED | Strichen GSP | SHET-RI-187 | St Fergus 132kV Substation- Establish a new 132kV St Fergus double busbar substation at the site of the existing St Fergus 132kV Switching Station. Split the double busbars and establish an open point between them. | 31/10/2024
|  | CS-09608 | LEL BILBO SOLAR LIMITED | Strichen GSP | SHET-RI-189 | Strichen-Fraserburgh to St Fergus 132kV OHL Reconductoring - Upgrade a section of the existing Strichen/Fraserburgh to St Fergus Switching Station 132kV SF1/SF2 OHL double circuit (approx. 6.2km) to have a minimum summer pre-fault rating of 231MVA. | 31/10/2024
Binn Wind Generating Station | PRO-000594 | CS-04258 | Scottish Hydro Electric Power Distribution Plc | Abernethy GSP | SHET-RI-111 (Abernethy Mesh Corner) | Development of the 132kV Abernethy Mesh Corner - At Abernethy 132/33kV substation, install a four circuit breaker mesh corner. This will be connected to the existing Burghmuir – Charleston 132kV double circuit overhead line. | 31/08/2022
Blackhillock Battery | PRO-001970 | CS-07336 | BLACKHILLOCK FLEXPOWER LTD | Blackhillock 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2026
|  | CS-07337 | BLACKHILLOCK FLEXPOWER LTD | Blackhillock 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2026
Blacklaw | PRO-000036 | CS-06706 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Blacklaw Wind Farm Substation | Blacklaw - H1 Works | Install a new 400kV gas insulated switchgear (GIS) double busbar bay at Wishaw substation. Install a 400kV cable circuit (approx. 700m) between the new GIS switchbay and the location of the new 400/132kV supergrid transformer. Install a new 400kV transformer disconnector. Install a new 400/132kV 360MVA transformer. Civil works to extend the existing Wishaw substation compound. Install a new 132kV circuit breaker at Wishaw substation. Install a new 132kV cable/OHL circuit between Wishaw and Blacklaw WF substation. Install two new 132kV line disconnectors at Blacklaw WF substation | 15/06/2029
Blackpark Battery Storage | PRO-000935 | CS-06686 | BLACKPARK ENERGY STORAGE LIMITED | Nairn GSP | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 31/12/2022
Blaen y Glyn | PRO-001589 | CS-04813 | BANC DU ENERGY PARK LIMITED | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 04/02/2027
|  | CS-04814 | BANC DU ENERGY PARK LIMITED | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 04/02/2027
|  | CS-04815 | BANC DU ENERGY PARK LIMITED | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 04/02/2027
|  | CS-04816 | BANC DU ENERGY PARK LIMITED | Chirk GSP | 131323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 04/02/2027
|  | CS-04817 | BANC DU ENERGY PARK LIMITED | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 04/02/2027
Blairgowrie BESS | PRO-003482 | CS-09422 | BLAIRGOWRIE BESS LTD | Coupar Angus GSP | 132kV Disconnector | Additionally, the installation of a new 132kV disconnector switch at Blairgowrie BESS 132kV substation will also be required | 30/05/2030
|  | CS-09424 | BLAIRGOWRIE BESS LTD | Coupar Angus GSP | SHET-RI-237 | Coupar Angus - Clunie 132kV Works - Establish a new 132kV single busbar nearby to the Coupar Angus area. The proposed location for this busbar compound will be next to or underneath the crossing point of the 132kV CCN/CCS circuits and the 275kV YZ1/YZ2 circuits (YZ1/YZ2 proposed to switch to 400kV under SHET-RI-093). For this new 132kV single busbar, 4x new 132kV bays will be required to connect the existing 132kV CCN/CCS circuits as seen from the SLD. A bus section has also been proposed on the busbar. | 30/05/2030
|  | CS-09421 | BLAIRGOWRIE BESS LTD | Coupar Angus GSP | 132kV Cable - Blairgowrie | Approximately 2km of 132kV cable will be required as part of this connection. | 30/05/2030
|  | CS-09423 | BLAIRGOWRIE BESS LTD | Coupar Angus GSP | SHET-RI-090 | Errochty – Clunie 132kV Reconductoring – Reconductor approximately 15.4km of the existing 132kV double circuit OHL between Errochty and Clunie substations. This double circuit is to be reconductored with UPAS conductor (1 x 300mm2) and will operate at 75 C to give a minimum summer pre-fault rating of 176MVA | 30/05/2030
|  | CS-09420 | BLAIRGOWRIE BESS LTD | Coupar Angus GSP | 132kV Feeder Bay - Blairgowrie BESS | Installation of a new 132kV feeder bay and any associated protection equipment at a new 132kV busbar site (as seen within SHET-RI-237) | 30/05/2030
Blankney Solar | PRO-001850 | CS-07069 | ACRE LANE ENERGYFARM LIMITED | Navenby 400kV Substation | 101687-203362 | Build a new Navenby 400kV Double Busbar Substation with 1 generator skeleton bay, 4 Feeder bays, and 1 Coupler Bay. | 01/04/2028
|  | CS-07070 | ACRE LANE ENERGYFARM LIMITED | Navenby 400kV Substation | 101687-203363 | Establish a double turn in connection between the new 400kV substation and the West Burton – Bicker Fen 400kV circuit 1 and 2 | 01/04/2028
|  | CS-07071 | ACRE LANE ENERGYFARM LIMITED | Navenby 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 01/04/2028
|  | CS-07072 | ACRE LANE ENERGYFARM LIMITED | Navenby 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 01/04/2028
|  | CS-07073 | ACRE LANE ENERGYFARM LIMITED | Navenby 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 01/04/2028
|  | CS-07074 | ACRE LANE ENERGYFARM LIMITED | Navenby 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 01/04/2028
|  | CS-07075 | ACRE LANE ENERGYFARM LIMITED | Navenby 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 01/04/2028
|  | CS-07076 | ACRE LANE ENERGYFARM LIMITED | Navenby 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 01/04/2028
Blarghour Wind | PRO-000398 | CS-06188 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2027
|  | CS-06189 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 31/10/2027
|  | CS-06190 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2027
|  | CS-06191 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2027
|  | CS-06192 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | SHET-RI-028 Thurso to Gills Bay | Gills Bay – Thurso South 132kV Double Circuit - It is proposed to construct a new 132kV GIS double busbar arrangement substation at a suitable location around Gills Bay (west of John O’Groats) and connect in two OHL radial circuits from Thurso south. (SHET-RI-028). | 31/10/2027
|  | CS-06193 | BLARGHOUR WIND FARM LIMITED | Blarghour Substation | Blarghour H1 works | H1 132kV AIS Switchgear | 31/10/2027
BLINDWELLS FARM BESS | PRO-002534 | CS-08793 | OPDE UK LIMITED | Arbroath GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 30/06/2032
|  | CS-08794 | OPDE UK LIMITED | Arbroath GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 30/06/2032
BLUE PLANET SOLAR | PRO-001703 | CS-04632 | BLUE PLANET SOLAR LIMITED | Dungeness 400kV Substation | 101570-203142 | At Dungeness 400kV double busbar substation: Make provision for connection of generator bay (User Works) Local works to facilitate extension of Sellindge OTS. | 31/10/2029
Blyth BESS | PRO-002817 | CS-09276 | SSE RENEWABLES SOLAR & BATTERY HOLDINGS LIMITED | Blyth 275kV Substation | 102754-205557 | Bar extension and associated works to facilitate connection of Users generator bay. | 31/10/2036
|  | CS-09275 | SSE RENEWABLES SOLAR & BATTERY HOLDINGS LIMITED | Blyth 275kV Substation | 102377-204823 | Double Circuit Turn in of Blyth-Eccles-Stella West OHL and Construction of a new 400kV double busbar substation with 4 feeder circuits, bus section, bus couplers and associated works. | 31/10/2036
Bodelwyddan BESS and PV | PRO-001657 | CS-04693 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 101568-203131 | At Bodelwyddan 400kV substation extend the site to make provision for a new generator bay. | 31/10/2029
|  | CS-04694 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 100570-201374 | 2. Double turn-in of PENT-BODE-CONQ 1 & 2 circuits - PENT end of circuit 2 to utilise existing OHL between T and BODE s/s (GM line). New OHL to carry CONQ end of (PENT-BODECONQ) circuit 2 turn in, and circuit 1 T. Building of 2 new bays to accommodate additional circuits | 31/10/2029
|  | CS-04695 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 032281-202001 | 1. Extension of Bodelwyddan 400kV substation. | 31/10/2029
|  | CS-04818 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 101006-202010 | Uprating of the Bodewyddan - Connahs Quay circuits 1+2 to achieve a Summer Post Fault rating of 2650 MVA | 31/10/2029
|  | CS-04819 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 101007-202011 | Uprating of the single circuit between Pentir - Trawsfynydd to achieve a post fault summer ratings of 2375MVA | 31/10/2029
|  | CS-04820 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 100975-201954 | Convert the current 132kV circuit between Pentir - Trawsfynydd, up to 400kV refurbishing/replacing where necessary, creating Pentir - Traws 400kV circuit 2 | 31/10/2029
|  | CS-04821 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 101267-202510 | Scope- Circuits between Wylfa and Pentir will need a new or an existing modificed intertrip scheme to monitor all circuits to trip generation for N-3 events. In addition,all circuits between Pentir-Legacy via TRAWS and CONHQ to monitor all circuits as a result of new connections in the area | 31/10/2029
|  | CS-04822 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor triggered from R4 connection | 31/10/2029
|  | CS-04823 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve a rating of at least 2375MVA post fault summer rating | 31/10/2029
|  | CS-04824 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 31/10/2029
|  | CS-04825 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor. | 31/10/2029
|  | CS-04826 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 31/10/2029
|  | CS-04827 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 31/10/2029
|  | CS-04828 | IGP SOLAR 21 LIMITED | Bodelwyddan 400kV Substation | 101277-202523 | Smartwires in both the Trawsfynydd legs on the TRAWS-CONQ-LEGA circuits. This is required as we get overloads on the BODE-CONQ circuits which are in excess of the Summer post fault rating (even after the circuit have been reconductored). | 31/10/2029
Bodinglee Wind Farm | PRO-001985 | CS-07389 | Banks Renewables (Bodinglee Wind Farm) Limited | Bodinglee Wind Farm 132kV | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 30/04/2029
Bolney | PRO-001031 | CS-04829 | PIVOTED POWER LLP | Bolney 400kV Substation | 100247-201145 | 1. Site extension to facilitate the transmission works 2. Install a tertiary cable box or bushings on the SGT 3 3. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer 4. Install an earthing transformer 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets 6. Local works to facilitate the Category 2 with Sellindge Operational Tripping Scheme (OTS) as described in Appendix F3 | 31/10/2027
|  | CS-04830 | PIVOTED POWER LLP | Bolney 400kV Substation | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 31/10/2027
|  | CS-04831 | PIVOTED POWER LLP | Bolney 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 &amp; 2 Circuits to provide a post fault winter rating of 3140MVA. | 31/10/2027
|  | CS-04832 | PIVOTED POWER LLP | Bolney 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 &amp; 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 31/10/2027
Bolney (tertiary) | PRO-000380 | CS-04833 | BOLNEY GREEN LIMITED | Bolney 400kV Substation | 100585-201208 | 1. Site extension to facilitate the transmission works 2. Install a tertiary cable box or bushings on the SGT 4. 3. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer. 4. Install an earthing transformer. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 6. Local works to facilitate the Category 2 with Sellindge Operational Tripping Scheme (OTS) as described in Appendix F3. | 30/10/2024
|  | CS-04834 | BOLNEY GREEN LIMITED | Bolney 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 &amp; 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 30/10/2024
|  | CS-04835 | BOLNEY GREEN LIMITED | Bolney 400kV Substation | 31867 | 1. Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent | 30/10/2024
|  | CS-04836 | BOLNEY GREEN LIMITED | Bolney 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 &amp; 2 Circuits to provide a post fault winter rating of 3140MVA. | 30/10/2024
Bolney BESS | PRO-004026 | CS-09234 | CSE45 LIMITED | Bolney 400kV Substation | 102436-204965 | Replacement, or modification, of existing towers and associated OHL works to facilitate a single Tee-Point connection to a new 400kV substation via the Lovedean - Bolney overhead line circuit. • Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks, and associated infrastructure. • Construction of 400kV busbar to accommodate the OHL Tee-In connection and the Users Generator Bay. • Local works to facilitate the extension of the Melksham Operational Tripping Scheme. | 11/09/2037
|  | CS-09235 | CSE45 LIMITED | Bolney 400kV Substation | 102695-205389 | • Extension of the 400kV busbars at the new Substation for the User’s bay. • Extension of Sellindge OTS to include this Generator. | 11/09/2037
Boom Power Feckenham Generation Hub | PRO-002312 | CS-09069 | BOOM POWER LTD | Feckenham 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 31/10/2033
|  | CS-09071 | BOOM POWER LTD | Feckenham 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 31/10/2033
|  | CS-09067 | BOOM POWER LTD | Feckenham 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 31/10/2033
|  | CS-09064 | BOOM POWER LTD | Feckenham 400kV Substation | 102092-204283 | Install 400/66kV 180MVA SGT2 and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation | 31/10/2033
|  | CS-09065 | BOOM POWER LTD | Feckenham 400kV Substation | 102092-204285 | Install static VAR compensation system and associated switchgear including 400kV circuit breaker and 400/14kV transformer to Feckenham 400kV substation | 31/10/2033
|  | CS-09068 | BOOM POWER LTD | Feckenham 400kV Substation | 032021-032021 | econductor the existing 2 x 570mm2 conductor on the CellarheadDrakelow 1 and 2 400kV circuits with 2 x 620mm2 conductor to achieve a pre fault summer rating of 2490MVA | 31/10/2033
|  | CS-09070 | BOOM POWER LTD | Feckenham 400kV Substation | 020903-020903 | Uprating/replacement of the Cowley – Walham and Cowley - Minety 400kV circuits cables sections to achieve 1193MVA or greater prefault Summer rating. | 31/10/2033
|  | CS-09066 | BOOM POWER LTD | Feckenham 400kV Substation | 101880-203857 | Uprate the Ratcliffe 400kV to Willington East 400kV circuit #2 (RATS4- WILE4-2) to summer pre-fault rating 1680MVA | 31/10/2033
|  | CS-09063 | BOOM POWER LTD | Feckenham 400kV Substation | 102189-204410 | Extension of 400kV main and reserve busbar of Feckenham 400kV substation to accommodate the user’s bay | 31/10/2033
BOOM Power Llanbabo Generation | PRO-001540 | CS-04840 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 100975-201954 | Convert the current 132kV circuit between Pentir - Trawsfynydd, up to 400kV refurbishing/replacing where necessary, creating Pentir - Traws 400kV circuit 2 | 30/10/2026
|  | CS-04841 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve a rating of at least 2375MVA post fault summer rating | 30/10/2026
|  | CS-04842 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101267-202510 | Scope- Circuits between Wylfa and Pentir will need a new or an existing modificed intertrip scheme to monitor all circuits to trip generation for N-3 events. In addition,all circuits between Pentir-Legacy via TRAWS and CONHQ to monitor all circuits as a result of new connections in the area | 30/10/2026
|  | CS-04843 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/10/2026
|  | CS-04844 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 100974-201953 | Construct a second double circuit between Pentir 400kV substation and the Wylfa 400kV substation (circuits No. 3 & 4) | 30/10/2026
|  | CS-04845 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor. | 30/10/2026
|  | CS-04846 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor triggered from R4 connection | 30/10/2026
|  | CS-04847 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 30/10/2026
|  | CS-04848 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 30/10/2026
|  | CS-04849 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101277-202523 | Smartwires in both the Trawsfynydd legs on the TRAWS-CONQ-LEGA circuits. This is required as we get overloads on the BODE-CONQ circuits which are in excess of the Summer post fault rating (even after the circuit have been reconductored). | 30/10/2026
|  | CS-04837 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101555-203096 | 1. Utilise spare bay at Wylfa 400kV to make provision for the User to connect their generator bay | 30/10/2026
|  | CS-04838 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101006-202010 | Uprating of the Bodewyddan - Connahs Quay circuits 1+2 to achieve a Summer Post Fault rating of 2650 MVA | 30/10/2026
|  | CS-04839 | Carrog Storage Facility Limited | Wylfa 400kV Substation | 101007-202011 | Uprating of the single circuit between Pentir - Trawsfynydd to achieve a post fault summer ratings of 2375MVA | 30/10/2026
Botley West - Cote Solar Power Station | PRO-001587 | CS-04333 | SOLARFIVE LTD | Botley West 400kV Substation | 101420-202783 | 1. Build temporary overhead line to divert the Cowley – Walham circuit and replace suspension tower 4TE037 with a new terminal tower. 2. Construct a new four-bay double busbar Botley West 400kV substation adjacent to tower 4TE037, comprising of two feeder bays, a bus coupler and space for installation of one generator bay. 3. Turn in the new Botley West 400kV substation to the Transmission System, creating Cowley – BotleyWest –Walham circuit. (Substation name, design, and location subject to further engineering assessment during NGET option selection phase) | 30/10/2026
|  | CS-04334 | SOLARFIVE LTD | Botley West 400kV Substation | 020903-020903 | Uprating of the Cowley - Walham 400kV circuit cables to achieve 1500MVA post-fault summer rating. | 30/10/2026
|  | CS-04335 | SOLARFIVE LTD | Botley West 400kV Substation | 101420- 202784 | Uprate the Bramley – Didcot 400kV circuits; including overhead line and cable sections. | 30/10/2026
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | PRO-002091 | CS-07611 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-07612 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-07615 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-07620 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-07621 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-07613 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-07614 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-07617 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-07616 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-07623 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-07618 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-07619 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-07622 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-07624 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-07625 | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
Brackenhills Wind | PRO-000592 | CS-06236 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 20/07/2023
|  | CS-06237 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-004 | Reconductor the Beauly - Foyers - Blackhillock 275kV double circuit line with larger capacity conductor between Beauly - Knocknagael and between Knocknagael - Blackhillock and Blackhillock - Kintore (XH1/XH2). The substation at Knocknagael is adjacent to the existing Foyers line tee point. | 20/07/2023
|  | CS-06238 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 20/07/2023
|  | CS-06239 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 20/07/2023
Braco Battery | PRO-000943 | CS-06209 | GIGABOX BRACO LIMITED | Braco West GSP |  | FALSE | 30/06/2022
Bradford West 100MW | PRO-001874 | CS-07177 | 24 POWER LTD | Bradford West 275kV Substation | 101744-203464 | Bradford West 275kV substation 1. Extend Mesh Corner 2 and install a Circuit breaker and associated disconnectors to allow connection of the Users generator circuit 2. Modify the mesh corner protection scheme as required, update Substation Control System and database changes | 31/08/2025
|  | CS-07178 | 24 POWER LTD | Bradford West 275kV Substation | 101611-203237 | Hotwire the 2x400mm2 section of the Rochdale - Whitegate 1 275kV circuit to operate at 65°C. | 31/08/2025
|  | CS-07179 | 24 POWER LTD | Bradford West 275kV Substation | 031380-031380 | Hotwire the 4x400mm2 sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 31/08/2025
|  | CS-07180 | 24 POWER LTD | Bradford West 275kV Substation | 101561-203105 | Uprate the cables sections on: 1) Rochdale – Whitegate 2 275kV circuit 2) Kearsley – Whitegate 1 and 2 275kV circuits | 31/08/2025
|  | CS-07181 | 24 POWER LTD | Bradford West 275kV Substation | 101744-203465 | On the Ferrybridge – Skelton Grange 1 275kV circuit, reconductor the 1x700mm2 section of the circuit with 1x772mm2 Warwick conductor or equivalent. | 31/08/2025
|  | CS-07182 | 24 POWER LTD | Bradford West 275kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm2 sections with 2x620mm2 GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 31/08/2025
|  | CS-07183 | 24 POWER LTD | Bradford West 275kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm2 sections of the circuits between towers ZZC40R and ZZC002 and towers ZZC002 and ZZC001 (13,15km total) with 2x570 mm2 strung to an operating temperature of 75°C. The remaining 1.9km section between ZZC46R and ZZC40R which is already 2x570 mm2should be hotwired to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A continuous. | 31/08/2025
|  | CS-07184 | 24 POWER LTD | Bradford West 275kV Substation | 101511-202976 | Hotwire the 2x400mm2 section of the Elland – Stalybridge circuit between towers ZP127 and ZP183 (17.86km) to an operating temperature of 75°C | 31/08/2025
|  | CS-07185 | 24 POWER LTD | Bradford West 275kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 31/08/2025
Bradwell Energy Park | PRO-004004 | CS-09179 | LOW CARBON SOLAR PARK 28 LIMITED | Rayleigh 400kV Substation | 102732-205518 | Extend Rayleigh 400kV substation main and reserve 1 busbars for the provision of one User Bay. | 30/10/2033
Braelangwell Wind Farm | PRO-000916 | CS-05508 | WIND DEVELOPMENT HOLDINGS LIMITED | Shin GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 01/02/2028
|  | CS-05509 | WIND DEVELOPMENT HOLDINGS LIMITED | Shin GSP | SHET-RI-123 | Shin – Loch Buidhe 132kV Reconductoring | 01/02/2028
|  | CS-05510 | WIND DEVELOPMENT HOLDINGS LIMITED | Shin GSP | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 01/02/2028
|  | CS-05511 | WIND DEVELOPMENT HOLDINGS LIMITED | Shin GSP | SHET-RI-052 - Lairg – Loch Buidhe 132kV Reinforcement | Establish a new 132kV double busbar at Lairg (Dalchork substation) and construct approximately 17km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. | 01/02/2028
Braidfield Battery Storage | PRO-002357 | CS-08387 | BRAIDFIELD BATTERY STORAGE LIMITED | Windyhills 132kV Substation | Braidfield - Disconnector at User Substation | Install one 132kV line disconnector at the Braidfield Battery Storage 132kV substation. | 27/09/2027
|  | CS-08385 | BRAIDFIELD BATTERY STORAGE LIMITED | Windyhills 132kV Substation | Braidfield - H1 works at Windyhill 132kV Substation | Install a new 132kV GIS double busbar bay, with associated 132kV disconnectors, at Windyhill 132kV substation. | 27/09/2027
|  | CS-08389 | BRAIDFIELD BATTERY STORAGE LIMITED | Windyhills 132kV Substation | SPT-RI-2148 | WindyHill SGT Auto-close scheme - Installation of an auto-close scheme across the three 275/132kV supergrid transformers at Windyhill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. It is proposed to run SGT3 on open standby and for the loss/opening of SGT1 (CB1380) or SGT2 (CB1480) an instruction shall be issued to close the SGT3 circuit breaker (CB1080) in order to keep two SGTs in service at all times. The scope of works also makes inclusion for the replacement of the SCADA/HMI system in order to facilitate the installation of this auto-close scheme | 27/09/2027
|  | CS-08386 | BRAIDFIELD BATTERY STORAGE LIMITED | Windyhills 132kV Substation | Braidfield - 132kV Circuit | Install a new 132kV circuit between Windyhill 132kV substation and Braidfield Battery Storage 132kV substation. This circuit is circa 3.8km in length from the desktop assessment carried out as part of the application process. | 27/09/2027
|  | CS-08388 | BRAIDFIELD BATTERY STORAGE LIMITED | Windyhills 132kV Substation | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 27/09/2027
|  | CS-08390 | BRAIDFIELD BATTERY STORAGE LIMITED | Windyhills 132kV Substation | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 27/09/2027
Braintree | PRO-001042 | CS-04850 | PIVOTED POWER LLP | Braintree 400kV Substation | 100542-201124 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to Disconnecting Circuit Breaker (DCB). 3. Install 72.5kV, 40kA* Disconnecting Circuit Breaker (DCB) at the 13kV side connecting Tertiary to Connection Assets for Users connection. * Under extreme conditions (G74) the specified 40kA DCB rating is exceeded when both SGTs at Braintree 400/132kV substation are set at identical tap positions, beyond tap position 5 and 13. | 30/10/2024
Braintree (Tertiary) | PRO-001043 | CS-05512 | CSE22 LIMITED | Braintree 400kV Substation | 100852-201706 | Infrastructure | 30/07/2025
|  | CS-05513 | CSE22 LIMITED | Braintree 400kV Substation | 100852-201707 | Connection | 30/07/2025
|  | CS-04851 | CSE22 LIMITED | Braintree 400kV Substation | 100504-201138 | Installation of over current protection at Braintree 132kV substation | 30/07/2025
|  | CS-04852 | CSE22 LIMITED | Braintree 400kV Substation | 100504-201083 | Turn-in Bramford-Braintree-Rayleigh Main circuit to Bulls Lodge 400kV substation | 30/07/2025
Bramford (Tertiary) | PRO-001016 | CS-04853 | PIVOTED POWER LLP | Bramford 400kV Substation | 100580-201128 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to Disconnecting Circuit Breaker (DCB) (to be confirmed at detailed design stage). 3. Install Disconnecting Circuit Breaker (DCB) at the 13kV side connecting Tertiary to Connection Assets for Users connection. 4. Repairment and restoration of the Automatic voltage control (AVC) at Bramford 400/132 kV substation. 5. Repairment and restoration of the auto close scheme at Bramford 400/132kV substation. | 01/11/2023
Bramford BESS | PRO-002071 | CS-08577 | CSE33 LIMITED | Bramford 400kV Substation | 101972-204099 | Extension of the site to accommodate new bay to facilitate a connection | 30/11/2029
|  | CS-08576 | CSE33 LIMITED | Bramford 400kV Substation | 101919-203926 | Extension of Bramford 400kV substation double busbars and establishing separate compound, to provide space for customer bay installation. | 30/11/2029
Bramford Tertiary | PRO-000397 | CS-04854 | BRAMFORD GREEN LIMITED | Bramford 400kV Substation | 100571 - 201216 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV Cable from Tertiary connection to 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting the Tertiary connection to Connection Assets for User’s connection 4. Repairment and restoration of the Automatic voltage control (AVC) at Bramford 400/132 kV substation. 5. Repairment and restoration of the auto close scheme at Bramford 400/132kV substation. 6. Extension of substation to facilitate User Connection | 31/10/2023
|  | CS-04855 | BRAMFORD GREEN LIMITED | Bramford 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 31/10/2023
|  | CS-04856 | BRAMFORD GREEN LIMITED | Bramford 400kV Substation | 021847-032344 | Bramford – Twinstead 400kV cable sections | 31/10/2023
Bramley (tertiary) | PRO-000396 | CS-05514 | BRAMLEY SOLAR LIMITED | Bramley | 100605-201257 | Install an earthing transformer on the 13kV tertiary connection Install a 13kV cable connecting earthing transformer DCB Install a 72.5kV, 40kA rated Disconnecting Circuit Breaker (DCB) to connection assets for the User’s connection | 31/10/2023
Bramley BESS | PRO-001104 | CS-09135 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101065-202138 | Uprate A861 Walham-Cowley (future Walham-Botley West & Botley West – Cowley) 400kV circuit overhead line sections by reconductoring (the 19.2km, 2x500mm2 Rubus at 75oC on L2 towers with summer pre-fault rating of 1438MVA section) with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring (the 61.7km, 4x400mm2 Zebra conductor at 50oC on L6 towers with summer pre-fault rating of 1862MVA) to 75oC to achieve a summer pre-fault rating of 2500MVA. | 29/09/2025
|  | CS-09134 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 29/09/2025
|  | CS-09139 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 29/09/2025
|  | CS-09146 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101501-202957 | Reconductor the Hinkley point - Sandford CSE circuit 1 (only ZG section, 2x500mm2 Rubus at 75oC) with 2x700mm2 Araucaria conductor at 90°C to achieve a pre-fault summer rating of 2397MVA for the entire circuit. | 29/09/2025
|  | CS-09145 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 102087-204278 | Uprate A87D Imperial Park – Melksham (future Imperial Park – Folly Farm – Melksham) 400kV circuit cable section (3.9km, with a summer pre-fault rating of 1424MVA) to a summer pre-fault rating of at least 1621MVA | 29/09/2025
|  | CS-09148 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 033769-033769 | Reconductor the Hinkley (Shurton) – Taunton 1 & 2 400kV circuits (2x500mm2 Rubus at 90oC) with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 29/09/2025
|  | CS-09147 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101501-202958 | Reconductor the Hinkley point - Sandford CSE circuit 2 (only ZG section, 2x500mm2 Rubus at 75oC) with 2x700mm2 Araucaria conductor at 90°C to achieve a pre-fault summer rating of 2397MVA for the entire circuit. | 29/09/2025
|  | CS-04857 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 100894-201793 | 1. Extension of Bicker Fen 400kV substation 2. Installation of tertiary cable box on the 13kV side of SGT1 at the Connection Site. 3. Installation of 13kV cable at the Connection Site. 4. Installation of earthing transformer at the Connection Site 5. Installation of 13kV Disconnector at the Connection Site. | 29/09/2025
|  | CS-09136 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101051-202109 | Uprate the 19.2km Twin Rubus (existing 75°C) section of the Walham – Cowley 400kV circuit to achieve at least 1500MVA pre-fault summer rating or greater and uprate the 2 Quad Zebra (existing 50°C) sections of the Walham – Cowley 400kV circuit between the future Botley West 400kV substation turn in and Cowley 400kV to achieve 1920MVA pre-fault summer rating or greater. | 29/09/2025
|  | CS-09140 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 102272-204627 | Construction of a new 400kV double circuit from the Bramley area to the Slough area (route TBC) | 29/09/2025
|  | CS-09137 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 29/09/2025
|  | CS-09142 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 100424-200970 | Uprate the Bramley - Melksham 400kV circuits 1 and 2 (81.6km, 2x400mm2 zebra conductor at 50oC on L2 towers with summer pre-fault rating of 931MVA) by reconductoring with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA. | 29/09/2025
|  | CS-09143 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 &amp; 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 29/09/2025
|  | CS-09138 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 102093-204284 | Uprate A844 Minety – Cowley 400kV circuit overhead line sections by reconductoring the 0.6km, 2x500mm2 Rubus at 75°C on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 99.5km, 4x400mm2 Zebra conductor at 50°C on L6 towers with summer pre-fault rating of 1862MVA to 75°C to achieve a summer pre-fault rating of 2500MVA | 29/09/2025
|  | CS-09141 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101420-202784 | Uprate the Bramley - Didcot Double circuits to increase thermal capacity: Including the Overhead line and the Cable sections | 29/09/2025
|  | CS-09144 | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 101497-202952 | Uprate the Melksham – Seabank leg of Melksham – Seabank – Sandford (future Melksham – Folly Farm and Folly Farm – Seabank leg of Folly Farm – Seabank – Sandford) 400kV circuit by hotwiring the existing 4x400mm2 Zebra at 50oC section to 75oC to achieve a summer pre-fault rating of 2500MVA and reconductoring the existing 2x700mm2 Araucaria conductor with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 29/09/2025
Branxton Energy Storage Facility | PRO-002076 | CS-07543 | EastCoastGridServices Ltd | Branxton 400kV Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 30/12/2027
|  | CS-07545 | EastCoastGridServices Ltd | Branxton 400kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 30/12/2027
|  | CS-07544 | EastCoastGridServices Ltd | Branxton 400kV Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 30/12/2027
|  | CS-07546 | EastCoastGridServices Ltd | Branxton 400kV Substation | SPT-RI-204 Wishaw - Smeaton - Torness - Eccles Overload Protection Scheme | An overload protection scheme installed within Wishaw - Smeaton - Torness - Eccles 275kV and 400kV network in order to protect the system in compliant Category 2 Intertripping Scheme as defined by the Grid Code. The Interrtripping Scheme will disconnect the generation within the area following system outage conditions being met. | 30/12/2027
Branxton PV & BESS Station | PRO-002122 | CS-08562 | ISLAND GREEN POWER UK LIMITED | Branxton 400kV Substation | SPT-RI-204 | Wishaw-Smeaton-Torness-Eccles Overload Protection Scheme -An overload protection scheme is proposed to be installed within the Wishaw – Smeaton – Torness – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following system outage conditions as specified in Appendix F of the Bilateral Connection Agreement - | 31/10/2028
|  | CS-08557 | ISLAND GREEN POWER UK LIMITED | Branxton 400kV Substation | Branxton PV&BESS works | 1. Installation of a new 400kV double busbar GIS bay at Branxton 400kV substation including a 400kV circuit breaker and associated equipment. 2. Associated portion of the platform cost for the establishing of the substation site. 3. Installation of a new 400kV cable circuit (approx. 2.9km) between Branxton 400kV substation and the User’s site. 4. Installation of a 400kV line disconnector at the User’s site | 31/10/2028
|  | CS-08561 | ISLAND GREEN POWER UK LIMITED | Branxton 400kV Substation | SPTRI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be uprated to achieve an increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm2 AAAC (Araucaria) conductor operating at 75°C. The maximum operating temperature of the conductor system will be increased from 75°C to 90°C. These works will not modify the prevailing circuit configuration- | 31/10/2028
|  | CS-08558 | ISLAND GREEN POWER UK LIMITED | Branxton 400kV Substation | SPT-RI-124 | 400kV GIS substation in Torness Area - A new 23 Bay double busbar 400kV GIS substation will be installed at a site yet to be determined in the Torness Area of East Lothian. This new substation is currently named as “Branxton 400kV Substation”. (SPT-RI-124 | 31/10/2028
|  | CS-08563 | ISLAND GREEN POWER UK LIMITED | Branxton 400kV Substation | SPT-RI-2963 | Branxton to Eccles Further Uprating – In order to alleviate the overloads identified as part of the system studies conducted it is necessary to reconductor both sides of the Branxton to Eccles circuits with twin HTLS “Curlew” conductor. This conductor shall give a summer pre-fault rating on the circuit of 2590MVA | 31/10/2028
|  | CS-08559 | ISLAND GREEN POWER UK LIMITED | Branxton 400kV Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 31/10/2028
|  | CS-08560 | ISLAND GREEN POWER UK LIMITED | Branxton 400kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 31/10/2028
Braybrooke | PRO-003429 | CS-08382 | SSE DE SOLAR HOLDCO LIMITED | Market Harborough 400kV Substation | 100816-201651 | Reconductor the Cottam – Grendon route to achieve a post fault winter rating of 2310MVA | 31/07/2032
|  | CS-08380 | SSE DE SOLAR HOLDCO LIMITED | Market Harborough 400kV Substation | 102381-204829 | Design, construct and commission a new 7 bay Market Harborough 400kV double busbar substation consisting of 2 feeder bays, 1 bus section bay, 1 bus coupler bay, 2 SGT bays and a User generator bay Modifications to the existing tee point on the Grendon – Market Harborough – Staythorpe and Grendon – Market Harborough – Cottam circuits to facilitate a connection to the new 400kV substation | 31/07/2032
|  | CS-08381 | SSE DE SOLAR HOLDCO LIMITED | Market Harborough 400kV Substation | 102512-205110 | Extension of the Market Harborough 400kV substation to accommodate a new bay to facilitate the connection of Braybrooke | 31/07/2032
|  | CS-08384 | SSE DE SOLAR HOLDCO LIMITED | Market Harborough 400kV Substation | 101263-202505 | 1. Hotwire 2x620mm2 sections of Grendon – Staythorpe circuit to standard operating temperature (170 degrees) | 31/07/2032
Braybrooke Solar and Battery Connection | PRO-002207 | CS-07967 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 100816-201651 | Reconductor the Cottam – Grendon route to achieve a post fault winter rating of 2310MVA | 31/10/2031
|  | CS-07968 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101927-203938 | 5. At Sundon 400kV: Replace circuit breakers X130, X510 and X710. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 31/10/2031
|  | CS-07975 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101245-202485 | Reconductor the existing 4x400mm2 conductor on the Eaton Socon – Wymondley 2 400kV circuit with 2x850mm2 90oC conductor to achieve a pre fault summer rating of 2400 MVA | 31/10/2031
|  | CS-07976 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 31/10/2031
|  | CS-07969 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 31/10/2031
|  | CS-07970 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 100591-201213 | Reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 31/10/2031
|  | CS-07971 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 31/10/2031
|  | CS-07973 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 31/10/2031
|  | CS-07974 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 31/10/2031
|  | CS-07977 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 100590-201212 | Reconductor the 2x500mm2 sections of the Ratcliffe – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 31/10/2031
|  | CS-07966 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 102099-204292 | Design, construct and commission a new 7 bay Market Harborough 400kV double busbar substation consisting of 2 feeder bays, 1 bus section bay, 1 bus coupler bay, 2 SGT bays and a User generator bay. Modifications to the existing tee point on the Grendon -Market Harborough – Staythorpe and Grendon – Market Harborough – Cottam circuits to facilitate a connection to the new 400kV substation. | 31/10/2031
|  | CS-07972 | Irena BESS LIMITED | Braybrooke (Network Rail) GSP | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 31/10/2031
Breach Solar Farm | PRO-001019 | CS-04925 | BURWELL 11 SOLAR LIMITED | Burwell 400kV Substation | 100631-201301 | 1. Install a tertiary cable box or bushing on SGT1 2. Install a 13kV cable (if required) from tertiary cable box or bushing to earthing transformer 3. Install an earthing transformer 4. Install 13kV disconnector at the 13kV side connecting the tertiary connection to Connection Assets | 24/11/2023
|  | CS-06143 | BURWELL 11 SOLAR LIMITED | Burwell 400kV Substation | 100630-201300 | Enabling works in respect of tertiary connection at Burwell for Waterbeach | 24/11/2023
Breakish Windfarm | PRO-002170 | CS-08788 | ARISE AB | Breakish 132/33kV | OHL Circuit - Breakish | Construct approximately 8km of single circuit 132kV overhead line from the Breakish Wind Farm substation to Broadford Collector Switching Station. The end of this line will be coupled to a new underground cable (0.5km approximately) that will connect the 8km single circuit 132kV overhead line to a new bay on the Broadford collector switching station 132kV busbars, via the required 132kV switchgear. | 31/05/2029
|  | CS-08789 | ARISE AB | Breakish 132/33kV | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 31/05/2029
|  | CS-08787 | ARISE AB | Breakish 132/33kV | Feeder Bay - Breakish | Install a new 132kV double busbar feeder bay at Broadford collector switching station | 31/05/2029
Bredbury | PRO-001041 | CS-04858 | PIVOTED POWER LLP | Bredbury 275kV Substation | NGET-RI-100248-200774 (Conn) | 1. Install earthing transformer on 13kV Tertiary connection 2. Install 13kV cable to motorised disconnector from tertiary connection 3. Install 13kV disconnector connecting tertiary to connection assets for Users connection | 30/10/2023
Breezy Hill Wind Farm | PRO-000475 | CS-09811 | BROCKWELL ENERGY LIMITED | New Cumnock 132kV Substation | SPT-RI-2301 | Clawfin Collector Substation – At New Cumnock Board “A” a new 132kV circuit breaker bay will be installed with a new 132kV cable circuit out to Clawfin Collector substation. This is the point where the cable circuit shall transition to an OHL for the Breezy Hill connection. At this same point a new tee off point shall be established for the Dersalloch WF connection to accommodate the requested increase in TEC. The cable circuit shall require a capacity of 182MVA. (SPT-RI-2301) | 30/04/2028
|  | CS-06196 | BROCKWELL ENERGY LIMITED | New Cumnock 132kV Substation | Breezy Hill H1 Works | 1. At Breezy Hill Wind Farm 132kV Substation, install a 132kV line disconnector. 2. Install ~6.5km of overhead line (wood pole, Poplar conductor) from Clawfin Collector to Breezy Hill Wind Farm 132kV substation. 3. Install a new 132kV circuit breaker bay at the Clawfin Collector substation. | 30/04/2028
|  | CS-06197 | BROCKWELL ENERGY LIMITED | New Cumnock 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/04/2028
|  | CS-06198 | BROCKWELL ENERGY LIMITED | New Cumnock 132kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/04/2028
|  | CS-06199 | BROCKWELL ENERGY LIMITED | New Cumnock 132kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 30/04/2028
|  | CS-06200 | BROCKWELL ENERGY LIMITED | New Cumnock 132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 30/04/2028
|  | CS-06201 | BROCKWELL ENERGY LIMITED | New Cumnock 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/04/2028
|  | CS-06202 | BROCKWELL ENERGY LIMITED | New Cumnock 132kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 30/04/2028
Bridgwater (tertiary) | PRO-000375 | CS-05515 | BRIDGWATER GREEN LIMITED | Bridgewater 400kV Substation | 100653-201333 | Install an earthing transformer on the 13kV tertiary connection Install a 13kV cable connecting earthing transformer to DCB Install a 72.5kV, 40kA rated Disconnecting Circuit Breaker (DCB) to connection assets for the User’s connection | 01/11/2026
|  | CS-04859 | BRIDGWATER GREEN LIMITED | Bridgewater 400kV Substation | 030752- 030752 | Works required to connect the User to the South West Operational Tripping Scheme (OTS) | 01/11/2026
Bridgwater 2 (tertiary) - New Conn | PRO-001347 | CS-04860 | ENSO GREEN HOLDINGS LIMITED | Bridgewater 400kV Substation | 101043-202096 | 1. Install earthing transformer on 13kV Tertiary connection 2. Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting the Tertiary to Connection Assets for User’s connection 4. Upgrading of Bridgwater Substation from 275/132kV to 400/132kV (subject to change at a later date) ** 5. Works required to connect the User to the Melksham Operational Tripping Scheme (OTS) **Works driven by Hinkley Point C project and not Enso Green Holdings H tertiary connection, but these works will be required for Enso Green Holdings H to connect. | 01/10/2024
|  | CS-04861 | ENSO GREEN HOLDINGS LIMITED | Bridgewater 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 01/10/2024
Brinsworth | PRO-003821 | CS-08924 | SSE RENEWABLES SOLAR & BATTERY HOLDINGS LIMITED | Brinsworth 400kV Substation | 102544-205147 | Extension of 400kV Brinsworth B 400kV busbars to connect user bay | 30/10/2032
|  | CS-08925 | SSE RENEWABLES SOLAR & BATTERY HOLDINGS LIMITED | Brinsworth 400kV Substation | 101812-203717 | A new 400kV route to be established between the Sheffield area and the East Midlands, to aid with North to South flows of generation which consists of rationalisation of existing Chesterfield 275kV to Chesterfield 400kV. The Chesterfield 400kV will have 4x460MVA, 400/132kV SGT along with feeders connecting to Brinsworth and High Marnham | 30/10/2032
Broadshore Offshore Wind Farm | PRO-002171 | CS-07750 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-25c | 0 | 31/10/2033
|  | CS-07759 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-07748 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-25a | 0 | 31/10/2033
|  | CS-07752 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-07751 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-25d | 0 | 31/10/2033
|  | CS-07757 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-07758 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-07749 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-25b | 0 | 31/10/2033
|  | CS-07753 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-07761 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-07755 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-07754 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-07760 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-07747 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-07756 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
Broken Cross Windfarm | PRO-000395 | CS-05516 | BROKEN CROSS WIND FARM LIMITED | Broken Cross Windfarm | SPT-RI-218 Coalburn 132kV Bus Coupler Auto-Close Scheme | An auto-close scheme will be installed at Coalburn 132kV substation, to close CB 1030 if either of the two supergrid transformers, supplying the coupled MAIN 1 or RESERVE 132kV busbars, is disconnected due to an unplanned outage. | 30/09/2023
|  | CS-05517 | BROKEN CROSS WIND FARM LIMITED | Broken Cross Windfarm | SPT-RI-155 | Replace the 3.2km 132kV undergroud cable section on the Coalburn to Linmill No.1 132kV circuit. | 30/09/2023
|  | CS-05518 | BROKEN CROSS WIND FARM LIMITED | Broken Cross Windfarm | Broken Cross H1 Enabling | 1. Install a 132kV disconnector at Broken Cross Wind Farm 132kV substation. 2. Install 3.2km of 132kV wood pole overhead line between Broken Cross Wind Farm 132kV substation and the Coalburn to Linnmill/Blacklaw Extension 132kV circuit intermediate terminal tower, where a ‘T’ connection will be formed. | 30/09/2023
|  | CS-05519 | BROKEN CROSS WIND FARM LIMITED | Broken Cross Windfarm | SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 30/09/2023
Brown Rig Wind Farm | PRO-004083 | CS-09305 | SSE RENEWABLES SERVICES (UK) LIMITED | Hawick 132kV Substation | SPT-RI-2378 | Teviot 400/132kV substation - Construct a new 400/132kV substation to facilitate the new 400kV OHL connections into the site as well as install two new 400/132kV 360MVA transformers and a 132kV double busbar substation for the Teviot windfarm connection. It is proposed to install Gas Insulated Switchgear (GIS) rated at 5000A. (SPT-RI-2378) | 31/10/2033
|  | CS-09304 | SSE RENEWABLES SERVICES (UK) LIMITED | Hawick 132kV Substation | NGET 101268-202511 | Installation of two new 400/132kV 240MVA SGT’s at Harker 132kV substation and associated bay asset | 31/10/2033
|  | CS-09309 | SSE RENEWABLES SERVICES (UK) LIMITED | Hawick 132kV Substation | Disconnector - Brown Rig | Installation of one 132kV line disconnector at the User’s Brown Rig 132/33kV substation. | 31/10/2033
|  | CS-09307 | SSE RENEWABLES SERVICES (UK) LIMITED | Hawick 132kV Substation | Feeder Bay (Teviot SS) - Brown Rig | Installation of one 132kV double busbar feeder bay at Teviot 132kV substation | 31/10/2033
|  | CS-09308 | SSE RENEWABLES SERVICES (UK) LIMITED | Hawick 132kV Substation | 132kV Circuit Teviot to User - Brown Rig | Installation of a new 132kV circuit between Teviot substation and the User’s substation. The circuit length is approximately 29km in length following the initial desktop assessment using both 132kV OHL and cable sections | 31/10/2033
|  | CS-09306 | SSE RENEWABLES SERVICES (UK) LIMITED | Hawick 132kV Substation | NGET-101268-202520 | Uprating of two 132kV cross border OHL circuits (Chapel Cross-Harker and Gretna-Harker-Hawick.) The preferred option is the replacement of the existing conductor with a higher rated conductor. In addition, a third circuit will be created on the single circuit V route to create Gretna-Harker-Hawick 1 and 2. On connection of further customers in Scotland these circuits will eventually become Faw Side-Gretna-Harker 1 and 2. (NGET-101268-202520) | 31/10/2033
|  | CS-09303 | SSE RENEWABLES SERVICES (UK) LIMITED | Hawick 132kV Substation | SPT-RI-1738 | 1. Teviot to Harker Reinforcements - It is proposed to construct at a location in the vicinity of Teviot wind farm site a double busbar 132kV AIS substation to which two 400/132kV 360MVA interbus supergrid transformers will be connected. A double busbar AIS 400kV substation will also be established at the wind farm site to which the interbusing transformers will be connected and two further bays will be provided to connect a double circuit OHL. From the 400kV substation a double circuit OHL of around 43km built on L8 towers and installed with twin Totara conductors will be constructed to Harker 400kV substation. SPT will build the OHL to SPT/NGET boundary and NGET will complete the construction of the scheme from the boundary to Harker. (SPT-RI-1738) | 31/10/2033
Bryn Tilti | PRO-001586 | CS-04700 | RHIWLAS ENERGY PARK LIMITED | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 04/02/2027
|  | CS-04702 | RHIWLAS ENERGY PARK LIMITED | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 04/02/2027
|  | CS-04703 | RHIWLAS ENERGY PARK LIMITED | Chirk GSP | 131323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 04/02/2027
|  | CS-04704 | RHIWLAS ENERGY PARK LIMITED | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 04/02/2027
|  | CS-04705 | RHIWLAS ENERGY PARK LIMITED | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 04/02/2027
Buchan 01 Offshore Wind Farm | PRO-001528 | CS-06576 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | Two new 400kV feeder bays at New Deer 2 400kV substation | At New Deer 2 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Relevant Transmission Licensee and the User (as OTSDUW User) will be the User side of the 400kV feeder circuit breakers/isolators at New Deer 2 400kV substation. | 31/10/2033
|  | CS-06577 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-06578 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-06579 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-06580 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-06581 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-06582 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-06583 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-06586 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-06587 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-06588 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-06590 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-06591 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-06592 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-06593 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-06594 | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
Buckland Marsh Solar Park | PRO-003695 | CS-08665 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 101051-202109 | Uprate A861 Walham- Cowley (future Walham- Botley West & Botley West - Cowley) 400kV circuit overhead line sections by reconductoring the 19.2km, 2x500mm2 Rubus at 75oC on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 61.7km, 4x400mm2 Zebra conductor at 50oC on L6 towers with summer pre-fault rating of 1862MVA to 75oC to achieve a summer pre-fault rating of 2500MVA | 31/10/2033
|  | CS-08668 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 100468-201037 | Reconductor the East Claydon -Leighton Buzzard and Cowley - Leighton Buzzard circuits. | 31/10/2033
|  | CS-08669 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 102093-204284 | Uprate A844 Minety – Cowley 400kV circuit overhead line sections by reconductoring the 0.6km, 2x500mm2 Rubus at 75°C on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 99.5km, 4x400mm2 Zebra conductor at 50°C on L6 towers with summer pre-fault rating of 1862MVA to 75°C to achieve a summer pre-fault rating of 2500MVA | 31/10/2033
|  | CS-08666 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 102386-204875 | Extend the main and reserve busbars at Botley West substation for one additional customer bay. Database update to capture additional generator bay. Design, project management, SAP commissioning resource to facilitate bay extension | 31/10/2033
|  | CS-08664 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 31/10/2033
|  | CS-08663 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 101420-202783 | 1. Build temporary overhead line to divert the Cowley – Walham circuit and replace suspension tower 4TE037 with a new terminal tower. 2. Construct a new four-bay double busbar Botley West 400kV substation adjacent to tower 4TE037, comprising of two feeder bays, a bus coupler and space for installation of one generator bay. 3. Turn in the new Botley West 400kV substation to the Transmission System, creating Cowley – BotleyWest –Walham circuit. (Substation name, design, and location subject to further engineering assessment during NGET option selection phase) | 31/10/2033
|  | CS-08667 | Arise Renewable Energy UK Limited | Botley West 400kV Substation | 101420-202784 | Uprate the Bramley – Didcot 400kV circuits; including overhead line and cable sections. | 31/10/2033
Builth Wells | PRO-001564 | CS-04862 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 31/10/2026
|  | CS-04863 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 033769-033769 | Reconductor the Exeter – Hinkley Point – Taunton 400kV circuits to achieve a 2787MVA pre-fault summer rating. | 31/10/2026
|  | CS-04864 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 31/10/2026
|  | CS-04865 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 31/10/2026
|  | CS-04866 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 101052-202110 | Install power flow control devices along the Imperial Park – Melksham 400kV circuit | 31/10/2026
|  | CS-04721 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 31/10/2026
|  | CS-04722 | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 31/10/2026
Burwell (Tertiary) | PRO-001109 | CS-04896 | PIVOTED POWER LLP | Burwell Main 400kV Substation | 10756-201150 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to Disconnecting Circuit Breaker (DCB). 3. Install Disconnecting Circuit Breaker (DCB) at the 13kV side connecting tertiary to connection assets for Users connection. | 30/06/2029
Bushbury Green Energy Centre | PRO-001907 | CS-07126 | INNOVA RENEWABLES LIMITED | Bushbury GSP | 101730-203440 | Extend Bushbury 275kV Mesh Corner Busbars for the provision of one User Bay | 30/10/2028
|  | CS-07127 | INNOVA RENEWABLES LIMITED | Bushbury GSP | 101731-203442 | Uprating/replacing Bishops wood-Penn-1 circuit to increase capacity above 1000MVA. | 30/10/2028
|  | CS-07128 | INNOVA RENEWABLES LIMITED | Bushbury GSP | 101732-203443 | Uprating/replacing Bushbury - Willenhall-1 circuit to increase capacity above 1000MVA | 30/10/2028
Bustleholme | PRO-001039 | CS-05520 | PIVOTED POWER LLP | Bustleholm GSP | 100670-201370 | 1. Extend substation to facilitate the connection 2. Install earthing transformeron the l3kVTertiary connection 3. Install 13kV cable from 13kV Tertiary connection to Disconnecting Circuit Breaker (DCB) 4. Install 4OkA Disconnecting Circuit Breaker (DCB) at the 1 3kV side connecting tertiary to connection assets for the Users connection | 31/05/2022
|  | CS-05521 | PIVOTED POWER LLP | Bustleholm GSP | 100670-201371 | Connection | 31/05/2022
Caird Hills | PRO-001382 | CS-06651 | EDP RENEWABLES UK LIMITED | Keith GSP | SHET-RI-073 | Keith – Macduff - Blackhillock 132kV Reinforcement | 30/06/2025
|  | CS-06652 | EDP RENEWABLES UK LIMITED | Keith GSP | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 30/06/2025
|  | CS-06653 | EDP RENEWABLES UK LIMITED | Keith GSP | Keith - Intertrip facilities | Item 1 - 1. Install intertrip facilities at Keith 132/33kV GSP substation and provide the status of both grid transformers to a new intertripping panel within the 33kV switchroom at Keith substation. The works will include provision of signals from the National Electricity Transmission System to the Host Distribution Network Operator. The intertrip will operate whenever GT1 or GT3 at Keith 132/33kV GSP substation are unavailable due to planned or unplanned outage conditions, reducing the export of Edintore II Wind Farm to 0MW. | 30/06/2025
|  | CS-06654 | EDP RENEWABLES UK LIMITED | Keith GSP | Intertrip scheme to reduce flow | Item 2 - 2. The Host Distribution Network Operator will install an intertrip scheme that will reduce the power flow from Edintore II to 0MW within 120ms upon receipt of an intertrip signal from the Relevant Transmission Licensee. | 30/06/2025
Cairn Duhie Wind Farm | PRO-001743 | CS-06904 | Renewable Energy Systems Limited | Berry Burn GSP | SHET-RI-175 | Berryburn 275kV Overhead Line Work | 31/10/2027
|  | CS-06905 | Renewable Energy Systems Limited | Berry Burn GSP | Cairn Duhie - Switch Bay | Between the new Tee in point and the new 275/33kV GT, install a new 275kV transformer breaker and associated disconnector switch. | 31/10/2027
Cairnmore Hill Wind Farm | PRO-001304 | CS-05526 | Renewable Energy Systems Limited | Thurso South GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 31/08/2026
|  | CS-05527 | Renewable Energy Systems Limited | Thurso South GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/08/2026
|  | CS-05528 | Renewable Energy Systems Limited | Thurso South GSP | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 31/08/2026
|  | CS-05529 | Renewable Energy Systems Limited | Thurso South GSP | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 31/08/2026
|  | CS-05530 | Renewable Energy Systems Limited | Thurso South GSP | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 31/08/2026
|  | CS-05531 | Renewable Energy Systems Limited | Thurso South GSP | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 31/08/2026
|  | CS-05532 | Renewable Energy Systems Limited | Thurso South GSP | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 31/08/2026
|  | CS-05533 | Renewable Energy Systems Limited | Thurso South GSP | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/08/2026
Caldwell Road | PRO-002710 | CS-09082 | TAGENERGY DEVELOPMENT UK LIMITED | Drakelow 400kV Substation | 102707-205409 | Extension of the existing Drakelow 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 31/10/2033
|  | CS-09083 | TAGENERGY DEVELOPMENT UK LIMITED | Drakelow 400kV Substation | 102485-205071 | Install SGT hot-standby scheme at Drakelow substation. | 31/10/2033
Callisterhall Wind Farm | PRO-001965 | CS-07498 | E Power Limited | Callisterhall 132kV | Calisterhall Item 1 | At Gretna 132kV substation, install a new 132kV AIS outdoor switchbay. | 27/04/2029
|  | CS-07499 | E Power Limited | Callisterhall 132kV | Callisterhall Item 2 | Install a 132kV cable section to go round the north of the substation and establish a cable sealing end. | 27/04/2029
|  | CS-07500 | E Power Limited | Callisterhall 132kV | Callisterhall Item 3 | Install ~15.5km of 132kV circuit (wood pole OHL) to Callisterhall wind farm site. At the wind farm site, install one 132kV line disconnector. | 27/04/2029
|  | CS-07501 | E Power Limited | Callisterhall 132kV | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 27/04/2029
|  | CS-07503 | E Power Limited | Callisterhall 132kV | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 27/04/2029
|  | CS-07502 | E Power Limited | Callisterhall 132kV | SPT-RI-230 | It is proposed to reconductor approximately 36km of the 132kV overhead line existing Gretna to Hawick circuit (AL and V Route), between Gretna and the proposed Faw Side Community Wind Farm ‘T’ connection. It is proposed to utilise LARK HTLS conductor. NGET own a section of AL and V Route on this circuit and will have to reinforce to match the SPT proposals. | 27/04/2029
Camblesforth GSP | PRO-002792 | CS-08443 | NORTHERN POWERGRID (YORKSHIRE) PLC | Camblesforth (Drax) GSP | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 28/10/2033
Camilla Farm | PRO-000886 | CS-05534 | NEXTPOWER EELPOWER CAMILLA LIMITED | Glenniston GSP | SPT-RI-234 | Glenniston 132kV Substation Reinforcement and Associated Works to increase the thermal rating of the equipment: a. Glenniston 132kV T1 LVDOC Relay. b. Glenniston 132kV T2 LVDOC Relay. In addition, replacement of the 132kV disconnectors 124 and 128 and bus section circuit breaker 120 to achieve a minimum rating of 185MVA. | 15/02/2022
Camster 2 Wind Farm | PRO-000963 | CS-05535 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2024
|  | CS-05536 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | Camster 2 Wind Farm | 1. Install 2 x 132kV transformer circuit breaker bays connected off the Mybster 132kV busbar extension, complete with protection and associated auxiliary equipment. 2. At Mybster 132/33kV substation, the Relevant Transmission Licensee shall replace the existing 2 x 30MVA and 1 x 60MVA 132/33kV transformers with higher rated twin 120MVA 132/33kV transformers within the same substation accommodation. The works will include all associated plinth foundations, transformer protection equipment, and 33kV cabling work associated with the two replacement 120MVA transformers. | 31/10/2024
|  | CS-05537 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-032b | Spittal – Mybster 132kV Reinforcement — This consists of a new higher capacity 132kV OHL and substation works between Spittal and Mybster substation. (SHET-RI-032b) | 31/10/2024
|  | CS-05538 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 31/10/2024
|  | CS-05539 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 31/10/2024
|  | CS-05540 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/10/2024
Canterbury North | PRO-001216 | CS-05541 | SOUTH EASTERN POWER NETWORKS PLC | Canterbury North GSP | Thermal overload relief work. | Thermal overload relief work. | 01/12/2021
|  | CS-05542 | SOUTH EASTERN POWER NETWORKS PLC | Canterbury North GSP | NGET-RI-11642 | Hotwiring of the Lovedean - Ninfield - Bolney circuits to increase their thermal rating. | 01/12/2021
|  | CS-05543 | SOUTH EASTERN POWER NETWORKS PLC | Canterbury North GSP | NGET-RI-21588 | Re-conductor the Dungeness - Sellindge OHL circuits to increase capacity. | 01/12/2021
|  | CS-05544 | SOUTH EASTERN POWER NETWORKS PLC | Canterbury North GSP | NGET-RI-30967 & NGET-RI-30968 | Construction of a new Sellindge double busbar bypass 400kV Substation. | 01/12/2021
|  | CS-05545 | SOUTH EASTERN POWER NETWORKS PLC | Canterbury North GSP | NGET-RI-31338, NGET-RI-31339 & NGET-RI-21497-5 | Installation of Flexible AC Transmission Solutions (FACTS) at Bolney, Ninfield and Richborough and associated works. | 01/12/2021
Canterbury Tertiary | PRO-001029 | CS-04914 | ENSO GREEN HOLDINGS LIMITED | Canterbury 400kV Substation | 100918-201842 | 1. Install a tertiary cable box or bushings on SGT2 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer 3. Install an earthing transformer 4. Install 13kV Disconnector at the 13kV side connection the tertiary to the Connection Assets. 5. Extension of the Sellindge OTS to include Richborough Energy Park. | 31/10/2025
|  | CS-04915 | ENSO GREEN HOLDINGS LIMITED | Canterbury 400kV Substation | 100298-200724 | 1. Re-conductor Fleet-Lovedean 400kV double circuits. | 31/10/2025
|  | CS-04916 | ENSO GREEN HOLDINGS LIMITED | Canterbury 400kV Substation | 033773-033773 | Thermal upgrade of Bramley – Fleet 400kV double circuits. | 31/10/2025
|  | CS-04917 | ENSO GREEN HOLDINGS LIMITED | Canterbury 400kV Substation | 3187 | 1. Thermal reinforcement to the South Coast, New offshore HVDC link between Suffolk and Kent | 31/10/2025
Capenhurst | PRO-002162 | CS-08911 | ENSO GREEN HOLDINGS LIMITED | Capenhurst 275kV Substation | 101960-204081 | - Extension of Capenhurst 275KV busbars to make provision for the connection of user. - Replace L45,H40,W10,W20 Breakers at Capenhurst 275kV substation. | 31/10/2030
Capenhurst (Tertiary) | PRO-000540 | CS-04918 | ENSO GREEN HOLDINGS LIMITED | Capenhurst 275kV Substation | 100956-201906 | 1. Install a tertiary cable box or bushings on SGT5A. 2. Install a 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 31/10/2025
Capenhurst Tertiary Connection | PRO-001028 | CS-04919 | HD888CAP LIMITED | Capenhurst 275kV Substation | 100533-201152 | 1. Install a tertiary cable box or bushings on SGT2B 2. Install a 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer at the 13kV side. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 31/10/2023
Carberry BESS (was Smeaton BESS) | PRO-003053 | CS-09609 | HARMONY ENERGY LIMITED | Smeaton 400kV | SPT-RI-3471 - New Dalkeith 400kV GIS Substation | Creation of a new Dalkeith 400kV GIS substation is proposed to be established on SPT owned land ~0.5km East of Smeaton substation under SPT-RI-3471. The new Dalkeith 400kV GIS substation is proposed to connect through the turn in of both ZS route circuits and at the moment is notionally a 12 bay 400kV GIS substation with the following bays: • 4 x DBB feeder bays for connection into ZS route circuits • 2 x bus section circuit breakers • 2 x bus couplers • 5 x DBB feeder bays for future connections (As a minimum | 30/06/2031
Car Duibh Wind Farm | PRO-002342 | CS-09188 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2034
|  | CS-09192 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2034
|  | CS-09187 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-213 | Installation of a new 275kV disconnector switch (L17) at Car Duibh 275kV substation, connecting the new 275kV metering circuit breaker (L10) to a 275kV busbar constructed under the new TORI SHET-RI-213. Car Duibh 275kV Substation and OHL Works - Construction of the new Car Duibh 275kV substation and a 275kV 5km double circuit tower line, connecting into the proposed Creag Dhubh - An Suidhe - Craig Murrail 275kV double circuit tower line in a "turn in" arrangement. This construction arrangement will turn this into a Creag Dhubh - Car Duibh - An Suidhe - Craig Murrail 275kV circuit. (SHET-RI-213) | 31/10/2034
|  | CS-09189 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2034
|  | CS-09191 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 31/10/2034
|  | CS-09190 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-077 | 3rd Subsea Cable Link Kintyre – Hunterston Reinforcement - Establish a third 240MVA 220kV subsea cable circuits between the 132kV substation at Crossaig and the existing 400kV busbar at Hunterston (SPT will make this connection and provide any necessary infrastructure at Hunterston). | 31/10/2034
|  | CS-09193 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-130a | North Argyll – Craig Murrail 275kV Operation - Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Creag Dhubh substation (established as part of SHET-RI-013) to Craig Murrail Substation. This will require the upgrade of substations on this circuit for 275kV operation | 31/10/2034
|  | CS-09194 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 31/10/2034
|  | CS-09195 | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bipole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 31/10/2034
Carlincraig Wind | PRO-000583 | CS-06640 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 30/09/2023
|  | CS-06641 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-004 | Reconductor the Beauly - Foyers - Blackhillock 275kV double circuit line with larger capacity conductor between Beauly - Knocknagael and between Knocknagael - Blackhillock and Blackhillock - Kintore (XH1/XH2). The substation at Knocknagael is adjacent to the existing Foyers line tee point. | 30/09/2023
|  | CS-06642 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/09/2023
|  | CS-06643 | Scottish Hydro Electric Power Distribution Plc | Macduff GSP | SHET-RI-073 | Keith – Macduff - Blackhillock 132kV Reinforcement | 30/09/2023
Carn Fearna Wind Farm | PRO-002231 | CS-08144 | STATKRAFT UK LTD | Carn Fearna Wind Farm 132/33kV Substation | Carn Fearna Wind Farm H1 SS | 1. Allowance to extend the Corriemoillie Substation 132kV busbars and install a new 132kV feeder bay comprising a line disconnector, a feeder circuit breaker and two busbar selector disconnectors. 2. Construction of 9.4km of single 132kV OHL from the User’s site to Corriemoillie 132kV Substation. 3. Installation of an indoor type 132kV line disconnector within a building at the User’s substation. 4. Associated secondary equipment including protection of the new equipment. | 30/06/2029
|  | CS-08146 | STATKRAFT UK LTD | Carn Fearna Wind Farm 132/33kV Substation | SHET-RI-065b | Beauly 3rd SGT Replacement- Replacement of third existing 275/132kV 120MVA SGT with a new 360MVA 275/132kV transformer. (SHET-RI-065b) | 30/06/2029
|  | CS-08145 | STATKRAFT UK LTD | Carn Fearna Wind Farm 132/33kV Substation | SHET-RI-065a | Beauly 132 kV Substation Redevelopment- Establish a new 132kV double busbar arrangement at Beauly substation, and transfer the circuits from the existing 132kV busbar to the new busbar. Connect the new 132kV double busbar to the existing 275kV busbar via two new 360MVA 275/132kV transformers. Third new 360MVA 275/132kV transformer will be undertaken under SHET-RI 065b. (SHET-RI-065a) | 30/06/2029
Carrick Wind Farm | PRO-001026 | CS-06676 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Carrick Wind Farm Substation | Carrick - H1 Substation | Installation of one 275kV disconnector at Carrick substation. | 28/02/2029
|  | CS-05549 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Carrick Wind Farm Substation | SPT-RI-293 | Carrick 275kV Substation - A new 275kV substation will be installed on the Coylton-Mark Hill 275kV circuit (YY route) approximately 25km northeast of Mark Hill substation. The YY route will be turned in to the new substation with a 275kV circuit breaker on each circuit. The new circuit breakers will maintain the single-phase high-speed auto reclose capability which currently exists on the YY route. (SPT-RI-293) | 28/02/2029
|  | CS-05550 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Carrick Wind Farm Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 28/02/2029
|  | CS-05551 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Carrick Wind Farm Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 28/02/2029
Carrington | PRO-001025 | CS-04920 | PIVOTED POWER LLP | Carrington 275kV Substation | NGET-RI-100278-200776 (Infra) | 1. Install earthing transformer on 13kV Tertiary connection 2. Install 13kV motorised Switch-Disconnector connecting tertiary to connection assets for Users connection – | 31/10/2028
Carsebank PV | PRO-001169 | CS-06246 | Scottish Hydro Electric Power Distribution Plc | Lunanhead GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 30/11/2021
Castlemilk 1 | PRO-003932 | CS-09679 | Queequeg renewables Ltd | Moffat GSP | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 31/10/2036
|  | CS-09678 | Queequeg renewables Ltd | Moffat GSP | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 31/10/2036
Cathkin Energy Storage | PRO-001925 | CS-07166 | CATHKIN ENERGY STORAGE LIMITED | East Kilbride GSP | Cathkin - Bus section reactor & two new 33kV 3-panel switchboards | At East Kilbride GSP, a bus section reactor (30 MVA) shall be installed alongside two new 33kV 3-panel switchboards. | 31/07/2024
Cathkin Quarry BESS | PRO-003200 | CS-09774 | Bluestone Energy Ltd | East Kilbride GSP | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 06/07/2026
|  | CS-09775 | Bluestone Energy Ltd | East Kilbride GSP | SPT-TOCO-518 | East Kilbride GSP - A bus section reactor will be installed on the SPT side of the GSP, with two new 33kV 3-panel switchboards | 06/07/2026
Ceislein Wind Farm | PRO-003256 | CS-08645 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Ceislien Wind Farm | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/10/2031
Cellarhead | PRO-002161 | CS-08827 | ENSO GREEN HOLDINGS LIMITED | Cellarhead 400kV Substation | 101976-204101 | At Cellarhead 400 kV substation, busbar extension to create the required space for the User generator bay. | 31/10/2033
Cellarhead 400kV Energy Storage | PRO-001685 | CS-04345 | C & S ENERGY LIMITED | Cellarhead 400kV Substation | 101346-202666 | Extension of the existing Cellarhead 400kV substation busbars to accommodate the User’s bay | 30/05/2024
|  | CS-04921 | C & S ENERGY LIMITED | Cellarhead 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/05/2024
|  | CS-04922 | C & S ENERGY LIMITED | Cellarhead 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/05/2024
Cellarhead Green Energy Centre | PRO-001758 | CS-04923 | INNOVA RENEWABLES LIMITED | Cellarhead 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2028
|  | CS-04924 | INNOVA RENEWABLES LIMITED | Cellarhead 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2028
|  | CS-04738 | INNOVA RENEWABLES LIMITED | Cellarhead 400kV Substation | 101357-202677 | Extension of the existing Cellarhead 400kV substation busbars to accommodate the User’s bay | 30/10/2028
Celtic Offshore Wind Farm | PRO-001760 | CS-05372 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 31/10/2031
|  | CS-05373 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 31/10/2031
|  | CS-05374 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400 to 132kV SGTs located within the 132kV compound | 31/10/2031
|  | CS-05375 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 31/10/2031
|  | CS-05376 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault Summer rating of 1650MVA. | 31/10/2031
|  | CS-05377 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-05378 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 020903-020903 | Uprating of Cowley-Minety 400kV circuit and Cowley-Minety 400kV cables to achieve 1300 MVA pre-fault Summer rating. | 31/10/2031
|  | CS-05379 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 31/10/2031
|  | CS-05380 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 31/10/2031
|  | CS-05381 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-05382 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 31/10/2031
|  | CS-05369 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101394-202731 | Infrastructure works at Alverdiscott 400kV substation for the generation connection of RWE Celtic offshore wind farm | 31/10/2031
|  | CS-05370 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101394-202732 | Extension of the OTS at Alverdiscott to incorporate the RWE Celtic offshore windfarm | 31/10/2031
|  | CS-05371 | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 31/10/2031
Celtic Sea Offshore Wind Farm | PRO-001763 | CS-04878 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 020903-020903 | Uprating of the Cowley - Walham 400kV circuit cables to achieve 1500MVA post-fault summer rating. | 31/10/2031
|  | CS-04879 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 31/10/2031
|  | CS-04880 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 31/10/2031
|  | CS-04881 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 31/10/2031
|  | CS-04882 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 31/10/2031
|  | CS-04883 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-04884 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-04871 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Hinkley Point - Exeter 400kV circuits to achieve a 3100MVA post fault winter rating. Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating | 31/10/2031
|  | CS-04872 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 31/10/2031
|  | CS-04873 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101389-202722 | Extension of the OTS at Alverdiscott to incorporate the wind farm. | 31/10/2031
|  | CS-04874 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 31/10/2031
|  | CS-04875 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 31/10/2031
|  | CS-04876 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101389-202721 | Substation works at Alverdiscott 400kV to enable generation connection of 400MW for Celtic Sea Offshore Wind Farm. | 31/10/2031
|  | CS-04877 | CELTIC SEA OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 31/10/2031
Celtic Sea Offshore Wind Farm (ESB) | PRO-002219 | CS-07933 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 31/10/2031
|  | CS-07942 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 020903-020903 | Uprating of the Cowley-Walham / Cowley Minety 400kV circuit cables to achieve 1900MVA post-fault summer rating | 31/10/2031
|  | CS-07945 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-07944 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 31/10/2031
|  | CS-07938 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 31/10/2031
|  | CS-07940 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101619-203253 | Reconductoring of the Landulph – Langage 2 circuit to achieve a post-fault Summer rating of 2150MVA. | 31/10/2031
|  | CS-07934 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400 to 132kV SGTs located within the 132kV compound | 31/10/2031
|  | CS-07936 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-07939 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101733-203445 | Extension of the South West OTS to incorporate offshore windfarm | 31/10/2031
|  | CS-07947 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 31/10/2031
|  | CS-07932 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 31/10/2031
|  | CS-07935 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault Summer rating of 1650MVA. | 31/10/2031
|  | CS-07943 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 1990MVA | 31/10/2031
|  | CS-07946 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 31/10/2031
|  | CS-07937 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 31/10/2031
|  | CS-07941 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 101620-203254 | Reconductoring of the Landulph – Indian Queens 2 circuit to achieve a post-fault Summer rating of 2300MVA. | 31/10/2031
|  | CS-07931 | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation | 102053-204223 | Infrastructure works for the generation connection of ESB Celtic Sea Offshore Wind farm | 31/10/2031
CENOS | PRO-001847 | CS-07380 | FLOTATION ENERGY PLC | Lackenby GSP | 101707-203410 | 0 | 30/10/2033
|  | CS-07381 | FLOTATION ENERGY PLC | Lackenby GSP | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 30/10/2033
|  | CS-07382 | FLOTATION ENERGY PLC | Lackenby GSP | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 30/10/2033
|  | CS-07383 | FLOTATION ENERGY PLC | Lackenby GSP | 100821-201659 | 0 | 30/10/2033
|  | CS-07384 | FLOTATION ENERGY PLC | Lackenby GSP | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 30/10/2033
|  | CS-07385 | FLOTATION ENERGY PLC | Lackenby GSP | 100481-201052 | 0 | 30/10/2033
|  | CS-07386 | FLOTATION ENERGY PLC | Lackenby GSP | 101703-203406 | 0 | 30/10/2033
|  | CS-07387 | FLOTATION ENERGY PLC | Lackenby GSP | 101705-203408 | 0 | 30/10/2033
|  | CS-07388 | FLOTATION ENERGY PLC | Lackenby GSP | 101706-203409 | Reconductor the Osbaldwick – Thornton 400kV OHL circuit ~17km with 3 x 700mm2 Araucaria conductor | 30/10/2033
|  | CS-07374 | FLOTATION ENERGY PLC | Lackenby GSP | 101699-203398 | 0 | 30/10/2033
|  | CS-07375 | FLOTATION ENERGY PLC | Lackenby GSP | 101702-203404 | 0 | 30/10/2033
|  | CS-07376 | FLOTATION ENERGY PLC | Lackenby GSP | 101702-203405 | 0 | 30/10/2033
|  | CS-07377 | FLOTATION ENERGY PLC | Lackenby GSP | 100818-201654 - DUPLICATE | 0 | 30/10/2033
|  | CS-07378 | FLOTATION ENERGY PLC | Lackenby GSP | 101699-203399 | 0 | 30/10/2033
|  | CS-07379 | FLOTATION ENERGY PLC | Lackenby GSP | 101386-202715 | Reconductor the 2x700mm2 sections of the Lackenby-Thornton 1+2 circuit with 2x850mm2 conductor. Reconductor the 4x400mm2 sections with 2x850mm2 conductor. Uprate the cable section of this circuit. (2850MVA). | 30/10/2033
Challoch Solar Farm | PRO-003041 | CS-09464 | SP Distribution plc | Newton Stewart GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 01/08/2028
|  | CS-09467 | SP Distribution plc | Newton Stewart GSP | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 01/08/2028
|  | CS-09466 | SP Distribution plc | Newton Stewart GSP | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 01/08/2028
|  | CS-09463 | SP Distribution plc | Newton Stewart GSP | SPT-RI-223 | Reconductor the existing circuits between Glenlee and Newton Stewart with High Temperature Low Sag conductors. | 01/08/2028
|  | CS-09465 | SP Distribution plc | Newton Stewart GSP | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 01/08/2028
Chalmerston Windfarm | PRO-004057 | CS-09766 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | Chalmerston Windfarm H1 works | 1. At the proposed New Cumnock North 400/275kV substation, install a 275kV GIS bay and associated equipment, a new 275/132kV 120MVA SGT and a 132kV disconnector. 2. Install ~6km of 132kV circuit (OHL is anticipated) to the User’s site. 3. At the User’s site, install one 132kV disconnector. | 31/10/2033
|  | CS-09771 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-3315 | New Cumnock North to Glenmuckloch 400kV OHL- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new double circuit OHL between (the proposed) New Cumnock North and Glenmuckloch 400kV substation. The scope of works shall consist of 2 stages: Stage 1 – establishment of a new double circuit OHL (L8 with Twin RUBUS conductor is proposed) from New Cumnock North towards Glenmuckloch. One side of the circuit shall be energised in this stage to provide a minimum scope required to enable a connection of New Cumnock BESS. Stage 2 – establishment of a second double busbar GIS switchgear bays at New Cumnock North 400kV substation to connect to the OHL No.1 circuit | 31/10/2033
|  | CS-09770 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-3309 | New Cumnock North 400kV GIS substation- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new 400kV substation in the vicinity of the existing New Cumnock 275kV substation. This shall be a double busbar GIS ‘New Cumnock North’ 400kV substation. This new substation shall facilitate the development of the NOA WCNC scheme (currently under review) | 31/10/2033
|  | CS-09767 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-231 | 0 | 31/10/2033
|  | CS-09769 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 31/10/2033
|  | CS-09768 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 31/10/2033
Chapelcross Solar PV and Storage | PRO-002031 | CS-08207 | EEB68 LIMITED | Chapelcross 132/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 29/10/2027
|  | CS-08210 | EEB68 LIMITED | Chapelcross 132/33kV Substation | SPT-RI-298 | Chapelcross to Gretna OHL Reinforcement | 29/10/2027
|  | CS-08208 | EEB68 LIMITED | Chapelcross 132/33kV Substation | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 29/10/2027
|  | CS-08209 | EEB68 LIMITED | Chapelcross 132/33kV Substation | SPT-RI-230 | It is proposed to reconductor approximately 36km of the 132kV overhead line existing Gretna to Hawick circuit (AL and V Route), between Gretna and the proposed Faw Side Community Wind Farm ‘T’ connection. It is proposed to utilise LARK HTLS conductor. NGET own a section of AL and V Route on this circuit and will have to reinforce to match the SPT proposals. | 29/10/2027
Chesterfield | PRO-003861 | CS-08954 | SSE RENEWABLES SOLAR & BATTERY HOLDINGS LIMITED | Chesterfield 400kV Substation (Not yet constructed) | 102533-205145 | Extension of 400kV Chesterfield busbars to connect user bay | 30/10/2032
|  | CS-08955 | SSE RENEWABLES SOLAR & BATTERY HOLDINGS LIMITED | Chesterfield 400kV Substation (Not yet constructed) | 101812-203717 | A new 400kV route to be established between the Sheffield area and the East Midlands, to aid with North to South flows of generation which consists of rationalisation of existing Chesterfield 275kV to Chesterfield 400kV. The Chesterfield 400kV will have 4x460MVA, 400/132kV SGT along with feeders connecting to Brinsworth and High Marnham | 30/10/2032
Chickerell | PRO-002186 | CS-08912 | ENSO GREEN HOLDINGS LIMITED | Chickerell 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 06/12/2036
|  | CS-08913 | ENSO GREEN HOLDINGS LIMITED | Chickerell 400kV Substation | 102057-204228 | Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure. Construction of 400kV Busbar to accommodate the OHL feeders and the Users Generator Bay(s). | 06/12/2036
Chickerell Solar PV & BESS | PRO-001598 | CS-05264 | CHICKERELL SOLAR LIMITED | Chickerell 400kV Substation | 101485-202932 | 1. Extension of existing Main busbar 2 and Reserve busbar 1/2 2. Installation of the one disconnector at Main busbar 2 and Reserve busbar 1/2 to provide the connection point for the generator 3. Installation of new circuit breaker to control MSC2 to maintain the substation operability 4. Works required to connect the User to Category 2 intertripping scheme | 01/10/2027
|  | CS-05265 | CHICKERELL SOLAR LIMITED | Chickerell 400kV Substation | 101033-202065 | Installation of stability OTS for the South West, driven by multiple generation customers | 01/10/2027
|  | CS-05266 | CHICKERELL SOLAR LIMITED | Chickerell 400kV Substation | 100298-200724 | Re-conductor Fleet - Lovedean OHL circuits to increase capacity. | 01/10/2027
|  | CS-05267 | CHICKERELL SOLAR LIMITED | Chickerell 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 01/10/2027
|  | CS-05268 | CHICKERELL SOLAR LIMITED | Chickerell 400kV Substation | 033773-033773 | Thermal upgrade of Bramley – Fleet 400kV double circuits. | 01/10/2027
|  | CS-05269 | CHICKERELL SOLAR LIMITED | Chickerell 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 01/10/2027
|  | CS-05270 | CHICKERELL SOLAR LIMITED | Chickerell 400kV Substation | 033769-033769 | Reconductor the Exeter – Hinkley Point – Taunton 400kV circuits to achieve a 3100MVA pre-fault summer rating | 01/10/2027
Chirk iDNO | PRO-001588 | CS-04742 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 04/02/2027
|  | CS-04743 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 04/02/2027
|  | CS-04744 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 04/02/2027
|  | CS-04745 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 04/02/2027
Chirmorie Wind Farm | PRO-000094 | CS-06664 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-301 | Mark Hill to Arecleoch Ext Tee 132kV Circuit | 30/04/2026
|  | CS-05561 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/04/2026
|  | CS-04259 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/04/2026
|  | CS-05556 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-205 | Installation of approximately 1km of 132kV overhead line between Chirmorie Wind Farm substation and the tee point on the Mark Hill to Stranoch wind farm overhead line, a 132kV isolator at Chirmorie wind farm substation and 132kV substation at Mark Hill and a 132kV switch bay will be installed. From this a 132kV circuit consisting 0.5km of underground cable and 13.5 of 132kV overhead line 300mm UPAS conductor) will be installed to the overhead line tee point connecting the circuits to Chirmorie and Stranoch wind farms. | 30/04/2026
|  | CS-05557 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-206 | At Mark Hill substation a 275kV switchbay will be installed to control a 275/132kV 240MVA transformer (SGT3). This will connect to a 132kV busbar (B Board) provided for the connection of renewable generation. | 30/04/2026
|  | CS-05559 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-136 | Reconductor the 275kV single circuit overhead line (YY route) between Coylton 275kV substation and Mark Hill 275kV substation. | 30/04/2026
|  | CS-05560 | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/04/2026
Chleansaid Wind Farm | PRO-001608 | CS-04471 | ESB ASSET DEVELOPMENT UK LIMITED | Chleansaid Wind Farm 132kV Substation | Chleansaid WF - H1 Works | Installation of indoor type line disconnector | 31/07/2027
|  | CS-04472 | ESB ASSET DEVELOPMENT UK LIMITED | Chleansaid Wind Farm 132kV Substation | SHET-RI-052 - Lairg – Loch Buidhe 132kV Reinforcement | Establish a new 132kV double busbar at Lairg (Dalchork substation) and construct approximately 17km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. | 31/07/2027
|  | CS-04473 | ESB ASSET DEVELOPMENT UK LIMITED | Chleansaid Wind Farm 132kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/07/2027
|  | CS-04474 | ESB ASSET DEVELOPMENT UK LIMITED | Chleansaid Wind Farm 132kV Substation | SHET-RI-133 Loch Buidhe SGT Upgrade | At Loch Buidhe substation remove the existing two 275/132kV 240MVA SGTs, replace with two new 275/132kV 480MVA SGTs and upgrade the 132kV switchboard | 31/07/2027
Cilfynydd | PRO-002088 | CS-08915 | ENSO GREEN HOLDINGS LIMITED | Cilfynydd 400kV Substation | 101947-203994 | Extension of Cilfynydd 400kV substation to provide space for one user bay. | 31/10/2030
|  | CS-08914 | ENSO GREEN HOLDINGS LIMITED | Cilfynydd 400kV Substation | 101947-203995 | Replacement of 6 Cilfynydd 400kV circuit breakers X120, X130, X230 and X110, X505 and X305 with new 63kA rated circuit breakers. | 31/10/2030
Cilfynydd BESS | PRO-002756 | CS-08906 | Cilfynydd BESS Limited | Cilfynydd 400kV Substation | 102584-205197 | Replacement of 5 Cilfynydd 400kV circuit breakers X205, X605, X405, X105, X210 with new 63kA rated circuit breakers. | 15/10/2037
|  | CS-08907 | Cilfynydd BESS Limited | Cilfynydd 400kV Substation | 101947-203995 | Replacement of 6 Cilfynydd 400kV circuit breakers X120, X130, X230 and X110, X505 and X305 with new 63kA rated circuit breakers. | 15/10/2037
|  | CS-08905 | Cilfynydd BESS Limited | Cilfynydd 400kV Substation | 102725-205508 | Extension of Cilfynydd 400kV substation to provide space for one user bay. | 15/10/2037
Cilfynydd Green Energy Centre | PRO-001663 | CS-04485 | CILFYNYDD GREEN ENERGY LIMITED | Cilfynydd 400kV Substation | 101376-202696 | Double busbar extension of Cilfynydd 400kV substation to provide space for the User’s generator bay. | 30/10/2028
|  | CS-04486 | CILFYNYDD GREEN ENERGY LIMITED | Cilfynydd 400kV Substation | 101376-202696 | Double busbar extension of Cilfynydd 400kV substation to provide space for the User’s generator bay. | 30/10/2028
|  | CS-04926 | CILFYNYDD GREEN ENERGY LIMITED | Cilfynydd 400kV Substation | 101376-202697 | Installation of a new commercial Operational Tripping Scheme (via extension of the existing Pembroke OTS). | 30/10/2028
|  | CS-04927 | CILFYNYDD GREEN ENERGY LIMITED | Cilfynydd 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 30/10/2028
|  | CS-04928 | CILFYNYDD GREEN ENERGY LIMITED | Cilfynydd 400kV Substation | 033769-033769 | Reconductor Hinkley Point – Taunton circuits 1 and 2 to achieve 2680MVA pre-fault summer rating. | 30/10/2028
|  | CS-04929 | CILFYNYDD GREEN ENERGY LIMITED | Cilfynydd 400kV Substation | 020903-020903 | Uprating of the Cowley - Walham 400kV circuit cables to achieve 1500MVA post-fault summer rating. | 30/10/2028
|  | CS-04930 | CILFYNYDD GREEN ENERGY LIMITED | Cilfynydd 400kV Substation | 101562-203112 | Reconductor Taunton - Exeter circuits 1 and 2 to achieve 2680MVA pre-fault summer rating. | 30/10/2028
Cilfynydd Grid Stability Services | PRO-002540 | CS-08442 | WP GRID SERVICES 18 LIMITED | Cilfynydd 400kV Substation | 102342-204504 | Reserved extension of Cilfynydd 400kV substation to provide space for the reserved pathfinder bay | 31/07/2025
Clachaig Glen Wind Farm | PRO-000878 | CS-05562 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Carradale 1 GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 30/04/2025
|  | CS-05563 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Carradale 1 GSP | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 30/04/2025
|  | CS-05564 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Carradale 1 GSP | SHET-RI-113 | Kintyre-Hunterston Subsea Cable Intertrip Scheme — Between Crossaig substation and Carradale GSP install an intertrip scheme which will monitor the two 220kV Crossaig – Hunterston subsea cables. Following the loss of both subsea cables (N-2) an intertrip signal will be sent to applicable users to switch out. | 30/04/2025
Clash Gour | PRO-001022 | CS-05565 | EDF ENERGY RENEWABLES LIMITED | Clash Gour Wind Farm 132kV Substation | Clash Gour 3 | On Circuit UH2, it is proposed to install 1 x 275kV line disconnector on the Blackhillock side of the transformer tee, 1 x 275kV line circuit breaker and 1 x 275kV line disconnector on the Knocknagael side of the transformer tee and transformer bay disconnector. | 30/10/2025
|  | CS-05566 | EDF ENERGY RENEWABLES LIMITED | Clash Gour Wind Farm 132kV Substation | Clash Gour 1 | Two new 275kV Towers will be constructed from the Knocknagael – Blackhillock 275kV double circuit tower line (UH2/CA1) to facilitate the installation of two 275kV tappings from circuit UH2 and circuit CA1, which will include down droppers connecting onto new 275kV switchgear located within the substation compound at the Clash Gour 275/132kV Substation. | 30/10/2025
|  | CS-05567 | EDF ENERGY RENEWABLES LIMITED | Clash Gour Wind Farm 132kV Substation | Clash Gour 4 | The installation of two 180/360MVA 275/132kV Transformers, associated HV and LV circuit breaker and the creation of a single 132kV busbar including a 132kV bus section circuit breaker. | 30/10/2025
|  | CS-05568 | EDF ENERGY RENEWABLES LIMITED | Clash Gour Wind Farm 132kV Substation | Clash Gour 2 | On Circuit CA1, it is proposed to install 1 x 275kV line disconnector on the Knocknagael side of the transformer tee, 1 x 275kV line disconnectors and 1 x 275kV line circuit breaker on the Blackhillock side of the transformer tee and transformer bay disconnector | 30/10/2025
Clashindarroch 2 | PRO-000041 | CS-05569 | VATTENFALL WIND POWER LTD | Cairnford GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/04/2025
|  | CS-05570 | VATTENFALL WIND POWER LTD | Cairnford GSP | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 30/04/2025
|  | CS-05571 | VATTENFALL WIND POWER LTD | Cairnford GSP | SHET-RI-025d | North East Reinforcement | 30/04/2025
|  | CS-05572 | VATTENFALL WIND POWER LTD | Cairnford GSP | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 30/04/2025
Clauchrie Windfarm | PRO-001021 | CS-05575 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132kV Substation | SPT-RI-282 | Markhill SGT4 | 31/10/2027
|  | CS-05576 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132kV Substation | Clauchrie H1 OHL/Cable | Installation of approximately 4km of 132kV underground cable or OHL circut between Mark Hill 132kV Substation and Clauchrie 132/33kV Substation. | 31/10/2027
|  | CS-05577 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132kV Substation | Clauchrie H1 SS | At Mark Hill Substation install a new 132kV switch bay and associated equipment and apparatus | 31/10/2027
|  | CS-08436 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 31/10/2027
|  | CS-08435 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 31/10/2027
|  | CS-08434 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132kV Substation | Clauchrie WF H1 Isolator | At Clauchrie Wind Farm 132/33kV Substation, install one 132kV line isolator. | 31/10/2027
Clean Planet Solar | PRO-003519 | CS-08453 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor | 01/11/2037
|  | CS-08458 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm2 conductor | 01/11/2037
|  | CS-08460 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 01/11/2037
|  | CS-08454 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 01/11/2037
|  | CS-08457 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 101468-202908 | Reconductor the Daines – Macclesfield 400kV with 2x780mm2 conductor | 01/11/2037
|  | CS-08461 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 01/11/2037
|  | CS-08455 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 400kV circuits and the Cellarhead – Macclesfield and Cellarhead – Daines 400kV circuits | 01/11/2037
|  | CS-08449 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 102525-205125 | Extend the 400kV substation compound to facilitate the busbar extension for an additional bay. | 01/11/2037
|  | CS-08459 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 100425-200971 | Reconductor the Feckenham – Ironbridge 400kV circuit with 2x620mm2 conductor | 01/11/2037
|  | CS-08451 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with new 2750MVA unit. | 01/11/2037
|  | CS-08452 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor | 01/11/2037
|  | CS-08456 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x780mm2 conductor or equivalent and uprating of the cable section of the circuit | 01/11/2037
|  | CS-08450 | Clean Planet Solar Farm Limited | Frodsham 400kV Substation | 101474-202916 | Uprate the Cellarhead – Drakelow 400kV circuits | 01/11/2037
Cleve Hill Solar Park | PRO-001097 | CS-04255 | CLEVE HILL SOLAR PARK LIMITED | Cleve Hill 400kV Substation | 031867-200324 | Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent. | 22/03/2024
|  | CS-04256 | CLEVE HILL SOLAR PARK LIMITED | Cleve Hill 400kV Substation | 100271-201784 | Extension of the Sellindge Operational Tripping Scheme (OTS) to include Cleve Hill Solar Park, with outputs to be provided at Cleve Hill 400kV substation | 22/03/2024
|  | CS-04257 | CLEVE HILL SOLAR PARK LIMITED | Cleve Hill 400kV Substation | 100271-200969 | Extension of Cleve Hill 400kV substation and provisions for a new Generator bay for Cleve Hill Solar Park | 22/03/2024
Cloiche Wind Farm | PRO-000425 | CS-05578 | SSE GENERATION LIMITED | Cloiche 132kV Substation | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 31/07/2026
|  | CS-05579 | SSE GENERATION LIMITED | Cloiche 132kV Substation | SHET-RI-085a | 2. Melgarve 400/132kV SGT1 – Install a new 400/132kV 480MVA transformer (SGT1) at a new site (Melgarve). This is in order to allow the connection of wind generation in the area. (SHET-RI-085a) | 31/07/2026
|  | CS-05580 | SSE GENERATION LIMITED | Cloiche 132kV Substation | SHET-RI-115 | Melgarve 400-132kV Substation Additional SGTs – At Melgarve substation (established under SHET-RI-085a and SHET-RI-085b), install an additional two 480MVA SGTs to enable the connection of wind generation in the area | 31/07/2026
|  | CS-05581 | SSE GENERATION LIMITED | Cloiche 132kV Substation | SHET-RI-085b | 3. Melgarve 400/132kV Substation – Establish a new 400/132 kV Substation at Melgarve, to allow the connection of wind generation in the area. (SHET-RI-085b) | 31/07/2026
|  | CS-05582 | SSE GENERATION LIMITED | Cloiche 132kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/07/2026
|  | CS-05583 | SSE GENERATION LIMITED | Cloiche 132kV Substation | SHET-RI-069 | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | 31/07/2026
Cloich Forest Wind Farm | PRO-001387 | CS-06665 | EDF ENERGY RENEWABLES LIMITED | Cloiche 132kV Substation | Cloich Forest H1 Works | 1. Installation of a new 132kV double busbar GIS bay at Currie 132kV substation. 2. Installation of a cable/OHL circuit from Currie 132kV substation to Cloich Forest Wind Farm substation (~25km). 3. Installation of a 132kV line disconnector at Cloich Forest Wind Farm substation. 4. Associated civil, miscellaneous and minor works. 5. Associated protection and control works. 6. Provision of communications, alarms, indications and metering from the User site | 30/07/2028
Cloud Hill Windfarm | PRO-001938 | CS-07327 | Cloud Hill Windfarm Limited | Cloud Hill Wind Farm 132kV Substation | Cloud Hill - OHL & cable circuit | 0 | 30/09/2028
|  | CS-07328 | Cloud Hill Windfarm Limited | Cloud Hill Wind Farm 132kV Substation | Cloud Hill - 132kV Disconnector | 0 | 30/09/2028
|  | CS-07329 | Cloud Hill Windfarm Limited | Cloud Hill Wind Farm 132kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 30/09/2028
|  | CS-07330 | Cloud Hill Windfarm Limited | Cloud Hill Wind Farm 132kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 30/09/2028
|  | CS-07331 | Cloud Hill Windfarm Limited | Cloud Hill Wind Farm 132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 30/09/2028
|  | CS-07326 | Cloud Hill Windfarm Limited | Cloud Hill Wind Farm 132kV Substation | Cloud Hill - Indoor GIS switchgear and disconnectors | 0 | 30/09/2028
Cnoc Buidhe Wind Farm | PRO-001672 | CS-04593 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | BPUWL 12 Item 1 | The construction of approximately 15 kilometres of 132kV overhead line (12.5km will be wood pole trident line the other 2.5km will be NETS structures) connecting between Crossaig/Carradale overhead line and the Cnoc Buidhe substation. | 31/10/2028
|  | CS-04594 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | BPUWL 12 Item 2 | At Cnoc Buidhe substation there will be 3x 132kV CB bays installed and a 132kV Disconnector | 31/10/2028
|  | CS-04595 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | BPUWL 12 Item 3 | The T point into the RC 2 circuit will comprise of a 132kV bay (1x 132kV Disconnector and 1x 132kV Circuit Breaker). This will be within a compound constructed for the connection | 31/10/2028
|  | CS-04596 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-013 and SPT-RI-028 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existing Inveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers. Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. Reconfigure Dalmally 275kV substation to a double busbar arrangement to allow the extension of the substation to develop new bays for the connection of renewable generation. (SHET-RI-013 and SPT-RI-028) | 31/10/2028
|  | CS-04597 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 31/10/2028
|  | CS-04598 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 31/10/2028
|  | CS-04599 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2028
|  | CS-04600 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 31/10/2028
|  | CS-04601 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2028
|  | CS-04602 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 31/10/2028
|  | CS-07985 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | Cnoc Buidhe Item 4 | Installation of a new 132kV double busbar circuit breaker bay on the new 132kV double busbar to be located at the new Carradale 132kV substation, installed as part of the TORI SHET-RI-158. This will replace the assets required at the T Point onto the RC2 circuit. | 31/10/2028
|  | CS-07983 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SPT-RI-028 | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | 31/10/2028
|  | CS-07984 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 31/10/2028
|  | CS-07986 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 31/10/2028
|  | CS-07987 | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | SHET-RI-077 | 3rd Subsea Cable Link Kintyre – Hunterston Reinforcement - Establish a third 240MVA 220kV subsea cable circuits between the 132kV substation at Crossaig and the existing 400kV busbar at Hunterston (SPT will make this connection and provide any necessary infrastructure at Hunterston). | 31/10/2028
Cockenzie BESS | PRO-004217 | CS-09392 | ELBESS LTD | Cockenzie 400/132kV Substation | Cockenzie BESS Disconnector | Installation of a 132kV disconnector at Cockenzie 400/132kV Substation | 31/07/2026
|  | CS-09390 | ELBESS LTD | Cockenzie 400/132kV Substation | SPT-RI-2907 | Cockenzie 400/132kV Substation - A new 400/132kV substation will be installed via a tee-off with ZA route (No.2 circuit ZA001A Tower). A new 400kV disconnector circuit breaker will be installed at the new substation, along with a 360MVA 400/132kV Super grid transformer. A new 132kV busbar will be established | 31/07/2026
|  | CS-09391 | ELBESS LTD | Cockenzie 400/132kV Substation | SPT-RI-1742 Cockenzie LMS (Cat 2) | 4. Cockenzie Load Management Scheme (Cat 2) – An overload protection scheme is proposed to be installed within the Cockenzie – Smeaton – Kaimes – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following defined system outage conditions. (SPT-RI-1742) | 31/07/2026
Cogle Moss Wind Farm | PRO-000973 | CS-06210 | COGLE MOSS RENEWABLES LLP | Mybster 2 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/08/2025
|  | CS-06211 | COGLE MOSS RENEWABLES LLP | Mybster 2 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 31/08/2025
|  | CS-06212 | COGLE MOSS RENEWABLES LLP | Mybster 2 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/08/2025
Coire Glas Pumped Storage | PRO-000073 | CS-05584 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | Coire Glas Pumped Storage H1 Works Item 2 | Construction of approximately 13km of double circuit 400kV steel tower line from Invergarry to the connection site. | 01/12/2027
|  | CS-05585 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | Coire Glas Pumped Storage H1 Works Item 1 | Installation of 400kV GIS double busbar arrangement and associated bus section circuit breakers/isolators at the connection site. | 01/12/2027
|  | CS-05586 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SHET-RI-068 | Upgrade the existing 132kV double circuit OHL between Fort Augustus and Invergarry substation by a new 400kV OHL. The existing 132kV OHL forms part of the Fort Augustus to Fort William FFE/FFW circuits. Part of the upgrade is to establish a 400/132kV substation at Invergarry to connect the existing 132kV OHL from Fort William and Invergarry Generation. The new 400kV OHL will terminate into the 400kV busbar at For Augustus. | 01/12/2027
|  | CS-05587 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 01/12/2027
|  | CS-05588 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SHET-RI-069 | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | 01/12/2027
|  | CS-06231 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 01/12/2027
|  | CS-06232 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 01/12/2027
|  | CS-06233 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SPT-RI-003 | Denny-Strathaven 400kV Reinforcement - Construct a new 400kV double circuit overhead line from Bon-nybridge to Newarthill and re-configure associated sites to establish a fourth north to south dou-ble circuit Supergrid route through the Scottish central belt. One side of the new overhead line will oper-ate at 400kV, the other at 275kV. This reinforcement will establish Denny-Bonnybridge, Bonnybridge-Wishaw, Wishaw-Strathaven No.2 and Wishaw-Torness 400kV circuits and a Denny-Newarthill-Easterhouse 275kV circuit. (SPT-RI-003) | 01/12/2027
|  | CS-06234 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 01/12/2027
|  | CS-06235 | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | SPT-RI-1560 | It is proposed to uprate the existing Denny-Braco West 275kV circuit to 400kV operation by transferring the circuit from its current bay in Denny 275kV substation to a new bay in Denny 400kV substation. | 01/12/2027
Copper Nose BESS | PRO-002356 | CS-07906 | Copper Nose Energy Ltd | Fawley 132kV Substation | 101562-203112 | Reconductor Taunton - Exeter 1 & 2 400kV circuits (2 x 500mm2 Rubus at 75oC) with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MV | 24/10/2036
|  | CS-07905 | Copper Nose Energy Ltd | Fawley 132kV Substation | 101498-202953 | Uprate the double circuits between the Exeter, Axminster & Chickerell substations by reconductoring the 4 x 400mm2 Zebra conductor sections with 3 x 700mm2 Araucaria conductor at 75°C and hotwiring the existing 3 x 700mm2 Araucaria conductor sections at 50°C to 75°C to achieve a pre-fault summer rating of 2790MVA. | 24/10/2036
|  | CS-07901 | Copper Nose Energy Ltd | Fawley 132kV Substation | 102141-204346 | Installation of a 4th 240MVA 400/132kV SGT at Fawley 400kV. | 24/10/2036
|  | CS-07909 | Copper Nose Energy Ltd | Fawley 132kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 24/10/2036
|  | CS-07910 | Copper Nose Energy Ltd | Fawley 132kV Substation | 101033-20265 | Installation of stability OTS for the South West, driven by multiple generation customers | 24/10/2036
|  | CS-07899 | Copper Nose Energy Ltd | Fawley 132kV Substation | 102127-204336 | Uprate the Lovedean - Nursling section (NASP Code: A84E) of the Lovedean – Mannington – Nursling circuit to summer pre fault rating of 2570MVA Reconductor to Triple Araucaria and hotwire to 75°C. Note: Under scheme 101387 the Lovedean - Mannington - Nursling circuit will become two circuits: Lovedean - Nursling and Mannington - Nursling | 24/10/2036
|  | CS-07900 | Copper Nose Energy Ltd | Fawley 132kV Substation | 102135-204339 | Uprate the Fawley – Mannington circuit (NASP Code: A837) to summer pre fault rating of 3160MVA Reconductor to Triple Araucaria and hotwire to 90°C Note: Under scheme 101387 the Fawley – Mannington circuit will become Fawley – Nursling and Nursling – Mannington. | 24/10/2036
|  | CS-07903 | Copper Nose Energy Ltd | Fawley 132kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 24/10/2036
|  | CS-07902 | Copper Nose Energy Ltd | Fawley 132kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 24/10/2036
|  | CS-07904 | Copper Nose Energy Ltd | Fawley 132kV Substation | 101833-203761 | Uprate the Chickerell - Mannington double circuit (NASP Code: A851 and A830) by hotwiring the existing 3 x 700mm2 Araucaria conductor at 50°C to 90°C to achieve a pre-fault summer rating of 3160MVA | 24/10/2036
|  | CS-07898 | Copper Nose Energy Ltd | Fawley 132kV Substation | 102136-204339 | Uprate the Mannington – Nursling section (NASP Code: A84D) of the Lovedean – Mannington - Nursling circuit to summer pre fault rating of 3160MVA Reconductor to Triple Araucaria and hotwire to 90°C Note: Under scheme 101387 the Lovedean – Mannington –Nursling circuit will become two circuits Lovedean – Nursling and Mannington – Nursling | 24/10/2036
|  | CS-07907 | Copper Nose Energy Ltd | Fawley 132kV Substation | 100424-200970 | Uprate the Bramley - Melksham 1 & 2 400kV circuits (81.6km, 2 x 400mm2 zebra conductor at 50oC on L2 towers with summer prefault rating of 931MVA) by reconductoring with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 24/10/2036
|  | CS-07908 | Copper Nose Energy Ltd | Fawley 132kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 24/10/2036
Cormoran Offshore Wind Farm | PRO-002390 | CS-08158 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-08159 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
|  | CS-08160 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 06/12/2036
|  | CS-08161 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
|  | CS-08163 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 06/12/2036
|  | CS-08164 | South West Wind Holdco Limited | Alverdiscott 400kV Substation |  | FALSE | 06/12/2036
|  | CS-08156 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 102365-204795 | Infrastructure works for the generation connection of Cormoran Offshore wind farm. | 06/12/2036
|  | CS-08162 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-08157 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 06/12/2036
Cornabo Wind | PRO-000659 | CS-03695 | Scottish Hydro Electric Power Distribution Plc | Tarland GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2026
|  | CS-03696 | Scottish Hydro Electric Power Distribution Plc | Tarland GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 31/10/2026
Cornharrow Wind Farm | PRO-001741 | CS-08301 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 31/10/2027
|  | CS-08303 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 31/10/2027
|  | CS-08306 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV | SPT-RI-2094 | Quantans Hill to Holmhill 132kV Circuit – At the proposed Quantans Hill wind farm site establish a 132kV substation and establish a 132kV busbar to which a 132kV line isolator is connected. Install around 6km of wood pole overhead line with HTLS conductor to connect Quantans Hill substation to Holmhill substation. At Holmhill substation install a 132kV circuit breaker to connect the OHL. | 31/10/2027
|  | CS-08304 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 31/10/2027
|  | CS-08305 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV | SPT-RI-1507 | Holmhill 132kV substation | 31/10/2027
|  | CS-08302 | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 31/10/2027
Cornwall Energy Park | PRO-002379 | CS-08770 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to triple Auriacuria 3 x 700mm2 at 90 degrees to achieve a summer pre-fault rating of 3000MVA | 06/12/2036
|  | CS-08761 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 06/12/2036
|  | CS-08759 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 06/12/2036
|  | CS-08760 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
|  | CS-08763 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101497-202952 | Reconductor the single circuit between Melksham - Seabank (route 4YX and 2VL) in order to achieve a pre fault summer rating of 2500MVA and post fault summer rating of 3210MVA. | 06/12/2036
|  | CS-08765 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101501-202957 | Reconductor the Hinkley point - Sandford CSE circuit 1 (only ZG section) in order to achieve a summer post fault rating of 2850MVA | 06/12/2036
|  | CS-08767 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101500-202955 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 1 in order to achieve a summer post fault rating of 2850MVA | 06/12/2036
|  | CS-08766 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101501-202958 | Reconductor the Hinkley point - Sandford CSE circuit 2 (only ZG section) in order to achieve a summer post fault rating of 2850MVA. | 06/12/2036
|  | CS-08762 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101498-202953 | Uprate the double circuit between the Exeter - Axminster – Chickerell substations, to achieve at least a post fault summer rating of 2420MVA | 06/12/2036
|  | CS-08756 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101620-203254 | Reconductoring of the Landulph – Indian Queens 2 circuit to achieve a post-fault Summer rating of 2300MVA. | 06/12/2036
|  | CS-08758 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 100480-201051 | Uprate the cable section of the Seabank -Whitson section of the three-ended Seabank -Whitson - Cilfynydd circuit to a pre-fault rating of 1800MVA | 06/12/2036
|  | CS-08755 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 102351-204521 | Replacement, or modification, of existing towers and associated OHL works to facilitate a full turn in of the Indian Queens - Landulph #2 (A87B) overhead line circuit. Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure. Construction of 400kV Busbar to accommodate the OHL turn-in and the Users Generator Bay. Local works to facilitate the extension of the Operational Tripping Scheme | 06/12/2036
|  | CS-08757 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101619-203253 | Reconductoring of the Landulph – Langage 2 circuit to achieve a post-fault Summer rating of 2150MVA. | 06/12/2036
|  | CS-08764 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101833-203761 | Uprate the Chickerel - Mannington double circuit (NASP Code: A851 and A830) to summer pre fault rating of 2200MVA. | 06/12/2036
|  | CS-08769 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 06/12/2036
|  | CS-08768 | GREEN ENERGY MAB LTD | Landulph 400kV Substation | 101500-202956 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 2 in order to achieve a summer post fault rating of 2850MVA | 06/12/2036
Corriegarth 2 Wind Farm | PRO-000420 | CS-06886 | CORRIEGARTH 2 WIND FARM LIMITED | Corriegarth 132/33kV substation | 132kV Disconnector, Trident Line and Cable | From a tee point on the existing Farigaig to Corriegarth 132kV circuit, install a new wood pole overhead line consisting of 3 wood pole structures. This is terminated onto a new 1km section of 132kV underground cable terminating on a new 132kV disconnector (103) within the Corriegarth 2 Wind Farm substation. | 31/07/2026
|  | CS-05589 | CORRIEGARTH 2 WIND FARM LIMITED | Corriegarth 132/33kV substation | SHET-RI-129 | Farigaig SGT1 Upgrade - Upgrade the 120MVA 275/132kV SGT1 at Farigaig substation to a 240MVA SGT, to facilitate the connection of generation in the area. | 31/07/2026
|  | CS-05590 | CORRIEGARTH 2 WIND FARM LIMITED | Corriegarth 132/33kV substation | SHET-RI-089 | Upgrade the 120MVA 275/132kV SGT1 at Farigaig substation to a 240MVA SGT to facilitate the connection of generation in the area. | 31/07/2026
Corriemoillie BESS | PRO-003992 | CS-09529 | VIRMATI ENERGY LTD | Corriemoillie 132kV Substation | SHET-RI-065b | Beauly 3rd SGT Replacement- Replacement of third existing 275/132kV 120MVA SGT with a new 360MVA 275/132kV transformer. (SHET-RI-065b) | 30/09/2029
|  | CS-09528 | VIRMATI ENERGY LTD | Corriemoillie 132kV Substation | SHET-RI-065a | Beauly 132 kV Substation Redevelopment- Establish a new 132kV double busbar arrangement at Beauly substation, and transfer the circuits from the existing 132kV busbar to the new busbar. Connect the new 132kV double busbar to the existing 275kV busbar via two new 360MVA 275/132kV transformers. Third new 360MVA 275/132kV transformer will be undertaken under SHET-RI 065b. (SHET-RI-065a) | 30/09/2029
Costa Head Wind Farm | PRO-000104 | CS-05591 | COSTA HEAD WIND FARM LIMITED | Costa Head 132/33kV Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/10/2028
|  | CS-05592 | COSTA HEAD WIND FARM LIMITED | Costa Head 132/33kV Substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 30/10/2028
|  | CS-05593 | COSTA HEAD WIND FARM LIMITED | Costa Head 132/33kV Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 30/10/2028
|  | CS-05594 | COSTA HEAD WIND FARM LIMITED | Costa Head 132/33kV Substation | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 30/10/2028
|  | CS-05595 | COSTA HEAD WIND FARM LIMITED | Costa Head 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 30/10/2028
|  | CS-05596 | COSTA HEAD WIND FARM LIMITED | Costa Head 132/33kV Substation | SHET-RI-019 | Establish a 220kV HVAC circuit over a distance of approximately 68km between the 275kV GIS substation at Dounreay on the mainland and the new 132kV substation in the vicinity of Finstown on Orkney. The HVAC circuit comprises of approximately 15km of land cable and 53km of subsea cable. Voltage Compensation devices will be installed at both cable ends within the substation compounds at Dounreay and Finstown. | 30/10/2028
Cottam | PRO-001502 | CS-04931 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101080-202165 | 1. At Cottam 400kV Substation, extend Main bar 1 and Reserve bar 1/2 to make provision for the User to connect their generator bay (also needs to include site extension) | 31/10/2029
|  | CS-04932 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 31/10/2029
|  | CS-04933 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 033496-033496 | 1. At West Burton 400kV substation install a Power electronics-based power flow control device in the Keadby – West Burton 1 circuit. | 31/10/2029
|  | CS-04934 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101263-202505 | 1. Hotwire 2x620mm2 sections of Grendon – Staythorpe circuit to standard operating temperature (170 degrees) | 31/10/2029
|  | CS-04935 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 31/10/2029
|  | CS-04936 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm2 AAAC sections of the circuits with 2×591mm2 ACCR conductor and the 2x700mm2 AAAC sections with 3x700mm2 AAAC conductor | 31/10/2029
|  | CS-04937 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 31/10/2029
|  | CS-04938 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100844-201689 | Reconductor Cottam – Staythorpe 1 circuit with 2x620mm2 conductor and uprate the cable section to 3 cores per phase | 31/10/2029
|  | CS-04939 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 31/10/2029
|  | CS-04940 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100816-201651 | 1. Hotwire the 2x500mm2 Rubus sections of the Cottam – Grendon 400kV circuit for operation at 90°C | 31/10/2029
|  | CS-04941 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 31/10/2029
|  | CS-04942 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 31/10/2029
|  | CS-04943 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 100451-201016 | 1. Reconductor the 2x500mm2 sections of the High Marnham – West Burton 400kV circuit with 2x700mm2 conductor and replace the cable section | 31/10/2029
|  | CS-04944 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101101-202200 | 1. Uprate the Bicker Fen – Walpole, Bicker Fen – Spalding North & Spalding North – Walpole 400kV circuit by reconductoring the 2 x redwood conductor sections to AAAC conductor | 31/10/2029
|  | CS-04945 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 03305-03305 | 1. Reconductor the 2x400 mm2 sections of the Elstree – Sundon circuits with 2x570mm2 conductor | 31/10/2029
|  | CS-04946 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101264-202506 | 1. Hotwire 4x400mm2 of Cottam – Ryhall circuit (A483) to 65°C, hotwire 3x700mm2 to 75°C | 31/10/2029
|  | CS-04947 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101262-202504 | 1. Installation of a power electronics-based power flow control device at Creyke Beck | 31/10/2029
|  | CS-04948 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 101266-202508 | 1. Hotwire the 4x400mm2 sections of the Sundon – Wymondley circuit to 75°C | 31/10/2029
|  | CS-04949 | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation |  | FALSE | 31/10/2029
Cottam Solar PV + BESS | PRO-001401 | CS-04730 | COTTAM SOLAR PROJECT LIMITED | Cottam 400kV Substation | 101100- 202198 | Provision of a spare skeletal bay at Cottam 400kV Substation (ex-generator 1 bay). | 01/09/2029
Cottered | PRO-002173 | CS-07812 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 30/10/2030
|  | CS-07813 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 30/10/2030
|  | CS-07798 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 30/10/2030
|  | CS-07809 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 101247-202487 | 13. Reconductor LEIGHTON BUZZARD-SUNDON4-1 (LEIB4A-SUND4-1) & LEIGHTON BUZZARD-SUNDON4-2 (LEIB4B-SUND4-2) 400kV circuit to achieve more than 2100MVA summer pre-fault rating. | 30/10/2030
|  | CS-07796 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 102003-204147 | 2. Provide a single turn in of the 400kV OHL between Pelham & Wymondely (A602) to the new 400kV (Cottered) substation | 30/10/2030
|  | CS-07816 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 30/10/2030
|  | CS-07807 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 100468-201037 | 11. Reconductor COWLEY - EAST CLAYDON (COWL4-ECLA4-1) and COWLEY – LEIGHTON BUZZARD (COWL4-LEIB4A-1) circuits to more than 2150MVA summer Pre-fault rating | 30/10/2030
|  | CS-07800 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 102012-204166 | 4. At Rye House 400kV: Replace circuit breakers X130. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2030
|  | CS-07795 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 102003-204155 | 1. Construction of a new 400kV AIS double busbar 400kV substation (Cottered) between Pelham 400kV and Wymondely 400kV substations, comprising a busbar coupler, 2 feeder bays and Users generator bay | 30/10/2030
|  | CS-07815 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 30/10/2030
|  | CS-07799 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 102011-204165 | 3. At Norwich Main 400kV: Replace circuit breakers X320, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2030
|  | CS-07808 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 100952-201899 | 12. Reconductor EAST CLAYDON-LEIGHTON BUZZARD (ECLA4- LEIB4B- 1) 400kV circuit to achieve more than 2095MVA summer pre-fault rating. | 30/10/2030
|  | CS-07810 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 101885-203861 | Reconductor MILLBROOK-SUNDON 4-1 (MILB4-SUND4-1) & MILLBROOK-SUNDON 4-2 (MILB4-SUND4-2) 400kV circuit to achieve more than 1605MVA summer pre-fault rating | 30/10/2030
|  | CS-07804 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 30/10/2030
|  | CS-07805 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 30/10/2030
|  | CS-07806 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm2 and 3M curlew 2x490mm2 @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm2 conductor | 30/10/2030
|  | CS-07803 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 30/10/2030
|  | CS-07802 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2030
|  | CS-07811 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 30/10/2030
|  | CS-07814 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3820 MVA | 30/10/2030
|  | CS-07801 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 101927-203938 | 5. At Sundon 400kV: Replace circuit breakers X130, X510 and X710. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2030
|  | CS-07797 | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 30/10/2030
Coventry | PRO-001005 | CS-04950 | PIVOTED POWER LLP | Coventry 275kV Substation | NGETR1-100278-200689 (INFRA) | 1. Condition assessment of 13kV cables and other assets to confirm suitability for re-use 2. Install earthing transformer on 13kV Tertiary connection* 3. Install 13kV disconnector connecting tertiary to connection assets for Users connection 4. Install 275/132kV Supergrid Transformer (SGT) and associated bay 5. Install 132kV cable from new SGT to existing WPD 132kV LV bay 6. Line entry modification at Coventry-Nechells circurt 7. Associated circuit breakers and disconnectors on Nechells circuit /Mesh Corner 4 *earthing transformer, disconnector, circuit breaker and earth switches associated with existing RSVC may be suitable for this connection. Confirmation to be sought via relevant studies and site inspections as to whether these works can be removed. | 26/05/2023
Cowley (Tertiary) | PRO-000407 | CS-05597 | COWLEY BALDON GREEN LIMITED | Cowley 400kV Substation | 100641-201316 | Install an earthing transformer on the 13kV tertiary connection Install a 13kV cable connecting earthing transformer to DCB Install a 72.5kV, 40kA rated Disconnecting Circuit Breaker (DCB) to connection assets for the User’s connection Install an auto-close scheme on the section breakers at Cowley 132kV substation to allow a solid running arrangement to be automatically established post fault. | 31/10/2022
Coylton 275kV Greener Grid Park | PRO-001551 | CS-04304 | COYLTON ENERGY LIMITED | Coylton 275/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/05/2025
|  | CS-09433 | COYLTON ENERGY LIMITED | Coylton 275/33kV Substation | Coylton 275kV H1 | At Coylton 275kV substation it is required to install a new 275kV disconnector | 30/05/2025
CPG Power | PRO-000542 | CS-05598 | ESB ASSET DEVELOPMENT UK LIMITED | Carrington 400KV Substation | 100348-200832 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to Disconnecting Circuit Breaker (to be confirmed at the detailed design stage). 3. Install 40kA DCB to connection assets for the User’s connection. | 30/06/2026
Craiginmoddie Wind Farm | PRO-003829 | CS-09787 | ENERGYFARM UK CRAIGINMODDIE LLP | Maybole 132/33KV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/09/2031
|  | CS-09788 | ENERGYFARM UK CRAIGINMODDIE LLP | Maybole 132/33KV Substation | SPT-RI-3062 - Coylton to Maybole 132kV Circuit Uprating | To accommodate the generation at Maybole GSP it is proposed to rebuild the route between Coylton and Maybole with a steel tower L7 route utilising twin UPAS conductor. The tee off circuit to Kilmarnock South will also be replaced with a new steel tower L7 route utilising single UPAS conductor on each side of the tower. The conductors will be tied together however such that the tee off connection is rated to the capacity as the Coylton to Maybole circuit. | 30/09/2031
|  | CS-09789 | ENERGYFARM UK CRAIGINMODDIE LLP | Maybole 132/33KV Substation | SPT-RI-3063 - Coylton SGT3 and Associated 132kV Circuit Breakers | The installation of SGT3 will require a the 275kV busbars at Coylton to be extended and a new 275kV circuit breaker and associated disconnector to be installed. The nameplate rating of the SGT will be 240MVA which is in line with the other two installed units at Colyton. From here a 132kV circuit breaker shall be installed connecting to a 132kV cable circuit which shall connect into the existing 132kV busbar arrangement via a second 132kV circuit breaker. As well as the new SGT and the associated 275kV and 132kV switchgear a second 132kV bus section circuit breaker is required to split the 132kV busbar up and limit the risk associated with a 132kV busbar fault. | 30/09/2031
|  | CS-09790 | ENERGYFARM UK CRAIGINMODDIE LLP | Maybole 132/33KV Substation | SPT-RI-3533 - Maybole to Craiginmoddie Tee 132kV OHL | To co-ordinate the connection of new wind farms located near the town of Maybole in the South West of Scotland it is proposed to establish a shared 132kV overhead line between Maybole 132kV substation and to a “Craiginmoddie Tee” location, approximately 5km south of Maybole 132kV substation. The installation of a new 132kV feeder bay at Maybole 132kV is required to facilitate the OHL connection. | 30/09/2031
Craig Moss Farm | PRO-003498 | CS-08441 | Greenswitch Capital Limited | Craig Moss Farm 132kV substation | Craig Moss H1 Cable | At Craig Moss Farm 132kV substation install a new 132kV line disconnector | 31/10/2036
|  | CS-08438 | Greenswitch Capital Limited | Craig Moss Farm 132kV substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 31/10/2036
|  | CS-08439 | Greenswitch Capital Limited | Craig Moss Farm 132kV substation | Craig Moss H1 OHL | Construct a new 132kV circuit between Dumfries North 400kV substation and Craig Moss Farm 132kV substation. From the desktop assessment carried out this circuit shall be comprised of an approximately 6km L4 132kV steel tower route and a 1.2km 132kV cable circuit. | 31/10/2036
|  | CS-08437 | Greenswitch Capital Limited | Craig Moss Farm 132kV substation | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 31/10/2036
|  | CS-08440 | Greenswitch Capital Limited | Craig Moss Farm 132kV substation | Craig Moss H1 SS | 1. Install a 400kV double busbar bay at Dumfries North 400/132kV substation 2. Install a 400/132kV 360MVA transformer at Dumfries North 400/132kV substation 3. Install a 132kV circuit breaker bay at Dumfries North 400/132kV substation | 31/10/2036
Craig Watch Wind Farm | PRO-001877 | CS-05436 | Craig Watch Wind Farm Limited | Craig Watch Substation | SHET-RI-176 | Pauls Hill/Glenfarclas Circuit Turn In - Move the existing open point from Keith 132kV Substation to Pauls Hill substation and then turn in the Pauls Hill/Glenfarclas circuit to Blackhillock 132kV Substation andrebuild the circuit from Blackhillock substation to Craig watch Substation. This will include the Tee connection onto the existing circuit. (SHET-RI-176 | 30/06/2028
|  | CS-05437 | Craig Watch Wind Farm Limited | Craig Watch Substation | SHET-RI-079 (a & b) | Blackhillock Additional SGTs- Reinforce the transmission network at Blackhillock substation by installing two additional new 275/132kV Supergrid Transformers. The transformers are to be rated at 360MVA. The SGTs will be connected to the existing 275kV AIS double busbar and 132kV GIS double busbar at Blackhillock. Two new 275kV AIS transformer circuit breaker bays and two new GIS transformer circuit breaker bays will also be required (SHET-RI-079 (a & b)). | 30/06/2028
|  | CS-05438 | Craig Watch Wind Farm Limited | Craig Watch Substation | 0 | 0 | 30/06/2028
Creag Riabhach Wind Farm | PRO-000109 | CS-05603 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 31/07/2027
|  | CS-05604 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | SHET-RI-052 - Lairg – Loch Buidhe 132kV Reinforcement | Establish a new 132kV double busbar at Lairg (Dalchork substation) and construct approximately 17km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. | 31/07/2027
|  | CS-05605 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 31/07/2027
|  | CS-05599 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 31/07/2027
|  | CS-05600 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 31/07/2027
|  | CS-05601 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | Creag Riabhach item 1 | At the new Dalchork 132kV grid substation install a new 132kV double busbar feeder bay complete with 2 x 132kV busbar selection switches (304 and 306), 1 x 132kV circuit breaker (305), 1 x 132kV line disconnector (303) and associated protection equipment. | 31/07/2027
|  | CS-05602 | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | Creag Riabhach Item 2 | Construct a new 22km 132kV radial circuit (comprising 20.6km of 132kV overhead wood pole line and 1.4km of 132kV underground cable) from Dalchork 132kV substation, terminating on a new 132kV line disconnector (203) installed at the Creag Riabhach 132kV substation location. | 31/07/2027
CREYKE BECK | PRO-001972 | CS-07572 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101890-203837 | Extend new Creyke Beck 400kV Substation to make provision for the connection of user bay | 31/05/2033
|  | CS-07573 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 31/05/2033
|  | CS-07574 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 31/05/2033
|  | CS-07581 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101553-203094 | The existing A408 Cottam – Staythorpe 1 400kV circuit will be turned in and out of new High Marnham 400kV substation to create a new Cottam – High Marnham & High Marnham – Staythorpe 400kV circuits. Circuits to be reconductored to achieve a minimum winter post fault rating of 3300MVA. | 31/05/2033
|  | CS-07575 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 31/05/2033
|  | CS-07576 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 31/05/2033
|  | CS-07579 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 31/05/2033
|  | CS-07582 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101593-101593 | Uprate the Cottam- Staythorpe circuit 1, to provide winter post fault rating of 3300MVA This includes the cable section. | 31/05/2033
|  | CS-07584 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 31/05/2033
|  | CS-07577 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100455-201020 | 1. Transpose the Cottam 1 circuit with the West Burton 1 circuit at Keadby 400kV substation. 2. Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby – Thorpe Marsh 400 kV circuit | 31/05/2033
|  | CS-07583 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 31/05/2033
|  | CS-07578 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 0333496-0333496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 31/05/2033
|  | CS-07580 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 31/05/2033
|  | CS-07585 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100450-201015 | Uprate the Cottam - Keadby 1 and 2 circuits to achieve a post fault winter rating of 3300MVA. | 31/05/2033
|  | CS-07586 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 100449-201014 | Uprate the Drax – Eggbrough 1 circuit to achieve a post fault summer rating of 2500MVA | 31/05/2033
|  | CS-07587 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 031380-031380 | Hotwire the 4x400mm2 sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 31/05/2033
|  | CS-07589 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 101968-204091 | Turn-in of both Creyke Beck - Thornton 1 & 2 circuits into a new 400kV AIS double busbar substation (Creyke Beck North) with 4 OHL feeder bays, 2 bus coupler bays and 1 bus section bay | 31/05/2033
|  | CS-07588 | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation | 033837-201650 | Replace breaker X110 at Existing New Creyke Beck 400kV Substation to 63KA with higher X/R ratio | 31/05/2033
Creyke Beck Bulk PP | PRO-002712 | CS-08433 | NORTHERN POWERGRID (YORKSHIRE) PLC | Creyke Beck 132kV | 102675-205361 | Construct a new 400kV double busbar substation including all necessary works required to connect it to the Main Interconnected Transmission System. | 31/10/2034
Cruachan Expansion | PRO-001889 | CS-06835 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SPT-RI-2321 | Cruachan to Dalmally 275kV circuits uprate - Uprate the overhead line circuits No.1 and No.2 between Cruachan and Dalmally 275kV substations (YX Route) by re-profiling of the existing conductors twin Totara from 39°C to 50°C will be required. (SPT-RI-2321) | 31/10/2030
|  | CS-06836 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 31/10/2030
|  | CS-06837 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SPT-RI-028 | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | 31/10/2030
|  | CS-06838 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2030
|  | CS-06839 | Drax Cruachan Expansion Limited | Cruachan 275kV Substation | SHET-RI-034 | Inverarnan 132kV QBs - Install 2 x 132kV 240MVA QBs at Inverarnan substation in series with the two 275/132kV SGTs connected to the Dalmally – Windyhill 275kV line. (SHET-RI-034) | 31/10/2030
Cruach Glenamachrie Wind Farm | PRO-002369 | CS-08167 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-046 | Taynuilt – North Argyll Reinforcement - Reinforce the transmission network between Taynuilt and North Argyll substation (established as part of SHET-RI-013). Rebuild approximately 12.5km of existing 132kV double circuit steel tower line between Creag Dhubh and Taynuilt with a heavy duty 132kV | 31/10/2034
|  | CS-08168 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2034
|  | CS-08170 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2034
|  | CS-08171 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 31/10/2034
|  | CS-08169 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 31/10/2034
|  | CS-08166 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2034
|  | CS-08172 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 31/10/2034
|  | CS-08173 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bipole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 31/10/2034
|  | CS-08174 | VOLTALIA UK LTD | Taynuilt GSP | SHET-RI-198 | Beinn Glass Tee 132kV Switching Station - Construct a new 132kV switching station at the site where the Beinn Glass 132kV circuit tees into the Taynuilt to Creag Dhubh 132kV tower line. At the new switching station, install a new 132kV line circuit breaker and associated disconnectors, protection panels, battery systems et | 31/10/2034
|  | CS-08175 | VOLTALIA UK LTD | Taynuilt GSP | SPT-RI-028 | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | 31/10/2034
Cryogenic Battery System (Synchronous) | PRO-000549 | CS-04951 | CRYOBATTERY ONE LIMITED | Carrington 400KV Substation | 101012-202029 | 1. Modifications to the busbar protection scheme and SCS database changes at Carrington 400kV substation. | 31/10/2024
|  | CS-04952 | CRYOBATTERY ONE LIMITED | Carrington 400KV Substation | 033285-033285 | 1. Re-conductor the Carrington 400kV to Daines 400kV 4 circuit (~2km) with 2x 620mm² GZTACSR gap type conductor at 170ºC. 2. Installation of a System to Generator intertrip scheme. | 31/10/2024
|  | CS-04953 | CRYOBATTERY ONE LIMITED | Carrington 400KV Substation | 033285-033567 | Rephasing of the Carrington – Penwortham circuit. | 31/10/2024
CS14 | PRO-003548 | CS-08500 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 102036-204192 | Infrastructure works for the generation connection of Fred Olson CS14 offshore wind farm | 31/10/2031
|  | CS-08504 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 31/10/2031
|  | CS-08507 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to triple Auriacuria 3 x 700mm2 at 90 degrees to achieve a summer pre-fault rating of 3000MVA | 31/10/2031
|  | CS-08505 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-08501 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 31/10/2031
|  | CS-08503 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 31/10/2031
|  | CS-08502 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 31/10/2031
|  | CS-08506 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 31/10/2031
CS4 | PRO-002239 | CS-08100 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 31/10/2031
|  | CS-08101 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 31/10/2031
|  | CS-08099 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 31/10/2031
|  | CS-08102 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 31/10/2031
|  | CS-08103 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-08104 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 31/10/2031
|  | CS-08105 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 31/10/2031
|  | CS-08098 | FRED OLSEN SEAWIND LIMITED | Alverdiscott 400kV Substation | 102035-204191 | 0 | 31/10/2031
Culham Storage | PRO-001946 | CS-07459 | STATERA ENERGY LIMITED | Culham Jet 400kV Substation | 101839-203775 | Extension of the 400kV Busbar at Culham Jet 400kV Substation to allow for the connection of a new User bay | 29/10/2027
|  | CS-07460 | STATERA ENERGY LIMITED | Culham Jet 400kV Substation | 101839-203776 | Connecting the 2nd circuit from Cowley to Didcot into Culham Jet 400kV substation | 29/10/2027
|  | CS-07461 | STATERA ENERGY LIMITED | Culham Jet 400kV Substation | 020903-020903 | Uprating of the Cowley-Walham / Cowley Minety 400kV circuit cables to achieve 1900MVA post-fault summer rating | 29/10/2027
Culraven Solar Farm | PRO-001294 | CS-04260 | SP Distribution plc | Tongland GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/11/2025
|  | CS-04261 | SP Distribution plc | Tongland GSP | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/11/2025
|  | CS-04262 | SP Distribution plc | Tongland GSP | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 30/11/2025
|  | CS-04263 | SP Distribution plc | Tongland GSP | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 30/11/2025
|  | CS-04264 | SP Distribution plc | Tongland GSP | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 30/11/2025
|  | CS-04265 | SP Distribution plc | Tongland GSP | SPT-RI-170 | Tongland 132/33kV GSP Reinforcement | 30/11/2025
Cumberhead | PRO-000114 | CS-05612 | CUMBERHEAD WIND ENERGY LIMITED | Cumberhead West GSP | SPT-RI-187 - Coalburn - Galawhistle Collector CABLE 132kV Circuit | Coalburn – Galawhistle Collector SS 132kV Circuit: New 132kV bays will be constructed at Coalburn and Galawhistle Collector Substations, and the associated civil works including a control building at Galawhistle Collector Substation. A 132kV underground cable circuit will be established between Coalburn 400/132kV substation and Galawhistle Wind Farm Collector Substation. | 31/08/2022
|  | CS-05613 | CUMBERHEAD WIND ENERGY LIMITED | Cumberhead West GSP | SPT-RI-218 Coalburn 132kV Bus Coupler Auto-Close Scheme | An auto-close scheme will be installed at Coalburn 132kV substation, to close CB 1030 if either of the two supergrid transformers, supplying the coupled MAIN 1 or RESERVE 132kV busbars, is disconnected due to an unplanned outage. | 31/08/2022
|  | CS-05614 | CUMBERHEAD WIND ENERGY LIMITED | Cumberhead West GSP | Cumberhead Item 1 | Establish a 132kV substation at the Cumberhead Wind Farm site. | 31/08/2022
|  | CS-05615 | CUMBERHEAD WIND ENERGY LIMITED | Cumberhead West GSP | Cumberhead Item 2 | Installation of a 132kV line disconnector and 132kV busbar. | 31/08/2022
|  | CS-05616 | CUMBERHEAD WIND ENERGY LIMITED | Cumberhead West GSP | Cumberhead Item 3 | Install 0.4km of 1600mm2 Al XLPE cable to loop in to the Coalburn – Galawhistle Collector substation circuit. | 31/08/2022
|  | CS-05617 | CUMBERHEAD WIND ENERGY LIMITED | Cumberhead West GSP | SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 31/08/2022
|  | CS-05618 | CUMBERHEAD WIND ENERGY LIMITED | Cumberhead West GSP | Cumberhead Item 4 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 31/08/2022
|  | CS-05619 | CUMBERHEAD WIND ENERGY LIMITED | Cumberhead West GSP | SPT-RI-180 | Coalburn SGTx Overload Protection Scheme: An overload protection scheme will be installed at Coalburn 400/132kV substation such that if SGT1 or SGT2 is overloaded, a trip signal will be issued to SPD at Linnmill GSP, and/or to SPT generation connected directly to Coalburn 132kV substation, to disconnect the appropriate generators to remove the overload. Following completion of Coalburn SGT3 (SPT-RI-144), this transformer will be added to the overload scheme proposed in this TORI (SPT-RI-180). | 31/08/2022
|  | CS-03699 | CUMBERHEAD WIND ENERGY LIMITED | Cumberhead West GSP | SPT-RI-238 - Cumberhead WF 132kV Collector substation | The collector substation will require the installation of a 132kV busbar section with two line disconnectors and short sections of underground cable (~0.2km each) to connect into the existing Coalburn to Galawhistle 132kV underground cable. From the 132kV busbar section a 132kV circuit breaker, with associated disconnectors, will be installed and connected to a 132/33kV 120MVA transformer with a shared 33kV busbar section. The works to establish this collector substation will include the construction of the substation platform as well as a control building to house SPT’s protection and control equipment. | 31/08/2022
Cumberhead West Wind Farm | PRO-000423 | CS-05620 | CUMBERHEAD WEST WIND FARM LTD. | Cumberhead West GSP | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 01/11/2024
|  | CS-05621 | CUMBERHEAD WEST WIND FARM LTD. | Cumberhead West GSP | SPT-RI-218 Coalburn 132kV Bus Coupler Auto-Close Scheme | An auto-close scheme will be installed at Coalburn 132kV substation, to close CB 1030 if either of the two supergrid transformers, supplying the coupled MAIN 1 or RESERVE 132kV busbars, is disconnected due to an unplanned outage. | 01/11/2024
|  | CS-05622 | CUMBERHEAD WEST WIND FARM LTD. | Cumberhead West GSP | SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 01/11/2024
Cygnus Offshore Windfarm | PRO-001530 | CS-06477 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-06478 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-06479 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-06480 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-06481 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-06482 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-06483 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-06468 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | Cygnus Item 1 | At New Deer 2 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Relevant Transmission Licensee and the User (as OTSDUW User) will be the User side of the 400kV feeder circuit breakers/isolators at New Deer 2 400kV substation. | 31/10/2033
|  | CS-06469 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-06470 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-06471 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 31/10/2033
|  | CS-06472 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-06473 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-06474 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-06475 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-06476 | RENANTIS UK LIMITED | Cygnus 220/66kV Offshore Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2033
Daer Wind Farm | PRO-000565 | CS-04275 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Daer Wind Farm Substation | SPT-RI-306 - Moffat 132kV Fault Level Mitigation Bus Section Circuit Breaker | Moffat 132kV substation existing compound extension to accommodate the connection of further generation into the site. The compound shall be extended with the existing 132kV busbars being extended into this area. The installation of a new 132kV bus section circuit breaker will be required in order to alleviate exceeding the fault level design limits at the site. | 14/07/2027
|  | CS-04276 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Daer Wind Farm Substation | Daer Wind Farm H1 Works 2 | Installation of a 12km 132kV circuit between Daer Wind Farm substation and Moffat 132kV substation. Indicative desktop studies show a 6km 132kV OHL circuit of trident construction using AAAC “Sycamore” conductor from the wind farm substation to a suitable termination point. From here a further 6km of 132kV underground cable will be installed to Moffat 132kV substation. | 14/07/2027
|  | CS-04277 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Daer Wind Farm Substation | Daer Wind Farm H1 Works 1 | Installation of a 132kV line disconnector at Daer Wind Farm substation | 14/07/2027
|  | CS-04278 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Daer Wind Farm Substation | SPT-RI-229 - Moffat SGT3 | A new 400/132kV 240MVA transformer, and associated 400kV and 132kV circuit breaker bays, shall be installed at Moffat 400/132kV substation to increase the available generation capacity at the 132kV substation. | 14/07/2027
|  | CS-04279 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Daer Wind Farm Substation | Daer Wind Farm H1 Works 3 | Daer Wind Farm 132kV Double busbar feeder bay at Moffat 132kV substation | 14/07/2027
Daines BESS | PRO-002050 | CS-07601 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x780mm2 conductor or equivalent and uprating of the cable section of the circuit | 01/11/2029
|  | CS-07605 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 01/11/2029
|  | CS-07591 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101938-203973 | At Carrington 400kV: 1. Installation of a 2000MVA 80hm series reactor | 01/11/2029
|  | CS-07596 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with new 2750MVA unit. | 01/11/2029
|  | CS-07593 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 01/11/2029
|  | CS-07594 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101468-202908 | Reconductor the Daines – Macclesfield 400kV with 2x780mm2 conductor | 01/11/2029
|  | CS-07595 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101948-204012 | 1. Installation of a System to generator scheme to monitor transmission Routes between Daines to Drakelow, Connahs Quay to Ironbridge, and Ironbridge – Rugeley/Feckenham | 01/11/2029
|  | CS-07597 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor | 01/11/2029
|  | CS-07598 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor | 01/11/2029
|  | CS-07603 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm2 conductor | 01/11/2029
|  | CS-07600 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 400kV circuits and the Cellarhead – Macclesfield and Cellarhead – Daines 400kV circuits | 01/11/2029
|  | CS-07602 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101468-202908 | Reconductor the Daines – Macclesfield 400kV with 2x780mm2 conductor | 01/11/2029
|  | CS-07604 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 100425-200971 | Reconductor the Feckenham – Ironbridge 400kV circuit with 2x620mm2 conductor | 01/11/2029
|  | CS-07606 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 01/11/2029
|  | CS-07607 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 100478-201049 | 1. Reconductor the 2x500mm2 and 2x570mm2 sections of the Drakelow – Willington East 400kV circuit with 2x 620mm2 GAP conductor | 01/11/2029
|  | CS-07608 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101939-203974 | 1. Recondcutor the Drakelow – Rugeley 400kV circuit with 2x620mm2 conductor GZTACCSR conductor or equivalent | 01/11/2029
|  | CS-07609 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101943-203988 | 1. Hotwire the 2x500mm2 conductor of the Drakelow – Ratcliffe on Soar 400kV circuit to an operating temperature of 90 degrees | 01/11/2029
|  | CS-07610 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101697-203383 | Hotwire the 2x400mm2 conductor on the Bredbury – South Manchester circuits | 01/11/2029
|  | CS-07590 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101929-203942 | At Daines 400kV Substation 1. Extension of Main and Reserve busbar X to facilitate connection of Users generator circuit 2. Extension of the busbar protection scheme and database changes as required | 01/11/2029
|  | CS-07592 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101561-203105 | Uprate the cables sections on: 1) Rochdale – Whitegate 2 275kV circuit 2) Kearsley – Whitegate 1 and 2 275kV circuits | 01/11/2029
|  | CS-07599 | SSE UTILITY SOLUTIONS LIMITED | Daines 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 01/11/2029
Daines Green Energy Centre | PRO-001902 | CS-07134 | INNOVA RENEWABLES LIMITED | Daines 400kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor | 30/10/2028
|  | CS-07135 | INNOVA RENEWABLES LIMITED | Daines 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 30/10/2028
|  | CS-07136 | INNOVA RENEWABLES LIMITED | Daines 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 400kV circuits and the Cellarhead – Macclesfield and Cellarhead – Daines 400kV circuits | 30/10/2028
|  | CS-07137 | INNOVA RENEWABLES LIMITED | Daines 400kV Substation | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x780mm2 conductor or equivalent and uprating of the cable section of the circuit | 30/10/2028
|  | CS-07129 | INNOVA RENEWABLES LIMITED | Daines 400kV Substation | 101727 - 203436 | Extend the Main and Reserve Busbar 1 to make provision for connection of generator bay (User Works). | 30/10/2028
|  | CS-07130 | INNOVA RENEWABLES LIMITED | Daines 400kV Substation | 101683-203351 | Hotwire the 2x400mm2 conductor on the Carrington – South 1 & 2 circuits to an operating temperature of 65°C | 30/10/2028
|  | CS-07131 | INNOVA RENEWABLES LIMITED | Daines 400kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 30/10/2028
|  | CS-07132 | INNOVA RENEWABLES LIMITED | Daines 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with new 2750MVA unit. | 30/10/2028
|  | CS-07133 | INNOVA RENEWABLES LIMITED | Daines 400kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor | 30/10/2028
Dalchork Farm | PRO-002807 | CS-09386 | Greenswitch Capital Limited | Dalchork Substation 132 kV | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/10/2032
|  | CS-09387 | Greenswitch Capital Limited | Dalchork Substation 132 kV | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2032
|  | CS-09389 | Greenswitch Capital Limited | Dalchork Substation 132 kV | SHET-RI-230 | Loch Buidhe – Dalchork 132 kV Reinforcement- Construction of approximately 17 km 132 kV double circuit between Dalchork - Loch Buidhe substations with same rating OHLs as of existing double circuit i.e. 414 MVA post fault summer ratings. Scope also includes construction of two feeder bays each at Dalchork substation and Loch Buidhe substation | 31/10/2032
|  | CS-09388 | Greenswitch Capital Limited | Dalchork Substation 132 kV | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2032
Dalmarnock Storage BESS | PRO-003737 | CS-09677 | DALMARNOCK STORAGE LTD | Dalmarnock 132 kV Substation | Line Disconnector - Dalmarnock Storage | Installation of 132kV line disconnector | 30/04/2030
|  | CS-09676 | DALMARNOCK STORAGE LTD | Dalmarnock 132 kV Substation | SPT-RI-3320 | Gresham House Dalmarnock BESS Collector & YF013 Tee In – In order to accommodate connections in this area, it is proposed to establish a collector substation at the existing Gresham House Dalmarnock BESS substation | 30/04/2030
|  | CS-09675 | DALMARNOCK STORAGE LTD | Dalmarnock 132 kV Substation | SPT-RI-2957 | Dalmarnock SGT1 & Charlotte Street 1 DCBs – To comply with SQSS circuit complexity as per Appendix B and accommodate a new generation and demand connection within the Dalmarnock area of the network, there is a requirement to replace the H13A disconnector at Dalmarnock 275/132kV substation with a DCB. Additionally, there is also a requirement to replace the H13B disconnector at Dalmarnock 275/132kV substation with a DCB | 30/04/2030
Damhead Creek 2 | PRO-001056 | CS-05625 | VPI POWER LIMITED | Kingsnorth 400kV Substation | 020622-031444 | 0 | 31/08/2025
Dealanach WLC WF | PRO-001722 | CS-07172 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 15/12/2026
|  | CS-07173 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-230 | It is proposed to reconductor approximately 36km of the 132kV overhead line existing Gretna to Hawick circuit (AL and V Route), between Gretna and the proposed Faw Side Community Wind Farm ‘T’ connection. It is proposed to utilise LARK HTLS conductor. NGET own a section of AL and V Route on this circuit and will have to reinforce to match the SPT proposals. | 15/12/2026
|  | CS-07174 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 15/12/2026
|  | CS-07175 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-294 | Ewe Hill to Hopsrig collector substations 132kV circuit | 15/12/2026
|  | CS-07176 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-2159 | Hopsrig Substation Grid T1A Transformer - A new 132/33kV 60MVA transformer will be installed at Hopsrig collector substation. This will create a new 33kV busbar to allow new generators to connect. (SPT-RI-2159) | 15/12/2026
|  | CS-07170 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-191 | The thermal capacity of the 132kV circuit between Gretna 132kV substation and Ewe Hill Wind Farm 132kV Collector Substation (works detailed in SPT-RI-017), will be increased by re-conductoring the 132kV overhead line utilising “Lark” High Temperature Low Sag (HTLS) conductor (~16km), and installing an additional 800mm2 Al XLPE 132kV underground cable in parallel with the existing cable(~0.3km), to give a minimum summer continuous rating of 224MVA. This is to accommodate additional generation connecting at the Ewe Hill Wind Farm 132kV Collector Substation. | 15/12/2026
|  | CS-07171 | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 15/12/2026
Dell Wind Farm | PRO-001012 | CS-05626 | DELL WIND FARM LIMITED | Dell 132kV Substation | SHET-RI-085b | 3. Melgarve 400/132kV Substation – Establish a new 400/132 kV Substation at Melgarve, to allow the connection of wind generation in the area. (SHET-RI-085b) | 30/04/2026
|  | CS-05627 | DELL WIND FARM LIMITED | Dell 132kV Substation | SHET-RI-069 | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | 30/04/2026
Derwent Solar PV Array | PRO-001648 | CS-05417 | ANESCO LIMITED | Thornton 400kV Substation | 101559-203102 | At Thornton 400kV substation extend busbars to make provision for connection of the User’s generator bay | 31/05/2032
|  | CS-05418 | ANESCO LIMITED | Thornton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph 400kV circuit with 2x620mm2 GZTACSR conductor | 31/05/2032
|  | CS-05419 | ANESCO LIMITED | Thornton 400kV Substation | 101552-203093 | At Thornton 400kV substation replace circuit breaker X805 with a new 63kA-rated circuit breaker with a X/R ratio of at least 24 At Thornton 400kV substation replace circuit breaker X230 with a new 63kA-rated circuit breaker with a X/R ratio of at least 24 | 31/05/2032
|  | CS-05420 | ANESCO LIMITED | Thornton 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 31/05/2032
|  | CS-05421 | ANESCO LIMITED | Thornton 400kV Substation | 101554-203095 | Reconductor the new High Marham - Staythorpe 400 kV circuit with 2x620mm2 GZTACSR conductor | 31/05/2032
|  | CS-05422 | ANESCO LIMITED | Thornton 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 31/05/2032
|  | CS-05423 | ANESCO LIMITED | Thornton 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 31/05/2032
|  | CS-05424 | ANESCO LIMITED | Thornton 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm2 conductor | 31/05/2032
|  | CS-05425 | ANESCO LIMITED | Thornton 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 31/05/2032
|  | CS-05426 | ANESCO LIMITED | Thornton 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 31/05/2032
|  | CS-05427 | ANESCO LIMITED | Thornton 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 31/05/2032
|  | CS-05428 | ANESCO LIMITED | Thornton 400kV Substation | 033754-033755 | Establish a new 400kV double circuit connecting to the Norton – Osbaldwick 400kV double circuit to Poppleton including all associated substation works | 31/05/2032
|  | CS-05429 | ANESCO LIMITED | Thornton 400kV Substation | 100449-201014 | Installation of a power electronics-based power flow control device on the Drax – Eggborough 400kV circuit 1 | 31/05/2032
|  | CS-05430 | ANESCO LIMITED | Thornton 400kV Substation | 101625-203259 | On the Drax – Eggborough 2 circuit, hotwire the 4x400mm2 conductor for an operating temperature of 75°C | 31/05/2032
|  | CS-05431 | ANESCO LIMITED | Thornton 400kV Substation | 100452-201017 | At Drax 400kV substation replace circuit breakers X120, X130, X220 and X330 with a tested X/R ratio of at least 28 and a peak withstand capability of at least 2.7 x RMS break | 31/05/2032
|  | CS-05432 | ANESCO LIMITED | Thornton 400kV Substation | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 31/05/2032
Deuchries Extension | PRO-000654 | CS-05628 | Scottish Hydro Electric Power Distribution Plc | Keith GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 01/10/2021
|  | CS-05629 | Scottish Hydro Electric Power Distribution Plc | Keith GSP | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 01/10/2021
Devol Moor Battery & Solar Project | PRO-004084 | CS-09311 | RELAY HOLDCO LIMITED | Devol Moor 400kV | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 17/10/2029
|  | CS-09312 | RELAY HOLDCO LIMITED | Devol Moor 400kV | SPT-RI-2833 | Devol Moor 400kV GIS Substation - At Devol Moor 400kV it is proposed to establish a new indoor GIS Double Busbar substation. The building is proposed to be sized to accommodate 14 bays. The initial GIS substation assets to be installed include the followings (subject to review):  5x 400kV Feeder Bays and associated switchgear; SGT1, SGT2, HUNE, WIYH and High Mathernock BESS  1x 400kV Bus Coupler  1x 400kV Bus Section  Space to be included with building to accommodate future connections  Removal of redundant equipment at existing 400kV Devol Moor substation. | 17/10/2029
|  | CS-09310 | RELAY HOLDCO LIMITED | Devol Moor 400kV | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 17/10/2029
Dewshill Windfarm | PRO-004115 | CS-09317 | SP Distribution plc | Newarthill GSP | Dewshill Sole Enabling Works | Asset Replacement (Newarthill Fault Level Mitigation) - A bus section reactor will be installed on the SPT side of the GSP, with two new 3-panel 33kV switchboards. | 30/04/2026
Didcot Road | PRO-002336 | CS-08685 | ARLINGTON ENERGY (DEVELOPMENT) LIMITED | Didcot 400kV Substation | 102220-204485 | To extend the busbar & construct an additional bay including all necessary equipment at Didcot 400kV main busbar for accommodating user to the connect at Didcot 400kV substation. | 31/10/2027
|  | CS-08688 | ARLINGTON ENERGY (DEVELOPMENT) LIMITED | Didcot 400kV Substation | 101065-202138 | Uprate A83A & A873 Melksham – Minety 1 & 2 400kV circuits 28km, 2x500mm2 Rubus at 85oC on L2 towers with summer pre-fault rating of 1568MVA by reconductoring with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 31/10/2027
|  | CS-08689 | ARLINGTON ENERGY (DEVELOPMENT) LIMITED | Didcot 400kV Substation | 101051-202109 | Uprate A861 Walham-Cowley (future Walham-Botley West & Botley West – Cowley) 400kV circuit overhead line sections by reconductoring the 19.2km, 2x500mm2 Rubus at 75oC on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 61.7km, 4x400mm2 Zebra conductor at 50oC on L6 towers with summer prefault rating of 1862MVA to 75oC to achieve a summer pre-fault rating of 2500MVA | 31/10/2027
|  | CS-08686 | ARLINGTON ENERGY (DEVELOPMENT) LIMITED | Didcot 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 31/10/2027
|  | CS-08687 | ARLINGTON ENERGY (DEVELOPMENT) LIMITED | Didcot 400kV Substation | 100424-200970 | Uprate the Bramley - Melksham 1 & 2 400kV circuits (81.6km, 2 x 400mm2 zebra conductor at 50oC on L2 towers with summer prefault rating of 931MVA) by reconductoring with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 31/10/2027
Dogger Bank Project 4 (Dogger Bank B) | PRO-000410 | CS-05632 | DOGGERBANK OFFSHORE WIND FARM PROJECT 2 PROJCO LIMITED | Dogger Bank 220kV Offshores | NGET-RI-31569 | Extend Creyke Beck 400kV Substation to make available a single skeletal generator bay for the Relevant Transmission Licensee at the Interface, assuming a single offshore transmission circuit. | 01/04/2024
Dogger Bank Project A | PRO-000411 | CS-04957 | DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank 220kV Offshores | 031570-031570 | Generation connection for Doggerbank P2 at Lackenby 400kV substation. Extension to the existing GIS building at the Lackenby substation to enable the connection of the Doggerbank connection bay. Transition bay from Alstom T155 and provision of skeleton bay including BB protection etc | 01/04/2023
|  | CS-04960 | DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank 220kV Offshores | 101243-202472 | Extension of the existing OTS at Lackenby 400kV substation for the connection of new generators | 01/04/2023
|  | CS-04961 | DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank 220kV Offshores | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 01/04/2023
|  | CS-04962 | DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank 220kV Offshores | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm2 conductor | 01/04/2023
|  | CS-04963 | DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank 220kV Offshores | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm2 AAAC sections of the circuits with 2×591mm2 ACCR conductor and the 2x700mm2 AAAC sections with 3x700mm2 AAAC conductor | 01/04/2023
|  | CS-05630 | DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank 220kV Offshores | NGET-RI-030543 | Extend Creyke Beck 400kV Substation to make available a single skeletal OFTO bay for the Relevant Transmission Licensee at the Interface Point. | 01/04/2023
Dogger Bank Project C | PRO-000409 | CS-05631 | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby GSP | 031570-031570 | Generation connection for Doggerbank P2 at Lackenby 400kV substation. Extension to the existing GIS building at the Lackenby substation to enable the connection of the Doggerbank connection bay. Transition bay from Alstom T155 and provision of skeleton bay including BB protection etc | 01/04/2025
|  | CS-07023 | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby GSP | 101243-202472 | Extension of the existing OTS at Lackenby 400kV substation for the connection of new generators | 01/04/2025
|  | CS-07024 | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby GSP | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 01/04/2025
|  | CS-07025 | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby GSP | 100821-201659 | Uprating of the Creyke Beck - Humber Refinery – Keadby and Creyke Beck - Keadby – Killingholme 4ZQ circuits to achieve a post-fault summer rating of 3320MVA | 01/04/2025
|  | CS-07026 | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby GSP | 100450-201015 | Hotwire the 4x400mm2 sections of the Cottam - Keadby 1 and 2 circuits to an operating temperature of 75°C and reconductor the 2x500mm2 AAAC sections of the circuits with 2×620mm2 GZTACSR conductor to achieve a post fault winter rating of 3400MVA. | 01/04/2025
Dogger Bank South West (was Irish Sea) | PRO-001386 | CS-04347 | RWE RENEWABLES UK LIMITED | Wylfa 400kV Substation | 101020-202043 | Infrastructure works at Wylfa 400kV substation necessary to connect 1500MW or the RWE R4 offshore wind project. | 01/04/2033
|  | CS-04348 | RWE RENEWABLES UK LIMITED | Wylfa 400kV Substation | 100974-201953 | Construct a second double circuit between Pentir 400kV substation and the Wylfa 400kV substation (circuits No. 3 and 4) | 01/04/2033
|  | CS-04349 | RWE RENEWABLES UK LIMITED | Wylfa 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 01/04/2033
|  | CS-04350 | RWE RENEWABLES UK LIMITED | Wylfa 400kV Substation | 101072-202151 | Extend the current Wylfa 400kV substation to enable the connection of a new Pentir - Wylfa OHL. | 01/04/2033
|  | CS-04351 | RWE RENEWABLES UK LIMITED | Wylfa 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 01/04/2033
Dog Trap Lane | PRO-001626 | CS-04954 | HD381GRE Limited | Minety 400kV Substation | 101488-202940 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new busbar 33kV substation at Minety to be connected via new 400/33kV SGT8A. 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 31/03/2025
|  | CS-04955 | HD381GRE Limited | Minety 400kV Substation | 020903-020903 | Uprating of Cowley-Minety 400kV circuit and Cowley-Minety 400kV cables to achieve 1300 MVA pre-fault Summer rating. | 31/03/2025
|  | CS-04956 | HD381GRE Limited | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 31/03/2025
Dolyfardyn | PRO-001584 | CS-04701 | Llyn Lort Energy Park Limited | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 04/02/2027
|  | CS-04710 | Llyn Lort Energy Park Limited | Chirk GSP | 101323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 04/02/2027
|  | CS-04712 | Llyn Lort Energy Park Limited | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 04/02/2027
|  | CS-04713 | Llyn Lort Energy Park Limited | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 04/02/2027
|  | CS-04714 | Llyn Lort Energy Park Limited | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 04/02/2027
Don Cossack | PRO-003875 | CS-09015 | Don Cossack Ltd | Tynemouth 275kV Substation | 100455-201020 | At Keadby 400kV substation: Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby –Thorpe Marsh 400kV circuit | 15/06/2034
|  | CS-09014 | Don Cossack Ltd | Tynemouth 275kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 15/06/2034
|  | CS-09020 | Don Cossack Ltd | Tynemouth 275kV Substation | 101504-202965 | Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit to provide a post-fault winter rating of 3820MVA: • Reconductor the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C • At Keadby 400kV substation, replace the X1005 feeder bay for the Drax – Keadby – Thorpe Marsh circuit | 15/06/2034
|  | CS-09012 | Don Cossack Ltd | Tynemouth 275kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 15/06/2034
|  | CS-09016 | Don Cossack Ltd | Tynemouth 275kV Substation | 101663-203316 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pulling mode capable of injecting up to -8 ohms along the Bicker Fen – West Burton 1 (A685) 400kV circuit | 15/06/2034
|  | CS-09017 | Don Cossack Ltd | Tynemouth 275kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 15/06/2034
|  | CS-09019 | Don Cossack Ltd | Tynemouth 275kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 15/06/2034
|  | CS-09021 | Don Cossack Ltd | Tynemouth 275kV Substation | 100450-201015 | Uprate the Cottam - Keadby 1 and 2 circuits to achieve a post fault winter rating of 3300MVA. | 15/06/2034
|  | CS-09023 | Don Cossack Ltd | Tynemouth 275kV Substation | 101386-202715 | Reconductor Lackenby –Thornton double circuit with 3 x 700mm2 at 90°C. Replace the disconnectors on both Thornton circuits at Lackenby substation, to equipment with an equal rating to provide a pre fault summer rating of 2790MVA | 15/06/2034
|  | CS-09010 | Don Cossack Ltd | Tynemouth 275kV Substation | 102394-204914 | Construction of a new 275kV double busbar substation of Tynemouth and transposition of circuits from existing single switch mesh. | 15/06/2034
|  | CS-09018 | Don Cossack Ltd | Tynemouth 275kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 15/06/2034
|  | CS-09022 | Don Cossack Ltd | Tynemouth 275kV Substation | 102178-204388 | Replacement of CB's S10, P10, W10, W20, H10 and H20 at Blyth 275kV Substation | 15/06/2034
|  | CS-09025 | Don Cossack Ltd | Tynemouth 275kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 15/06/2034
|  | CS-09009 | Don Cossack Ltd | Tynemouth 275kV Substation | 102394-204915 | Make provision for connection of generator bay at Tynemouth 275kV GIS substation. | 15/06/2034
|  | CS-09024 | Don Cossack Ltd | Tynemouth 275kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 15/06/2034
|  | CS-09011 | Don Cossack Ltd | Tynemouth 275kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 15/06/2034
|  | CS-09013 | Don Cossack Ltd | Tynemouth 275kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 15/06/2034
Dorenell Battery | PRO-000427 | CS-05573 | DORENELL WINDFARM EXTENSION LIMITED | Dorenell BESS 132KV substation | Clashindarroch Extension Item 1 | Installation of a second 132kV disconnector and a new terminal tower to replace tower 3 of the Dorenell-Blackhillock 132kV circuits, with down-leads and gantries terminating on this 132kV disconnector. | 31/10/2023
Dorenell Windfarm Extension | PRO-002415 | CS-08428 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-08417 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | Dorenell Extension Wind Farm H1 SS | Installation of 2 x new 400kV bays at ‘Blackhillock 2’, comprising line disconnectors, 2 x feeder circuit breakers and 4 x busbar selector disconnectors. Installation of 2 x 400kV line disconnectors at the User’s substation Construction of approximately 21.7km of double circuit line and cable from the User’s site to Blackhillock 2 400kV substation. The line shall comprise 20km double circuit 400kV OHL plus 0.5km and 1.2km 400kV UGC sections. Cable sections are required due to the NETS SQSS stipulation of a maximum OHL length of 20km. | 31/10/2033
|  | CS-08419 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-08420 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-08422 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-08430 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-08418 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-08424 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-08429 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-08431 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-08425 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-08427 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-08421 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-08423 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-08426 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-08432 | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation | SHET-RI-199 | Blackhillock 2 400kV Substation - Establish a new 400kV substation close to Blackhillock 400kV substation and tie in the proposed 400kV circuits as part of the NOA BBNC/BPNC upgrade. (SHETRI-199) | 31/10/2033
Douglas West Extension | PRO-000422 | CS-05641 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-268 | Coalburn to Douglas North Existing 132kV Cable Rating Enhancement | 30/06/2025
|  | CS-05637 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 30/06/2025
|  | CS-05638 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-251 | Coalburn to Douglas West 132kV Cable Reinforcement | 30/06/2025
|  | CS-05639 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 30/06/2025
|  | CS-05640 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-240 | Douglas West Wind Farm 132kV Substation | 30/06/2025
|  | CS-09786 | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm | SPT-RI-218 Coalburn 132kV Bus Coupler Auto-Close Scheme | An auto-close scheme will be installed at Coalburn 132kV substation, to close CB 1030 if either of the two supergrid transformers, supplying the coupled MAIN 1 or RESERVE 132kV busbars, is disconnected due to an unplanned outage. | 30/06/2025
Dounreay | PRO-002318 | CS-08498 | Sun4net Ltd | Dounreay 132kV Converter | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/07/2026
|  | CS-08499 | Sun4net Ltd | Dounreay 132kV Converter | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/07/2026
Doveryard Energy Centre | PRO-000765 | CS-06772 | SP Distribution plc | Kilmarnock South GSP | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 19/05/2025
|  | CS-06773 | SP Distribution plc | Kilmarnock South GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 19/05/2025
Drakelow | PRO-000428 | CS-04964 | ENSO GREEN HOLDINGS LIMITED | Drakelow 400kV Substation | 100582-201204 | 1. Install earthing transformer on 13kV tertiary connection 2. Install 13kV cable connecting earthing transformer to DCB 3. Install 72.5kV, 40kA rated DCB to connection assets for Users connection | 31/10/2024
Drakelow BESS | PRO-002033 | CS-07360 | HARMONY ENERGY LIMITED | Drakelow 132kV | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/06/2028
|  | CS-07361 | HARMONY ENERGY LIMITED | Drakelow 132kV | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/06/2028
|  | CS-07362 | HARMONY ENERGY LIMITED | Drakelow 132kV | 101467-202907 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 1820 MVA. | 30/06/2028
|  | CS-07363 | HARMONY ENERGY LIMITED | Drakelow 132kV | 101884-203860 | Reconductor the Enderby legs of both East Claydon – Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2110MVA – 2490MVA (both Will and Enderby) | 30/06/2028
|  | CS-07364 | HARMONY ENERGY LIMITED | Drakelow 132kV | 101889-203868 | 0 | 30/06/2028
|  | CS-07355 | HARMONY ENERGY LIMITED | Drakelow 132kV | 101882-203858 | 0 | 30/06/2028
|  | CS-07356 | HARMONY ENERGY LIMITED | Drakelow 132kV | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/06/2028
|  | CS-07357 | HARMONY ENERGY LIMITED | Drakelow 132kV | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/06/2028
|  | CS-07358 | HARMONY ENERGY LIMITED | Drakelow 132kV | 101329-202649 | Hotwire Enderby – Ratcliffe 400kV circuits 1 and 2 to 65 deg. C to achieve a pre-fault summer rating of 2500MVA. | 30/06/2028
|  | CS-07359 | HARMONY ENERGY LIMITED | Drakelow 132kV | 101466-202906 | Reconductor the existing 2x570mm2 conductor on the CellarheadDaines 1 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2800 MVA | 30/06/2028
Drakelow Green Energy Centre | PRO-001693 | CS-04958 | DRAKELOW GREEN ENERGY LIMITED | Drakelow 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2026
|  | CS-04959 | DRAKELOW GREEN ENERGY LIMITED | Drakelow 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2026
|  | CS-04965 | DRAKELOW GREEN ENERGY LIMITED | Drakelow 400kV Substation | 101329-202649 | Hotwire Enderby – Ratcliffe 400kV circuits 1 and 2 to 65 deg. C to achieve a pre-fault summer rating of 2260MVA. | 30/10/2026
|  | CS-04966 | DRAKELOW GREEN ENERGY LIMITED | Drakelow 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2026
|  | CS-04967 | DRAKELOW GREEN ENERGY LIMITED | Drakelow 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2026
|  | CS-04968 | DRAKELOW GREEN ENERGY LIMITED | Drakelow 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2026
|  | CS-04969 | DRAKELOW GREEN ENERGY LIMITED | Drakelow 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 1820 MVA. | 30/10/2026
|  | CS-04644 | DRAKELOW GREEN ENERGY LIMITED | Drakelow 400kV Substation | 101330-202250 | Extension of the existing Drakelow 400kV substation Main and Reserve Busbars to accommodate the User’s bay | 30/10/2026
Drax | PRO-001355 | CS-05015 | ENSO GREEN HOLDINGS D LIMITED | Drax 400kV Substation | 101056-202118 | Extend busbars at Drax 132kV Substation to accommodate new bay connection (specifics to be determined in detailed design stage) | 30/06/2025
|  | CS-05016 | ENSO GREEN HOLDINGS D LIMITED | Drax 400kV Substation | 100173-200455 | Carry out a civil infrastructure survey to evaluate the bay infrastructure ratings of the bus coupler and bus section circuit breakers (120 and130) at Drax 132kV Substation. Dependant on the outcome, reinforcement of the bay infrastructure may be required | 30/06/2025
|  | CS-05017 | ENSO GREEN HOLDINGS D LIMITED | Drax 400kV Substation | 100171-200448/ 100171-200449 | Uprate the Thorpe Marsh – West Melton 1 275kV circuit by reconductoring the circuit 2x500mm conductor operating at 90 degrees and uprating the cable sections. | 30/06/2025
Drax Solar | PRO-001759 | CS-07044 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101668-203321 | 1. Busbar extensions to provide space within M6 and R4/5/6 at Drax 400kV substation to accommodate a new HV SGT bay 2. Installation of a Section CB on the reserve bar R4/5/6. | 30/09/2029
|  | CS-07045 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101668-203322 | 1. Install and commission a new 400kV Supergrid Transformers (SGT) bay at Drax 400kV substation. 2. Install 400kV switchgear at Drax 400kV substation. This equipment will include the HV side SGT bay disconnectors and circuit breakers 3. Procure, install and commission a new 460MVA rated 400/132kV SGT 4. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. 5. Install 132kV switchgear at Drax 400kV substation on the LV side of the SGT. This equipment will include the HV side SGT bay disconnectors and circuit breaker. | 30/09/2029
|  | CS-07046 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 30/09/2029
|  | CS-07047 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 033512-033512 & 033513-033513 | Uprate the Keadby – West Burton circuits 1 and 2 to achieve a post fault summer rating of 2800MVA | 30/09/2029
|  | CS-07048 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101509-202974 | Replace the existing Ferrybridge 275kV substation with a new substation, to be built offline with circuits from the existing substation being transferred to the new substation | 30/09/2029
|  | CS-07049 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101508-202472 | Uprating/Replacement of the following CB at Monk Fryston 275kV substation:S10 and L25 | 30/09/2029
|  | CS-07050 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101504-202965 | 1. Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby –Thorpe Marsh 400kV circuit to provide a post-fault summer rating of 3300 MVA. 2. At Keadby 400kV substation, replace the X1005 feeder bay for the Drax –Keadby – Thorpe Marsh circuit. | 30/09/2029
|  | CS-07051 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101666-203319 | Uprating/Replacement of the following CBs 130 and 230 at Ferrybridge 132kV substation | 30/09/2029
|  | CS-07052 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 033754-033754 | Uprating/Replacement of the CB L45 at Monk Fryston 275kV substation | 30/09/2029
|  | CS-07053 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101661-203312 | Uprating/Replacement of the CB T10 at Monk Fryston 275kV substation | 30/09/2029
|  | CS-07054 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 30/09/2029
|  | CS-07055 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 100455-201020 | 1. Transpose the Cottam 1 circuit with the West Burton 1 circuit at Keadby 400kV substation. 2. Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby – Thorpe Marsh 400 kV circuit | 30/09/2029
|  | CS-07056 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 30/09/2029
|  | CS-07057 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101663-203316 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pulling mode capable of injecting up to -8 ohms along the Bicker Fen – West Burton 1 (A685) 400kV circuit | 30/09/2029
|  | CS-07058 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101041-202083 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +8 ohms along the Cottam – West Burton 1 (A413) 400kV circuit | 30/09/2029
|  | CS-07059 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 30/09/2029
|  | CS-07060 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101667-203320 | Installation of 2x200 MVAr MSC at Cottam 400kV substation | 30/09/2029
|  | CS-07061 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 101593-203208 & 030613-030613 | Uprate the Cottam – Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 30/09/2029
|  | CS-07062 | BOOM DEVELOPMENTS LTD | Drax 400kV Substation | 100449-201014 | Uprate the Drax – Eggbrough 1 circuit to achieve a post fault summer rating of 2500MVA | 30/09/2029
Drongan Battery Storage | PRO-002287 | CS-08375 | Drongan Battery Storage Ltd | Coylton 132/33kV Substation | Drongan - 132kV Disconnector | At Coylton 132kV substation, installation of one new 132kV disconnector | 20/10/2026
|  | CS-08376 | Drongan Battery Storage Ltd | Coylton 132/33kV Substation | SPT-RI-224 | At Coylton substation, the existing SGT1 and SGT2 275/132kV 120MVA transformers will be replaced (on line) with 240MVA units. | 20/10/2026
|  | CS-08377 | Drongan Battery Storage Ltd | Coylton 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 20/10/2026
Druim Leathann BEGA | PRO-000966 | CS-05642 | DRUIM LEATHANN WINDFARM LIMITED | Stornoway GSP | Druim Leathann Wind Farm Enabling works - Items 4-7 | The relevant transmission licensee will install a second 30/60 MVA 132/33 kV transformer (G2) and associated 33 kV transformer circuit breaker/isolator in a new building at Stornoway 132/33 kV Grid Supply Point. Protections and control modifications as required. Associated civil works. Miscellaneous and minor works. | 31/03/2027
|  | CS-05643 | DRUIM LEATHANN WINDFARM LIMITED | Stornoway GSP | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 31/03/2027
|  | CS-05644 | DRUIM LEATHANN WINDFARM LIMITED | Stornoway GSP | SHET-RI-042 | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHET-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly. | 31/03/2027
|  | CS-05645 | DRUIM LEATHANN WINDFARM LIMITED | Stornoway GSP | Druim Leathann Wind Farm enabling works - item 1 | Install 132 kV circuit switcher on the new 132/33 kV transformer (G2) and carry out associated cable and busbar works | 31/03/2027
Drumfad Battery Storage System | PRO-002419 | CS-08329 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Helensburgh 33kV Substation | SPT-RI-2691 | 1. Windyhill, Strathleven, Helensburgh and Sloy Load Management Scheme - The load management scheme required here shall monitor the two Windyhill to Sloy double circuits. This LMS shall monitor if one of the circuits is out of service and if an overload is detected on the adjacent circuit. Due to the configuration of the circuits in this area it will be required to interface with the 132kV circuit breakers at Sloy substation. The circuits to be monitored are the CK route and CL route. | 31/10/2027
|  | CS-08334 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Helensburgh 33kV Substation | SPT-RI-2148 | WindyHill SGT Auto-close scheme - Installation of an auto-close scheme across the three 275/132kV supergrid transformers at Windyhill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. It is proposed to run SGT3 on open standby and for the loss/opening of SGT1 (CB1380) or SGT2 (CB1480) an instruction shall be issued to close the SGT3 circuit breaker (CB1080) in order to keep two SGTs in service at all times. The scope of works also makes inclusion for the replacement of the SCADA/HMI system in order to facilitate the installation of this auto-close scheme | 31/10/2027
|  | CS-08335 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Helensburgh 33kV Substation | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 31/10/2027
|  | CS-08331 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Helensburgh 33kV Substation | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 31/10/2027
Drumlithie Battery Storage | PRO-002299 | CS-07930 | DRUMLITHIE BATTERY LIMITED | Fetteresso GSP | Drumlithie Battery Storage A1 | At Fetteresso 132/33kV GSP substation, install a new 132/33kV 120MVA Grid Transformer and associated 33kV metering circuit breaker and ancillary items. The transformer will be installed within the existing substation compound | 31/10/2028
|  | CS-07929 | DRUMLITHIE BATTERY LIMITED | Fetteresso GSP | Drumlithie Battery Storage A1 | At Fetteresso 132/33kV GSP substation, install a new HV circuit breaker and associated disconnectors | 31/10/2028
Drummarnock Wind Farm | PRO-001912 | CS-08464 | Drummarnock Wind Farm Limited | Bonnybridge GSP | SPT-RI-286 | Bonnybridge SGT1 Auto Changeover Scheme - An auto-changeover scheme will be installed on the Bonnybridge 275/132kV transformer SGT1 such that SGT1 will remain disconnected but on hot standby in case of a fault on Bonnybridge SGT2, Denny 275/132kV SGT3, or a double circuit fault on the Bonnybridge-Westfield 132kV circuits. This is required for fault level mitigation on the Bonnybridge 132kV busbar. | 01/10/2026
Drum of Clunas Wind and Solar Park | PRO-003970 | CS-09513 | BROADHAVEN DISTRIBUTION LTD | Drum of Clunas 275kV | Drum of Clunas Sole | Installation of a 275kV disconnector at the User’s site, on the Network side of the circuit breaker mentioned in Appendix G of this Bilateral Connection Agreement. | 31/10/2031
|  | CS-09514 | BROADHAVEN DISTRIBUTION LTD | Drum of Clunas 275kV | SHET-RI-229 | Cawdor Wind Farm substation and OHL Works – Construction of a new 275kV line circuit breaker bay on the 275kV Knocknagael - Blackhillock "CA1" circuit at the future Cawdor 275kV Substation. This construction arrangement will turn this into a Knocknagael - Cawdor - Blackhillock 275kV circuit. | 31/10/2031
Drumore Farm | PRO-002397 | CS-09782 | HYDROCK CONSULTANTS LIMITED | Alness 132/33kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2030
|  | CS-09783 | HYDROCK CONSULTANTS LIMITED | Alness 132/33kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2030
|  | CS-09784 | HYDROCK CONSULTANTS LIMITED | Alness 132/33kV Substation | SHET-RI-224 Alness 2 GSP 275kV Reinforcement | 0 | 31/10/2030
|  | CS-09778 | HYDROCK CONSULTANTS LIMITED | Alness 132/33kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/10/2030
|  | CS-09779 | HYDROCK CONSULTANTS LIMITED | Alness 132/33kV Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90 degrees Celsius to increase the continuous current rating of the circuit | 31/10/2030
|  | CS-09780 | HYDROCK CONSULTANTS LIMITED | Alness 132/33kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 31/10/2030
|  | CS-09781 | HYDROCK CONSULTANTS LIMITED | Alness 132/33kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 31/10/2030
Dunach Wind Farm | PRO-002754 | CS-09369 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-034 | Inverarnan 132kV QBs - Install 2 x 132kV 240MVA QBs at Inverarnan substation in series with the two 275/132kV SGTs connected to the Dalmally – Windyhill 275kV line. (SHET-RI-034) | 31/10/2034
|  | CS-09368 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2034
|  | CS-09370 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-046 | Taynuilt – North Argyll Reinforcement - Reinforce the transmission network between Taynuilt and North Argyll substation (established as part of SHET-RI-013). Rebuild approximately 12.5km of existing 132kV double circuit steel tower line between Creag Dhubh and Taynuilt with a heavy duty 132kV | 31/10/2034
|  | CS-09375 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 31/10/2034
|  | CS-09376 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 31/10/2034
|  | CS-09380 | GALILEO 04 LIMITED | Taynuilt GSP | SPT-RI-2319 | Carradale – Kilmarnock South subsea cable - Installation of 2 x 240MVA 220kV subsea cable circuits from Carradale (SHE Transmission) to the South of Troon. Installation of two underground cable circuits from the South of Troon to Kilmarnock South and two associated 400/220kV transformer at Kilmarnock South (SP Transmmission). | 31/10/2034
|  | CS-09378 | GALILEO 04 LIMITED | Taynuilt GSP | SPT-RI-028 | Dalmally 275kV Extension and Dalmally-Windyhill 275kV Uprating - replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). Uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). Extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). | 31/10/2034
|  | CS-09373 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2034
|  | CS-09371 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2034
|  | CS-09381 | GALILEO 04 LIMITED | Taynuilt GSP | Dunach WF - Disconnector | Installation of 1 x 132kV line disconnector on the Taynuilt side of the metering circuit breaker at Dunach Wind 132kV substation; approximately 11.5km of 132kV circuit between the new Dunach Wind 132kV substation and the existing Taynuilt substation, consisting of 11.2km of overhead line and 0.3km of underground cable | 31/10/2034
|  | CS-09379 | GALILEO 04 LIMITED | Taynuilt GSP | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 31/10/2034
|  | CS-09382 | GALILEO 04 LIMITED | Taynuilt GSP | Dunach WF - Taynuilt Bay | At the Taynuilt substation, installation of a new 132kV bay consisting of 1x 132kV circuit breaker and 2x 132kV disconnectors will also be required, along with an extension to the Taynuilt substation grounds, site platform and control building | 31/10/2034
|  | CS-09377 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-197 | Kintyre to North Wales HVDC Link - Construction of a new AC/DC converter station, with the AC end connected to the Creag Dhubh 275kV double busbar substation. The DC circuit is to be a bipole, solid return design, routed through the sea towards North Wales (landing point to be confirmed). | 31/10/2034
|  | CS-09372 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 31/10/2034
|  | CS-09374 | GALILEO 04 LIMITED | Taynuilt GSP | SHET-RI-130a | North Argyll – Craig Murrail 275kV Operation - Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Creag Dhubh substation (established as part of SHET-RI-013) to Craig Murrail Substation. This will require the upgrade of substations on this circuit for 275kV operation | 31/10/2034
Dungeness Energy Park | PRO-001986 | CS-07244 | LOW CARBON SOLAR PARK 14 LIMITED | Newchurch 400kV Substation | 101701-203401 | 1. Uprate the Dungeness – Ninfield OHL circuits to increase capacity. | 31/10/2031
|  | CS-07242 | LOW CARBON SOLAR PARK 14 LIMITED | Newchurch 400kV Substation | 101801-203687 | 1. Reconfiguration of Dungeness 400kV Main and Reserve Busbars to accommodate User’s Bay | 31/10/2031
|  | CS-07243 | LOW CARBON SOLAR PARK 14 LIMITED | Newchurch 400kV Substation | 031867-200324 | Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent. | 31/10/2031
Dunns Farm | PRO-003504 | CS-09539 | SP Distribution plc | East Kilbride South GSP | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 29/10/2027
|  | CS-09540 | SP Distribution plc | East Kilbride South GSP | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 29/10/2027
|  | CS-09538 | SP Distribution plc | East Kilbride South GSP | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 29/10/2027
Dyce Battery Storage | PRO-002332 | CS-07958 | Dyce Battery Storage Limited | Dyce GSP | Protection Settings - Dyce BESS | Modification to the existing LV Directional Overcurrent (DOC) protection settings at Dyce 132/33kV substation | 30/10/2025
|  | CS-07959 | Dyce Battery Storage Limited | Dyce GSP | Loss of Mains - Dyce BESS | A loss of mains scheme will be configured at Dyce GSP as requested by the User. | 30/10/2025
|  | CS-07957 | Dyce Battery Storage Limited | Dyce GSP | ANM Signals | This scheme requires the Relevant Transmission Licensee to provide signals into an Active Network Management (ANM) scheme to be installed by the Host Distribution Network Operator at Dyce 132/33kV GSP substation. These signals will be provided to the Host Distribution Network Operator via a separate relay panel within the 33kV Switchroom. The required measurement points and operation requirements to implement this ANM scheme will be determined through the detailed design phase. | 30/10/2025
Earba PSH | PRO-004030 | CS-09669 | EARBA LIMITED | Earba PSH Powerhouse Substation | SPT-RI-2095 | Kincardine North 400kV Substation - The scope of works at Kincardine North 400kV Substation (ref. NOA Code LWUP) is summarised as follows. The new Kincardine North 400kV GIS Substation will initially connect the following circuits: SHE Transmission Alyth No.1 400kV, SHE Transmission Alyth No.2 400kV, Denny North No.1 400kV, Denny North No.2 400kV, Kincardine No.1 400kV, and Kincardine No.2 400kV. The substation will be equipped with two bus section circuit breakers and two bus coupler circuit breakers | 31/10/2029
|  | CS-09667 | EARBA LIMITED | Earba PSH Powerhouse Substation | SHET-RI-172 | Dalwhinnie 400kV Substation - Establish a new 400kV substation on the Beauly-Denny GM1 circuit (between Fort Augustus and Tummel) in the geographical area between Laggan and Dalwhinnie | 31/10/2029
|  | CS-09666 | EARBA LIMITED | Earba PSH Powerhouse Substation | SPT-RI-1560 | It is proposed to uprate the existing Denny-Braco West 275kV circuit to 400kV operation by transferring the circuit from its current bay in Denny 275kV substation to a new bay in Denny 400kV substation. | 31/10/2029
|  | CS-09668 | EARBA LIMITED | Earba PSH Powerhouse Substation | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 31/10/2029
|  | CS-09665 | EARBA LIMITED | Earba PSH Powerhouse Substation | SHET-RI-172 | Dalwhinnie 400kV Substation - Establish a new 400kV substation on the Beauly-Denny GM1 circuit (between Fort Augustus and Tummel) in the geographical area between Laggan and Dalwhinnie | 31/10/2029
|  | CS-09664 | EARBA LIMITED | Earba PSH Powerhouse Substation | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 31/10/2029
Earl Shilton BESS | PRO-001950 | CS-07408 | Exagen Development Limited | Earl Shilton 275kV | 101831-203755 | 0 | 26/10/2029
|  | CS-07409 | Exagen Development Limited | Earl Shilton 275kV | 101329-202649 | Hotwire Enderby – Ratcliffe 400kV circuits 1 and 2 to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 26/10/2029
|  | CS-07410 | Exagen Development Limited | Earl Shilton 275kV | 101593-203208 | Reconductor Cottam-Staythorpe 400kV circuit 1 to achieve a post summer rating of 2960 MVA | 26/10/2029
|  | CS-07411 | Exagen Development Limited | Earl Shilton 275kV | 100459- 201024 | 0 | 26/10/2029
|  | CS-07412 | Exagen Development Limited | Earl Shilton 275kV | 100591-201213 | Reconductor Ratcliffe – Staythorpe 400kV circuit; reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 2780MVA | 26/10/2029
|  | CS-07413 | Exagen Development Limited | Earl Shilton 275kV | 100590-201212 | Reconductor the existing 2 x 500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2 x 620mm2 conductor and uprate the cable section to provide a post fault summer rating of 2780MVA | 26/10/2029
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | PRO-001139 | CS-06051 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 30/05/2029
|  | CS-06052 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 30/05/2029
|  | CS-06053 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 30/05/2029
|  | CS-06054 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 30/05/2029
|  | CS-04327 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 30/05/2029
|  | CS-04328 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 30/05/2029
|  | CS-04329 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 30/05/2029
|  | CS-04330 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | SPT-RI-028 | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | 30/05/2029
|  | CS-04331 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation | Earraghail H1 Works | The construction of approximately 5.6km of 275kV double circuit overhead line between the Craig Murrail - Crossaig overhead line and the Earraghail 275/33kV substation. At the wind farm substation, the 275kV overhead line will terminate onto a circuit breaker bay. The sole enabling works will include construction of two 275kV AIS line bays with associated line isolators (L13 and L23) and Circuit Breaker isolators (L15 and L25), and a 275kV AIS transformer circuit breaker bay with associated transformer circuit breaker (H10) and transformer circuit breaker isolator (H17). | 30/05/2029
East Anglia One North | PRO-000269 | CS-05651 | EAST ANGLIA ONE LIMITED | EA1N 275/66kV Offshore Platform | 20834-2 | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 31/03/2026
|  | CS-05652 | EAST ANGLIA ONE LIMITED | EA1N 275/66kV Offshore Platform | 20834-2A | Establish a new fully equipped GIS bay at Bramford 400kV substation interfacing with a 1200MW capacity OFTO circuit. | 31/03/2026
|  | CS-05018 | EAST ANGLIA ONE LIMITED | EA1N 275/66kV Offshore Platform | 100911-201829 | At Friston 400kV Substation; Facilitate an OFTO connection in to a spare bay and provide an intertrip facility. | 31/03/2026
|  | CS-05019 | EAST ANGLIA ONE LIMITED | EA1N 275/66kV Offshore Platform | 100077-200227 | Construct a new 400kV double busbar substation at Friston consisting of four feeder bays, one bus coupler and one section breaker bay. | 31/03/2026
|  | CS-05021 | EAST ANGLIA ONE LIMITED | EA1N 275/66kV Offshore Platform | 100077-201203 | Connect the new 400kV substation at Friston to the Transmission System by teeing in to the existing two double circuits between Bramford and Sizewell. Construct a new 400kV single-switch mesh busbar switching compound north of the new 400kV substation at Friston and divert the existing Bramford-Leiston-Sizewell 400kV circuit in to the switching compound. | 31/03/2026
East Anglia Three | PRO-000270 | CS-06667 | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 101238-202465 | At Bramford 400 kV Substation: Phase 1 - Facilitate an OFTO connection in a spare bay and provide an intertrip facility. | 31/01/2026
|  | CS-06668 | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 020834-030647 | At Bramford 400 kV Substation: Phase 1 - To accommodate the additional OFTO bay, the 400kV GIS busbar will be extended to include a fourth busbar section. | 31/01/2026
|  | CS-06669 | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 31/01/2026
|  | CS-06670 | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 020315-020315-CLSD | Construct an initial nine bay 400kV GIS substation at Bramford as a two section GIS substation with one bus coupler and two bus sections to be subsequently extended by a further section turning in existing Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 31/01/2026
|  | CS-06671 | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 020834-021494 | At Bramford 400 kV Substation: Phase 2 - Extend the Phase 1 GIS substation by a further nine bays; comprising of five OHL feeder bays to receive the reconfigured Pelham 1 & 2 circuits, Sizewell 1 & 2 circuits and the Norwich 2 circuit. | 31/01/2026
East Anglia Two | PRO-000134 | CS-05649 | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 20834-2 | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 31/12/2025
|  | CS-05650 | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 20834-2A | Establish a new fully equipped GIS bay at Bramford 400kV substation interfacing with a 1200MW capacity OFTO circuit. | 31/12/2025
|  | CS-05020 | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 100077-201203 | Connect the new 400kV substation at Friston to the Transmission System by teeing in to the existing two double circuits between Bramford and Sizewell. Construct a new 400kV single-switch mesh busbar switching compound north of the new 400kV substation at Friston and divert the existing Bramford-Leiston-Sizewell 400kV circuit in to the switching compound. | 31/12/2025
|  | CS-05022 | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 100077-200227 | Construct a new 400kV double busbar substation at Friston consisting of four feeder bays, one bus coupler and one section breaker bay. | 31/12/2025
|  | CS-05023 | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 100077-201239 | Establish a spare bay at the new Friston 400 kV substation, interfacing with the OFTO circuit. | 31/12/2025
East Claydon Greener Grid Park | PRO-002314 | CS-09223 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101879-203856 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #1 (RATS4-WILE4-1) to summer pre-fault rating 2490 MVA | 01/11/2036
|  | CS-09208 | STATKRAFT UK LTD | East Claydon 400kV Substation | 100816-201651 | Reconductor Cottam - Grendon ZDA & ZA route to 2x570mm2 conductor to achieve a post fault winter rating of 2310MVA. | 01/11/2036
|  | CS-09205 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101592-203207 | Reconductor East Claydon – Amersham Main – Iver 400kV double circuit route (55.5km, 2x500mm2 Twin Rubus conductor on L2 Towers at 75oC with a summer pre-fault rating of 1466MVA) to 2x620mm2 Twin Matthew Conductor at 170°C to achieve a new summer pre-fault rating of 2490 MVA. | 01/11/2036
|  | CS-09200 | STATKRAFT UK LTD | East Claydon 400kV Substation | 102625-205259 | Transpose the Cowley and Enderby / Patford Bridge 2 circuits on to the East Claydon 400kV M2/R2 busbar extensions | 01/11/2036
|  | CS-09196 | STATKRAFT UK LTD | East Claydon 400kV Substation | 102623-205257 | Extension of East Claydon 400kV double busbar (M2/R2) substation to provide space for the User’s generation connection bay | 01/11/2036
|  | CS-09217 | STATKRAFT UK LTD | East Claydon 400kV Substation | 102108-204302 | Uprate the Iver – Laleham circuit 1 | 01/11/2036
|  | CS-09219 | STATKRAFT UK LTD | East Claydon 400kV Substation | 102110-204304 | Uprate both Ealing – Laleham circuit 1 and 2 | 01/11/2036
|  | CS-09224 | STATKRAFT UK LTD | East Claydon 400kV Substation | 102636-205302 | Upgrade the Cowley – Culham Jet – Didcot circuits | 01/11/2036
|  | CS-09202 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101248-202488 | Reconductoring of Sundon – Wymondley 1 and 2 circuits, modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham - Wymondley 400kV and from Wymondley – Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation | 01/11/2036
|  | CS-09215 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101889-203868 | Reconductor the East Claydon legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490 MVA. | 01/11/2036
|  | CS-09204 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101316-202621 | Hotwire A881 East Claydon – Cowley 400kV circuit (36.3km, 4x400mm2 zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 01/11/2036
|  | CS-09197 | STATKRAFT UK LTD | East Claydon 400kV Substation | 102112-204306 | Install a bus coupler circuit breaker on busbars M1/R1 | 01/11/2036
|  | CS-09198 | STATKRAFT UK LTD | East Claydon 400kV Substation | 102023-204178 | The replacement of SGT1, SGT2, SGT3 and SGT4 and any associated assets in order to achieve a rating of 460MVA. The transformers will also have a higher impedance at East Claydon 400/132kV substation to resolve the fault level issues at the tertiary winding of the SGTs | 01/11/2036
|  | CS-09199 | STATKRAFT UK LTD | East Claydon 400kV Substation | 102624-205258 | Install two bus section circuit breakers on busbars M1 and R1 (one on each bus bar) | 01/11/2036
|  | CS-09207 | STATKRAFT UK LTD | East Claydon 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 01/11/2036
|  | CS-09214 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101884-203860 | Reconductor the Enderby legs of both East Claydon – Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2110MVA – 2490MVA (both Will and Enderby) | 01/11/2036
|  | CS-09211 | STATKRAFT UK LTD | East Claydon 400kV Substation | 020903-020903 | Uprating of the Cowley – Walham / Cowley – Minety 400kV circuit cables to achieve 1650MVA post-fault summer rating | 01/11/2036
|  | CS-09212 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101420-202784 | Uprate the Bramley – Didcot 400kV circuits; including overhead line and cable sections. | 01/11/2036
|  | CS-09218 | STATKRAFT UK LTD | East Claydon 400kV Substation | 102109-204303 | Uprate Iver – West Weybridge circuit. | 01/11/2036
|  | CS-09201 | STATKRAFT UK LTD | East Claydon 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 01/11/2036
|  | CS-09216 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 1 & 2 to achieve a pre-fault summer rating of 2790MVA | 01/11/2036
|  | CS-09221 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101978-204103 | Uprate the Drakelow 400kV -to- Ratcliffe On Soar 400kV circuit #1 (DRAK4-RATS4-1) to summer pre-fault rating 2490MVA | 01/11/2036
|  | CS-09206 | STATKRAFT UK LTD | East Claydon 400kV Substation | 100468-201037 | Uprate the Cowley – East Claydon and Cowley – Leighton Buzzard – Sundon circuits | 01/11/2036
|  | CS-09209 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 01/11/2036
|  | CS-09203 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 01/11/2036
|  | CS-09220 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101885-203861 | Reconductor MILLBROOK-SUNDON 4-1 (MILB4-SUND4-1) & MILLBROOK-SUNDON 4-2 (MILB4-SUND4-2) 400kV circuit to achieve more than 1605MVA summer pre-fault rating | 01/11/2036
|  | CS-09210 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101245-202485 | Reconductor the existing 4x400mm2 conductor on the Eaton Socon – Wymondley 2 400kV circuit with 2x850mm2 90oC conductor to achieve a pre fault summer rating of 2400 MVA | 01/11/2036
|  | CS-09222 | STATKRAFT UK LTD | East Claydon 400kV Substation | 101880-203857 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4-WILE4-2) to summer pre-fault rating 2490MVA | 01/11/2036
|  | CS-09213 | STATKRAFT UK LTD | East Claydon 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 01/11/2036
East Claydon Solar PV | PRO-001573 | CS-07462 | STATERA ENERGY LIMITED | East Claydon 400kV Substation | 101282-202532 | Extension of East Claydon 400kV double busbar substation to provide space for the User’s generation connection bay. | 01/10/2026
|  | CS-07463 | STATERA ENERGY LIMITED | East Claydon 400kV Substation | 100893-201795 | 1. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT1. 2. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT2. | 01/10/2026
|  | CS-07464 | STATERA ENERGY LIMITED | East Claydon 400kV Substation | 021847-021847 | Bramford to Twinstead new overhead line circuit | 01/10/2026
|  | CS-07465 | STATERA ENERGY LIMITED | East Claydon 400kV Substation | 101316-202621 | Hotwire A881 East Claydon – Cowley 400kV circuit (36.3km, 4x400mm2 zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 01/10/2026
|  | CS-07466 | STATERA ENERGY LIMITED | East Claydon 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 01/10/2026
|  | CS-07467 | STATERA ENERGY LIMITED | East Claydon 400kV Substation | 100952-201899 | Uprate all three down droppers on the East Claydon - Leighton Buzzard - Sundon circuit and hotwire the sections of 4x400mm2 zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 01/10/2026
|  | CS-07468 | STATERA ENERGY LIMITED | East Claydon 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 01/10/2026
East Pit | PRO-002736 | CS-09167 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 101505-202969 | - Eastern side GIS extension of Rhigos 400kV substation double busbars including AIS-GIS conversion module for provision of the User’s generator bay1 - Replace AIS bus coupler bay with new GIS bus coupler to facilitate space for new generator bays within existing substation compound (avoiding development of contaminated land)1 - Installation of a new Commercial/Category 2 Operational Tripping Scheme at Rhigos 400kV substation | 15/10/2037
|  | CS-09169 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 020903-020903 | Uprate Hinksey cable section of the Cowley – Walham – Minety 400kV circuits; add second core per phase on both circuits in order to achieve at least 2900MVA post- fault summer rating | 15/10/2037
|  | CS-09171 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 102093-204284 | Uprate A844 Minety – Cowley 400kV circuit overhead line sections by reconductoring the 0.6km, 2x500mm2 Rubus at 75°C on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 99.5km, 4x400mm2 Zebra conductor at 50°C on L6 towers with summer pre-fault rating of 1862MVA to 75°C to achieve a summer pre-fault rating of 2500MVA | 15/10/2037
|  | CS-09172 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 100424-200970 | Uprate the Bramley - Melksham 400kV circuits 1 and 2 (81.6km, 2x400mm2 zebra conductor at 50oC on L2 towers with summer pre-fault rating of 931MVA) by reconductoring with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA. | 15/10/2037
|  | CS-09174 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 102087-204278 | Uprate A87D Imperial Park – Melksham (future Imperial Park – Folly Farm – Melksham) 400kV circuit cable section (3.9km, with a summer pre-fault rating of 1424MVA) to a summer pre-fault rating of at least 1621MVA | 15/10/2037
|  | CS-09176 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 102094-204287 | Installation of a new 200MVAr mechanically switched capacitor bank (MSC) at either Minety 400kV or Melksham 400kV Substation for pre-fault voltage compliance | 15/10/2037
|  | CS-09175 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 15/10/2037
|  | CS-09168 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 102641-205308 | GIS Extension of Rhigos 400kV substation double busbar for provision of the User’s generator bay | 15/10/2037
|  | CS-09173 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 101497-202952 | Uprate the Melksham – Seabank leg of Melksham – Seabank – Sandford (future Melksham – Folly Farm and Folly Farm – Seabank leg of Folly Farm – Seabank – Sandford) 400kV circuit by hotwiring the existing 4x400mm2 Zebra at 50oC section to 75oC to achieve a summer pre-fault rating of 2500MVA and reconductoring the existing 2x700mm2 Araucaria conductor with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 15/10/2037
|  | CS-09177 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 101065-202138 | Uprate A83A & A873 Melksham – Minety 1 & 2 400kV circuits 28km, 2x500mm2 Rubus at 85oC on L2 towers with summer pre-fault rating of 1568MVA by reconductoring with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 15/10/2037
|  | CS-09170 | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation | 101051-202109 | Uprate A861 Walham- Cowley (future Walham- Botley West & Botley West - Cowley) 400kV circuit overhead line sections by reconductoring the 19.2km, 2x500mm2 Rubus at 75oC on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 61.7km, 4x400mm2 Zebra conductor at 50oC on L6 towers with summer pre-fault rating of 1862MVA to 75oC to achieve a summer pre-fault rating of 2500MVA | 15/10/2037
Eaton Socon PV Storage | PRO-002218 | CS-09298 | CSE37 Limited | Eaton Socon 400kV Substation | 102106-204300 | 1. Make enable/build tertiary connections on the SGT 3. 2. Condition assessment of 13kV cable and other assets to confirm suitability for reuse. 3. Install earthing transformer on 13kV Tertiary connection. 4. Install 13kV Cable (if required) from 13kV Tertiary connection to the 13kV Disconnector. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 30/10/2029
|  | CS-09299 | CSE37 Limited | Eaton Socon 400kV Substation | 101428-202800 | 1. The design, procurement and offline construction of a ten bay 400kV GIS substation at Eaton Socon; comprising of three feeder bays, three HV SGT bays, two busbar coupler bays, one busbar section bay and one Third Party bay. 2. The decommissioning and demolition of the existing 400kV substation at Eaton Socon following the completion of the new substation. | 30/10/2029
Eaton Socon Solar | PRO-001513 | CS-05024 | RNA-ENERGY LTD | Eaton Socon 400kV Substation | 101215-202437 | Extension of the existing Eaton Socon 400kV Substation Main and Reserve Busbars to accommodate the User’s bay | 31/10/2028
|  | CS-05025 | RNA-ENERGY LTD | Eaton Socon 400kV Substation | 101245-202485 | Reconductoring of the Eaton Socon -Wymondley 2 circuit | 31/10/2028
|  | CS-05026 | RNA-ENERGY LTD | Eaton Socon 400kV Substation | 100591-201213 | Reconductor Ratcliffe – Staythorpe 400kV circuit; reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 2780MVA | 31/10/2028
|  | CS-05027 | RNA-ENERGY LTD | Eaton Socon 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 31/10/2028
|  | CS-05028 | RNA-ENERGY LTD | Eaton Socon 400kV Substation | 100952-201899 | Uprate all three downdroppers on the East Claydon - Leighton Buzzard - Sundon circuit to provide a pre-fault summer rating of 2400MVA | 31/10/2028
Eclipse at Creyke Beck 400/33kV Substation | PRO-002499 | CS-07735 | Eclipse Power Networks Limited |  | 033837-201648 | At Creyke Beck 400kV Substation: Move Creyke Beck - Thornton 2 circuit and Creyke Beck - Humber Refinery - Keadby circuit to the new GIS Creyke Beck 400kV Compound. Install interconnector 2 at the vacated Creyke Beck-Thornton 2 feeder bay to Creyke Beck 400kV Main and Reserve busbar | 30/07/2027
|  | CS-07733 | Eclipse Power Networks Limited |  | 100964-201978 | At Creyke Beck 400kV substation: Extend the substation to accommodate anew bay for a 400/33kV SGT HV Bay. | 30/07/2027
|  | CS-07734 | Eclipse Power Networks Limited |  | 033837-201012 | At Creyke Beck 400kV Substation: Build a new 400kV double busbar compound with 2 feeders bay, 1 coupler bay, 1 section bay and connect 2 new interconnectors to Creyke Beck 400kV substation | 30/07/2027
|  | CS-07732 | Eclipse Power Networks Limited |  | 100964-201924 | 1. Installation of a new 150MVA rated 400/33kV SGT including HV and LV bays 2. Establish a new single busbar 33kV substation at Creyke Beck to be connected via the new 400/33kV SGT. 3. Installation of an earthing transformer connecting onto the 33kV busbar. 4. Protection and control modification as required 5. Associated civil works. 6. Miscellaneous and minor works. | 30/07/2027
EcoKincardine | PRO-003557 | CS-09661 | Econergy International Limited | Kincardine North 400kV Substation | SPT-RI-2095 | Kincardine North 400kV Substation - The scope of works at Kincardine North 400kV Substation (ref. NOA Code LWUP) is summarised as follows. The new Kincardine North 400kV GIS Substation will initially connect the following circuits: SHE Transmission Alyth No.1 400kV, SHE Transmission Alyth No.2 400kV, Denny North No.1 400kV, Denny North No.2 400kV, Kincardine No.1 400kV, and Kincardine No.2 400kV. The substation will be equipped with two bus section circuit breakers and two bus coupler circuit breakers | 31/07/2028
|  | CS-09660 | Econergy International Limited | Kincardine North 400kV Substation | SPT-RI-2083 | Kincardine North – Wishaw 400kV reinforcement (DWUP)- Establish 400kV infrastructure through the centre of the network following the East Coast 400kV onshore incremental (ECUP) reinforcement, but in advance of the completion of existing Denny to Wishaw 400kV reinforcement (DWNO). The scope of this TORI will be aligned with the ‘DWUP’ option submitted to the 2021/22 Network Options Assessment (NOA) process. It is proposed to reconfigure and update existing 275kV single circuit between the Kincardine and Wishaw to 400kV operation to establish a new Kincardine North – Wishaw 400kV circuit. | 31/07/2028
|  | CS-09659 | Econergy International Limited | Kincardine North 400kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 31/07/2028
EcoMossmorran | PRO-003469 | CS-09760 | Econergy International Limited | Mossmoran 275kV Substation | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 20/10/2031
|  | CS-09761 | Econergy International Limited | Mossmoran 275kV Substation | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 20/10/2031
|  | CS-09762 | Econergy International Limited | Mossmoran 275kV Substation | SHET-RI-185 | Kintore - Tealing 400kV circuit – Establish a new 400 kV double circuit overhead line between Kintore 400 kV substation and Tealing 400 kV substation. | 20/10/2031
|  | CS-09759 | Econergy International Limited | Mossmoran 275kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 20/10/2031
Edinbane Windfarm | PRO-000135 | CS-07398 | VATTENFALL WIND POWER LTD | Edinbane GSP | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 01/01/2030
|  | CS-07399 | VATTENFALL WIND POWER LTD | Edinbane GSP | SHET-RI-135 | 4. Broadford – Edinbane Reinforcement (SHET-RI-135) | 01/01/2030
Eggborough | PRO-002049 | CS-07504 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 101821-203734 | Substation Control System database changes and the Relevant Tranmission Licencee’s operations commissioning resource | 16/06/2032
|  | CS-07511 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 16/06/2032
|  | CS-07519 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 16/06/2032
|  | CS-07505 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 100161-200456 | Uprating of CB X120 at Eggborough 400kV substation to 63kA rating | 16/06/2032
|  | CS-07510 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 101263-202505 | Grendon-Staythorpe Uprating to 2490MVA pre-fault rating during Summer | 16/06/2032
|  | CS-07513 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 16/06/2032
|  | CS-07518 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 100816-201651 | Reconductor Cottam- Grendon ZDA and ZA OHL with 3090MVA rating postfault during Winter | 16/06/2032
|  | CS-07506 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm2 sections of the circuits between towers ZZC40R and ZZC002 and towers ZZC002 and ZZC001 (13,15km total) with 2x570 mm2 strung to an operating temperature of 75°C. The remaining 1.9km section between ZZC46R and ZZC40R which is already 2x570 mm2should be hotwired to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A continuous. | 16/06/2032
|  | CS-07525 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 101869-203836 | Reconductoring of Cottam to Eaton Socon line (A481 and A482) with triple araucaria to achieve a 3820MVA post-fault Winter rating | 16/06/2032
|  | CS-07526 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 101855-203810 | Reconductoring of Macclesfield to Stalybridge line (A23A) with 1530MVA prefault rating during Summer | 16/06/2032
|  | CS-07507 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 100905-201821 | At Keadby replace the CB (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3800MVA | 16/06/2032
|  | CS-07509 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 100798-201612 | Uprate Cottam - West Burton circuit with twin Warwick conductor at 180 degrees for a pre-fault summer rating of 2950MVA. Works to include replacement of disconnector and circuit breaker at Cottam, OHL reconductoring and protection replacement | 16/06/2032
|  | CS-07523 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 101276-202522 | Reconductoring of Ryhall to Eaton Socon line (A484) with 3820MVA postfault rating during Winter | 16/06/2032
|  | CS-07508 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 100450-201015 | Uprate the Cottam - Keadby 1 and 2 circuits to achieve a post fault winter rating of 3400MVA | 16/06/2032
|  | CS-07515 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 16/06/2032
|  | CS-07512 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 101264-202506 | Cottam-Ryhall reconductoring with 3820MVA post-fault rating during Winter | 16/06/2032
|  | CS-07517 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 101697-203381 | ZE: CELL4-MACC4 OHL Reconductoring with 2690MVA rating pre-fault during Summer | 16/06/2032
|  | CS-07514 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 16/06/2032
|  | CS-07524 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 16/06/2032
|  | CS-07516 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 101561-203105 | Kearsley-Rochdale-Whitegate circuit cable uprating with 480MVA pre-fault rating during Summer | 16/06/2032
|  | CS-07521 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 030613-030613 | Reconductor Cottam-Staythorpe 2 with 2890MVA post-fault rating during Winter | 16/06/2032
|  | CS-07522 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 033766-033766 | DRAX4-EGGB4 reconductor for 2250MVA pre-fault rating during Summer | 16/06/2032
|  | CS-07520 | SSE UTILITY SOLUTIONS LIMITED | Eggborough 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post fault winter rating of 3420MVA | 16/06/2032
Eggborough CCGT and BESS | PRO-000136 | CS-09643 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100171-200449 | Uprating of the Thorpe Marsh – West Melton 1 circuit to cater for 1160/920 MVA post-fault (winter/summer), comprising: Reconductoring of the OHL section | 01/10/2026
|  | CS-09639 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100161-200405 | Provision of the required space for the User to connect two of the generator bays at Eggborough 400kV substation. | 01/10/2026
|  | CS-09650 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 01/10/2026
|  | CS-09653 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 101775- 203564 | Hotwire the 4 x 400mm2 sections of the Drax – Thornton 1 & 2 circuits for operation at 75°C | 01/10/2026
|  | CS-09642 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100171-200448 | Uprating of the Thorpe Marsh – West Melton 1 circuit to cater for 1160/920 MVA post-fault (winter/summer), comprising: Uprating of the cable section | 01/10/2026
|  | CS-09641 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 033513-033513 | Hotwiring of the Keadby – West Burton 2 circuit to cater for 3100/2600 MVA post-fault (winter/autumn. | 01/10/2026
|  | CS-09646 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100987-201984 | Uprate the existing bays in the Creyke Beck – Thornton 1 circuit to achieve a post-fault summer rating of 3600MVA | 01/10/2026
|  | CS-09649 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 01/10/2026
|  | CS-09640 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100528-201118 | Uprating of SGT3 (750MVA) at Thorpe Marsh 400kV substation with a 400/275kV 1100 MVA interbus transformer | 01/10/2026
|  | CS-09644 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 01/10/2026
|  | CS-09648 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 101386-202715 | Reconductor Lackenby –Thornton double circuit with 3 x 700mm2 at 90°C. Replace the disconnectors on both Thornton circuits at Lackenby substation, to equipment with an equal rating to provide a pre fault summer rating of 2790MVA | 01/10/2026
|  | CS-09645 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 102208-204431 | Reconductor the Norton – Osbaldwick circuits with 2 x 620mm2 GAP conductor | 01/10/2026
|  | CS-09647 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 100909-201825 | Uprate the existing bays in the Creyke Beck – Thornton 2 circuit (A323) to achieve a post-fault summer rating of 3600MVA | 01/10/2026
|  | CS-09651 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 102173-204381 | Reconductor the Lackenby – Saltholme and Lackenby – Norton 400kV circuit with 2 x 772mm2 Warwick conductor as per NOA LNRE | 01/10/2026
|  | CS-09652 | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 101706-203409 | Reconductor the Osbaldwick – Thornton 400kV OHL circuit ~17km with 3 x 700mm2 Araucaria conductor | 01/10/2026
Elchies Wind Farm | PRO-000151 | CS-05654 | ELCHIES WIND LIMITED | Elchies 132/33kV Substation | Elchies Wind Farm H1 Works | The installation of an outdoor AIS 132kV transformer circuit breaker and disconnector at the Elchies 132/33kV Substation. Approximately 24km of 132kV circuit will be required to connect Elchies 132/33kV substation to the a new 132kV bay connected to the 132kV Busbar at Blackhillock 275/132kV substation. Approximately 200m of 132kV underground cable will be required to connect to the Blackhillock 132kV busbar | 30/06/2027
|  | CS-05655 | ELCHIES WIND LIMITED | Elchies 132/33kV Substation | SHET-RI-079 | Additional 275/132kV SGT’s at Blackhillock - Reinforce the transmission network at Blackhillock substation by installing two additional new 275/132kV Supergrid Transformers. The transformers are to be rated at 360MVA. (SHETL- RI-079) | 30/06/2027
ElecLink | PRO-000286 | CS-05656 | ELECLINK LIMITED | Sellindge 400kV Substation | NGET-RI-31832S | The provision of one bus section bay and one bus coupler bay to facilitate the User connection at a new 400kV GIS 7 bay Sellindge substation. | 30/06/2019
Elland Bulk PP | PRO-002778 | CS-08514 | NORTHERN POWERGRID (YORKSHIRE) PLC | Elland 132kV Substation | 102753-205556 | Replacement of L43 and H43 with disconnector circuit breaker (DCB) at Elland 275kV substation. | 30/10/2036
|  | CS-08513 | NORTHERN POWERGRID (YORKSHIRE) PLC | Elland 132kV Substation | 102037-204194 | 1. Extension of mesh corner for installation of 240MVA, 275/132kV SGT 5 in Elland 275kV substation. 2. Installation and commissioning of associated equipment and circuit breaker at Elland 275kV substation. 3. Build, connect and commission a new 240MVA, 275/132kV super grid transformer and associated cable work along with 40kA rms breaker rating at Elland substation. 4. Extension the main and reserve busbars at Elland 132kV substation to accommodate the new SGT bay. 5. Extension the main and reserve busbars at Elland 132kV substation to accommodate the new user bay. 6. The auto close scheme to close the selected bus coupler circuit breaker(s) following the loss of an on-load super grid transformer during an outage of another super grid transformer at Elland 132kV substation. Also the scheme to connect the hot standby SGT to the section on outage/loss of an on-load supergrid transformer is observed. | 30/10/2036
Elstree (tertiary) | PRO-000400 | CS-05034 | ELSTREE GREEN LIMITED | Elstree 275kV Substation | 003606-020741 | 1. Completion of the Elstree 132kV substation GIS transfer | 31/10/2025
|  | CS-05657 | ELSTREE GREEN LIMITED | Elstree 275kV Substation | 100640-201314 | Install earthing transformer on the 13kV tertiary connection. Install 13kV cable connecting earthing transformer to the disconnecting circuit breaker. Install a 72.5kV, 40kA-rated disconnecting circuit breaker to the connection assets for the User’s connection. | 31/10/2025
Elstree 400MW BESS | PRO-002169 | CS-07695 | Hilfield Energy Limited | Elstree 400kV Substation | 102033-204189 | 1. Installation and commissioning of a fifth 360MVA 275/132kV SGT, including associated assets. 2. Extension of main and reserve busbar to facilitate User feeder bay connections. 3. Extensions of new 132kV GIS hall to accommodate busbar extension for new relevant transmission licensee and User GIS bays. | 31/10/2029
|  | CS-07698 | Hilfield Energy Limited | Elstree 400kV Substation | 101659-203313 | Reconductoring the existing 2x400mm2 conductor on the Tilbury- Warley double circuit with 2x500mm2 conductor to achieve a pre- Fault summer rating of 1120MVA | 31/10/2029
|  | CS-07696 | Hilfield Energy Limited | Elstree 400kV Substation | 101826-203749 | 1. Installation and commissioning of a fourth 360MVA 275/132kV SGT, including associated assets. 2. Extension of main and reserve busbar to facilitate User feeder bay Connections 3. Extensions of new 132kV GIS hall to accommodate busbar extension for new relevant transmission licensee and User GIS bays. | 31/10/2029
|  | CS-07697 | Hilfield Energy Limited | Elstree 400kV Substation | 101379-202701 | 1. Installation of new towers/modification of existing towers and associated OHL works to facilitate a double circuit turn in of the Elstree – Warley 1 & 2 overhead line circuits. 2. Design, procurement and construction of a 275kV double busbar substation; with associated bus couplers, bus sections, feeder bays and SGT HV bays. 3. Installation and commissioning of three 360MVA 275/132kV SGT, including associated assets. 4. Design, procurement and construction of a 132kV double busbar substation; with associated bus couplers, bus sections, SGT HV bays and skeletal User bays. 5. Works required to establish the new 275/132kV substation, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure. | 31/10/2029
|  | CS-07699 | Hilfield Energy Limited | Elstree 400kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 31/10/2029
|  | CS-07700 | Hilfield Energy Limited | Elstree 400kV Substation | 102047-204214 | Reconductor Elstree 275kV – Elstree B 275kV double circuit | 31/10/2029
Elvanfoot (25MW) Energy Storage | PRO-003278 | CS-08943 | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 275/132/33kV | SPT-RI-2927 | Elvanfoot 132kV to Elvanfoot Energy Storage 132/33kV Collector Substation | 26/10/2029
|  | CS-08942 | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 275/132/33kV | SPT-RI-226 | Installation of a new 275/132kV 360MVA transformer and a new 132kV busbar at Elvanfoot substation, to allow new generators to connect. | 26/10/2029
Elvanfoot (50MW) Energy Storage | PRO-003279 | CS-08941 | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 275/132/33kV | SPT-RI-2927 | Elvanfoot 132kV to Elvanfoot Energy Storage 132/33kV Collector Substation | 26/10/2029
|  | CS-08940 | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 275/132/33kV | SPT-RI-226 | Installation of a new 275/132kV 360MVA transformer and a new 132kV busbar at Elvanfoot substation, to allow new generators to connect. | 26/10/2029
Elvanfoot (9.8 MW) Energy Storage | PRO-001721 | CS-04681 | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 132kV/33kV Substation | SPT-RI-226 | Installation of a new 275/132kV 360MVA transformer and a new 132kV busbar at Elvanfoot substation, to allow new generators to connect. | 06/12/2024
|  | CS-04682 | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 132kV/33kV Substation | SPT-RI-1876 | 2. Elvanfoot 132/33kV Grid Transformer - Install a 132/33kV 60MVA transformer at Elvanfoot to accommodate the increased generation connecting at 33kV into the site. (SPT-RI-1876) | 06/12/2024
Enderby (Akira) | PRO-000426 | CS-05037 | ENDERBY BATTERY STORAGE LIMITED | Enderby 400kV Substation | 100812-201639 | 1. Install earthing transformer on 13kV tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3. Install Disconnector at the 13kV side connecting Tertiary to Connection Assets for Users connection. 4. Works required to connect the User to the operational tripping scheme as described in Appendix F3 of the Bilateral Connection Agreement* *Dealoding to manage users import limit during N-2 scenarios to 50MW. The users export will not be limited. | 31/08/2023
Enderby Tertiary | PRO-000430 | CS-05038 | CLUMP FARM SOLAR LIMITED | Enderby 400kV Substation | 100862-201723 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting Tertiary to User Assets for User’s connection. | 01/05/2024
Energy Isles | PRO-000447 | CS-05658 | ENERGY ISLES SHETLAND LIMITED | Energy Isles 132kV Substation | SHET-RI-116 | Kergord - Yell 132kV Connection - on Shetland install a new 132kV single circuit between the Kergord 132kV substation (established as part of SHET-RI-053) and a new tee point on Yell, to enable the connection of renewable generation. (SHET-RI-116) | 30/11/2028
|  | CS-05659 | ENERGY ISLES SHETLAND LIMITED | Energy Isles 132kV Substation | SHET-RI-053 | Shetland 600MW HVDC Link and Kergord 132kV Substation ‒ Construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Noss Head in Caithness. The HVDC switching station works will be part of SHET-RI-062 and will integrate with the Caithness-Moray Transmission Reinforcement (part of SHET-RI-031). The HVDC link includes a 600MW HVDC converter station and 132kV Substation at Kergord in Shetland. The new 132kV Substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of subsea cable between Shetland and the HVDC switching station in Caithness. (SHET-RI-053) | 30/11/2028
|  | CS-06672 | ENERGY ISLES SHETLAND LIMITED | Energy Isles 132kV Substation | Energy Isles Enabling Works | 1. Construction of approximately 20.6 km of a new 132 kV single circuit, comprising 2.0 km UGC and 18.6 km OHL. The circuit will run from the proposed South Yell Switching Station (constructed under SHET-RI-116) to the 132kV Energy Isles substation at the North end of Yell, terminating on a new 132 kV disconnector (103) to be installed within the Energy Isles Wind Farm substation building. The 132kV disconnector (103) will be connected to the TCA 132kV metering circuit breaker (105) and 132kV disconnector (107). 2. The 132 kV circuit will connect to the new South Yell 132 kV Switching Station via 132 kV busbar feeder bay, complete with 1 x 132 kV bus disconnector (307), 1 x 132 kV Circuit Breaker (305), 1 x 132 kV line disconnector (303) and associated protection equipment. | 30/11/2028
Enoch Hill | PRO-000152 | CS-05660 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Enoch Hill 132/33kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 30/05/2023
|  | CS-05661 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Enoch Hill 132/33kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/05/2023
|  | CS-05662 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Enoch Hill 132/33kV Substation | SHET-RI-176 | Pauls Hill/Glenfarclas Circuit Turn In - Move the existing open point from Keith 132kV Substation to Pauls Hill substation and then turn in the Pauls Hill/Glenfarclas circuit to Blackhillock 132kV Substation andrebuild the circuit from Blackhillock substation to Craig watch Substation. This will include the Tee connection onto the existing circuit. (SHET-RI-176 | 30/05/2023
|  | CS-05663 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Enoch Hill 132/33kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 30/05/2023
|  | CS-05664 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Enoch Hill 132/33kV Substation | Enoch Hill Part 1 | 1. Extend the new 132kV substation compound at New Cumnock collector substation site location Grid Reference E251966, N608134 and install 1 x 132kV feeder bay. 2. Establish new 132/33kV substation compound at Enoch Hill Wind Farm site location, Grid Reference E255430,N608980 including the control /switch room 3. Installation of 0.25km of 132kV underground cable between New Cumnock and Enoch Hill Wind Farm substation. 4. Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 30/05/2023
|  | CS-05665 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Enoch Hill 132/33kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/05/2023
|  | CS-05666 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Enoch Hill 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/05/2023
EOLFI Offshore | PRO-001538 | CS-04402 | Shell New Energies UK Ltd | Eolfi Offshore Substation | EOLFI H1 Enabling Works | At Tealing 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Onshore Transmission Licensee and the User (as OTSDUW User) will be the User side of the 400kV feeder circuit breakers/isolators at Tealing 400kV substation. | 31/10/2033
|  | CS-04403 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-04404 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-04405 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-04406 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-04407 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 31/10/2033
|  | CS-04408 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-04409 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-04410 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-04411 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-04412 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-04413 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 31/10/2033
|  | CS-04414 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2033
|  | CS-04415 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-04416 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-04417 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-147 | Tealing 400kV Substation - Establish a new 400kV substation close to the existing Tealing 275kV substation. | 31/10/2033
|  | CS-04418 | Shell New Energies UK Ltd | Eolfi Offshore Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
Eppynt Common | PRO-001882 | CS-05039 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 31/10/2026
|  | CS-05040 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 31/10/2026
|  | CS-05042 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 31/10/2026
|  | CS-05043 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 31/10/2026
|  | CS-05044 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 033769-033769 | Reconductor the Exeter – Hinkley Point – Taunton 400kV circuits to achieve a 2787MVA pre-fault summer rating. | 31/10/2026
|  | CS-05045 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 100424-200970 | Reconductor the Bramley – Melksham 400kV circuits 1 and 2 to achieve a pre-fault summer rating of 1581MVA. | 31/10/2026
|  | CS-05046 | GARREG FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101052-202110 | Install power flow control devices along the Imperial Park – Melksham 400kV circuit | 31/10/2026
Equinor Celtic Sea 1 | PRO-004037 | CS-09246 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-09247 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
|  | CS-09248 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 06/12/2036
|  | CS-09250 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-09245 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Hinkley (Shurton) – Taunton 1 & 2 400kV circuits (2x500mm2 Rubus at 90oC) with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 06/12/2036
|  | CS-09251 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to triple Auriacuria 3 x 700mm2 at 90 degrees to achieve a summer pre-fault rating of 3000MVA | 06/12/2036
|  | CS-09249 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
Equinor Celtic Sea 2 | PRO-004038 | CS-09252 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Hinkley (Shurton) – Taunton 1 & 2 400kV circuits (2x500mm2 Rubus at 90oC) with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 06/12/2036
|  | CS-09254 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
|  | CS-09253 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-09256 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
|  | CS-09257 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-09258 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to triple Auriacuria 3 x 700mm2 at 90 degrees to achieve a summer pre-fault rating of 3000MVA | 06/12/2036
|  | CS-09255 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 06/12/2036
|  | CS-09259 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation | 102622-205256 | 102622-205256 | 06/12/2036
ER BBR Energy | PRO-003508 | CS-09322 | ER PROJECT DEVELOPMENT CO LIMITED | ER BBR Energy 132kV Substation | SPT-RI-003 | Denny-Strathaven 400kV Reinforcement - Construct a new 400kV double circuit overhead line from Bon-nybridge to Newarthill and re-configure associated sites to establish a fourth north to south dou-ble circuit Supergrid route through the Scottish central belt. One side of the new overhead line will oper-ate at 400kV, the other at 275kV. This reinforcement will establish Denny-Bonnybridge, Bonnybridge-Wishaw, Wishaw-Strathaven No.2 and Wishaw-Torness 400kV circuits and a Denny-Newarthill-Easterhouse 275kV circuit. (SPT-RI-003) | 30/10/2029
|  | CS-09324 | ER PROJECT DEVELOPMENT CO LIMITED | ER BBR Energy 132kV Substation | SPT-RI-2815 | New Denny North 275/123kV Super Grid Transformer- At Denny North substation it is proposed to install a new 275/132kV 240MVA Super Grid Transformer to allow for Stirling 132kV and Devonside 132kV substations to be radially fed via Denny North. Reconfiguration of the existing Denny North – Bonnybridge 132kV (CN Route) high capacity circuit is also proposed to create two 132kV feeder circuits between Denny North and Stirling 132kV/Devonside 132kV. These two circuits will be reinforced to accommodate a pre-fault summer rating of 240MVA on each of these circuits. Normally Open Points will be created at Bonnybridge 132kV and Westfield 132kV substations. The works outlined in this TORI are subject to the works being completed under SPT-RI-2083 (Kincardine North – Wishaw 400kV Reinforcement) | 30/10/2029
|  | CS-09323 | ER PROJECT DEVELOPMENT CO LIMITED | ER BBR Energy 132kV Substation | SPT-RI-2083 | Kincardine North – Wishaw 400kV reinforcement (DWUP)- Establish 400kV infrastructure through the centre of the network following the East Coast 400kV onshore incremental (ECUP) reinforcement, but in advance of the completion of existing Denny to Wishaw 400kV reinforcement (DWNO). The scope of this TORI will be aligned with the ‘DWUP’ option submitted to the 2021/22 Network Options Assessment (NOA) process. It is proposed to reconfigure and update existing 275kV single circuit between the Kincardine and Wishaw to 400kV operation to establish a new Kincardine North – Wishaw 400kV circuit. | 30/10/2029
Erebus | PRO-000471 | CS-06300 | BLUE GEM WIND LIMITED | Pembroke 132kV Substation | 100802-201618: | Re-utilise the spare bay at Pembroke 132kV substation to facilitate the connection of a generator bay and extend the Pembroke operational tripping scheme (OTS). | 02/11/2026
|  | CS-06301 | BLUE GEM WIND LIMITED | Pembroke 132kV Substation | 100838-201680 | Replacement of feeder circuit breakers X105 and X305 of Pembroke - Swansea North 400 kV Circuits 1 and 3 and modification of feeder protection to allow faster operation times. | 02/11/2026
Eredine Wind Farm | PRO-002005 | CS-08470 | RWE RENEWABLES UK ONSHORE WIND LIMITED | An Suidhe 275/33kV | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 31/10/2030
|  | CS-08467 | RWE RENEWABLES UK ONSHORE WIND LIMITED | An Suidhe 275/33kV | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 31/10/2030
|  | CS-08472 | RWE RENEWABLES UK ONSHORE WIND LIMITED | An Suidhe 275/33kV | SPT-RI-028 | Dalmally 275kV Extension and Dalmally-Windyhill 275kV Uprating - replace and reconfigure Dalmally 275kV substation to a double busbar arrangement (Scope 1). Uprate the overhead line conductor between Dalmally and Windyhill (Scope 2). Extend Dalmally 275kV Substation and install two new double busbar bays to provide SHE Transmission with two 275kV points of connection at Dalmally 275kV Substation (Scope 3). | 31/10/2030
|  | CS-08468 | RWE RENEWABLES UK ONSHORE WIND LIMITED | An Suidhe 275/33kV | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2030
|  | CS-08471 | RWE RENEWABLES UK ONSHORE WIND LIMITED | An Suidhe 275/33kV | SPT-RI-2317 | Dalmally to Windyhill Reinforcement - It is proposed to uprate the existing overhead line circuits No.1 and No.2 between Dalmally and Windyhill 275kV substations from twin Totara operating at 50°C to 90°C as a minimum. (SPT-RI-2317) | 31/10/2030
|  | CS-08469 | RWE RENEWABLES UK ONSHORE WIND LIMITED | An Suidhe 275/33kV | SHET-RI-130a | North Argyll – Craig Murrail 275kV Operation - Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Creag Dhubh substation (established as part of SHET-RI-013) to Craig Murrail Substation. This will require the upgrade of substations on this circuit for 275kV operation | 31/10/2030
|  | CS-08466 | RWE RENEWABLES UK ONSHORE WIND LIMITED | An Suidhe 275/33kV | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2030
|  | CS-08465 | RWE RENEWABLES UK ONSHORE WIND LIMITED | An Suidhe 275/33kV | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2030
ER MSM Energy | PRO-003480 | CS-09321 | ER PROJECT DEVELOPMENT CO LIMITED | ER MSM Energy 132kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 31/10/2030
|  | CS-09320 | ER PROJECT DEVELOPMENT CO LIMITED | ER MSM Energy 132kV Substation | ER MSM Energy | 1. Extending the Mossmorran substation compound. 2. Installing a new 400kV circuit breaker at Mossmorran. 3. Installing a new 400/132kV 240MVA SGT at Mossmorran. 4. Installing a new 132kV circuit breaker bay at Mossmorran substation. 5. Installing a new 132kV cable/OHL between Mossmorran and ER MSM Energy substation. This circuit should be capable of 222MVA. 6. Installing a new 132kV line disconnector at the ER MSM Energy substation. | 31/10/2030
Erskine Gas Generation | PRO-001203 | CS-06327 | SP Distribution plc | Erskine GSP | SPT-RI-235 - Erskine T1 and T2 132/33kV Transformer Reinforcement | Erskine T1 and T2 132/33kV Transformer Reinforcement - At Erskine GSP the existing GRID T1 and GRID T2 transformers are 30MVA 132/33kV units which have both been identified as being due for replacement during the RIIO-T1 period. It is proposed to replace the two existing 30MVA 132/33kV grid transformers with two 60MVA grid transformers, as well as the associated transformer bay and protection equipment. To minimise outages, the installation of the new T1 and T2 transformers will be carried out offline. | 31/10/2021
Essendine | PRO-001643 | CS-04446 | MALLARD PASS SOLAR FARM LIMITED | Ryhall (Network Rail) GSP | 101515-202984 | Facilitate installation of generator bay (Connection Asset) on Mesh Corner 2 at Ryhall 400kV Substation | 01/01/2028
|  | CS-05041 | MALLARD PASS SOLAR FARM LIMITED | Ryhall (Network Rail) GSP | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 01/01/2028
Euchanhead Wind Farm | PRO-001011 | CS-05667 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation | Euchanhead H1 SS | At Lorg substation, one 132kV line isolator will be installed to tee into the Lorg to Holmhill 132kV circuit. | 29/10/2029
|  | CS-05668 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation | SPT-RI-211 | Construct a new 132kV switching station, named Holm Hill, and install a 132kV OHL circuit between the new site and the tee off points to Shepherds Rig and Lorg wind farms. At an appropriate tee-off point on the New Cumnock to Kendoon 132kV circuit, install the new Holm Hill 132kV Switching Station containing one 132kV circuit breaker with two associated disconnectors. Install ~8km of 132kV wood pole overhead line with High Temperature Low Sag (HTLS) EAGLE conductor (190°C, minimum summer pre-fault rating 295MVA) to the tee point between Shepherd’s Rig and Lorg wind farms. | 29/10/2029
|  | CS-05669 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 29/10/2029
|  | CS-05670 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation | Euchanhead H1 OHL | Installation of approximately 3.5km of 132kV wood pole overhead line from Euchanhead substation to Lorg 132kV substation. | 29/10/2029
|  | CS-05671 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 29/10/2029
Ewerby | PRO-002017 | CS-07826 | SSE UTILITY SOLUTIONS LIMITED | Navenby 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 30/10/2029
|  | CS-07821 | SSE UTILITY SOLUTIONS LIMITED | Navenby 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 30/10/2029
|  | CS-07822 | SSE UTILITY SOLUTIONS LIMITED | Navenby 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 30/10/2029
|  | CS-07819 | SSE UTILITY SOLUTIONS LIMITED | Navenby 400kV Substation | 101687-203363 | Establish a double turn in connection between the new 400kV substation and the West Burton – Bicker Fen 400kV circuit 1 and 2 | 30/10/2029
|  | CS-07824 | SSE UTILITY SOLUTIONS LIMITED | Navenby 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 30/10/2029
|  | CS-07820 | SSE UTILITY SOLUTIONS LIMITED | Navenby 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 30/10/2029
|  | CS-07823 | SSE UTILITY SOLUTIONS LIMITED | Navenby 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 30/10/2029
|  | CS-07825 | SSE UTILITY SOLUTIONS LIMITED | Navenby 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 30/10/2029
|  | CS-07818 | SSE UTILITY SOLUTIONS LIMITED | Navenby 400kV Substation | 101777-203568 | Establishment of new generator bay at new Navenby 400kV substation including bus bar extension and associate P&C and SCS modifications | 30/10/2029
|  | CS-07817 | SSE UTILITY SOLUTIONS LIMITED | Navenby 400kV Substation | 101687-203362 | Build a new Navenby 400kV Double Busbar Substation with 4 Feeder bays, and 1 Coupler Bay, in the vicinity of tower 4ZM508 Extension of the newly built Navenby 400kV substation busbars to accommodate the User’s bay | 30/10/2029
Exeter (Tertiary) | PRO-001047 | CS-05047 | PIVOTED POWER LLP | Exeter 400kV Substation | 030572–030752 | . Creation of a new Melksham Operational Tripping Scheme. | 01/11/2025
|  | CS-05048 | PIVOTED POWER LLP | Exeter 400kV Substation | 100298-200724 | 1. Re-conductor Fleet-Lovedean 400kV double circuits. | 01/11/2025
|  | CS-05049 | PIVOTED POWER LLP | Exeter 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 01/11/2025
|  | CS-06195 | PIVOTED POWER LLP | Exeter 400kV Substation | 100758-201149 | 1. Install earthing transformer on 13kV Tertiary connection 2.Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3.Install 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets for Users connection. 4.Installation of a system to generator Category 2 operational intertripping scheme required for the conditions outlined in F3 Schedule 1. 5. Works required to connect the User to the Melksham Operational Tripping Scheme as described in F3 to be constructed by the User under Customer Build agreement | 01/11/2025
Exeter BESS and PV (Post-Interactivity Revised Offer) | PRO-001827 | CS-05050 | IGP SOLAR 20 LIMITED | Exeter 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 &amp; 2 Circuits to provide a post fault winter rating of 3140MVA. | 31/12/2029
|  | CS-05051 | IGP SOLAR 20 LIMITED | Exeter 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 31/12/2029
|  | CS-05052 | IGP SOLAR 20 LIMITED | Exeter 400kV Substation | 101033-202065 | Installation of stability OTS for the South West, driven by multiple generation customers | 31/12/2029
|  | CS-05054 | IGP SOLAR 20 LIMITED | Exeter 400kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 31/12/2029
|  | CS-05055 | IGP SOLAR 20 LIMITED | Exeter 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 &amp; 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 31/12/2029
|  | CS-05056 | IGP SOLAR 20 LIMITED | Exeter 400kV Substation | 033769-033769 | Reconductor the Taunton - Hinkley Point - Exeter 400kV circuits to achieve a 3100MVA post fault winter rating. Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating | 31/12/2029
|  | CS-05057 | IGP SOLAR 20 LIMITED | Exeter 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a summer post fault rating of 2450MVA. | 31/12/2029
|  | CS-04760 | IGP SOLAR 20 LIMITED | Exeter 400kV Substation | 101563-203114 | At Exeter Main 400kv substation: 1. Extension of existing Main busbar 2 and Reserve busbar 2 to accommodate the installation of generator bay by the User. 2. Local Works required to connect the User to Category 2 intertripping scheme as outline in Appendix F3. 3. Local Works required to connect the User to the Melksham operational Tripping Scheme as described in F3 | 31/12/2029
|  | CS-04761 | IGP SOLAR 20 LIMITED | Exeter 400kV Substation | 101564-203118 | Extension of the Exeter Main 400kV substation into Blacklands Larch Plantation to facilitate Generation connections | 31/12/2029
Exeter Main | PRO-002082 | CS-08930 | ENSO GREEN HOLDINGS LIMITED | Exeter 400kV Substation | 101936-203971 | Infrastructure works at Exeter Main 400kv substation: Extension of existing Main busbar 2 and Reserve busbar 2 to accommodate the installation of generator bay by the User (User Works) | 24/11/2031
|  | CS-08931 | ENSO GREEN HOLDINGS LIMITED | Exeter 400kV Substation | 101564-203118 | Extension of the Exeter Main 400kV substation into Blacklands Larch Plantation to facilitate Generation connections | 24/11/2031
Exeter Main Tertiary | PRO-000452 | CS-05058 | EXETER MAIN BATTERY LIMITED | Exeter 400kV Substation | 100864-201727 | 1. Install earthing transformer on 13kV tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3. Install Disconnector at the 13kV side connecting Tertiary to Connection Assets for User’s connection. 4. Works required to connect the User to the Melksham Operational Tripping Scheme as described in Appendix F3 of the Bilateral Connection Agreement. | 01/05/2024
|  | CS-05059 | EXETER MAIN BATTERY LIMITED | Exeter 400kV Substation | 030572–030752 | . Creation of a new Melksham Operational Tripping Scheme. | 01/05/2024
|  | CS-05060 | EXETER MAIN BATTERY LIMITED | Exeter 400kV Substation | 100298-200724 | Re-conductor Fleet - Lovedean OHL circuits to increase capacity. | 01/05/2024
Eye Grid Services Facility | PRO-003688 | CS-08655 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 102516-205115 | Works to facilitate the Category 4 Operational Tripping scheme as described in Appendix F3 of the Bilateral Connection Agreement | 20/05/2025
|  | CS-08654 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 102333-204493 | Extension of the Main and Reserve busbars at Yaxley 400kV substation to facilitate User connection | 20/05/2025
|  | CS-08656 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ration of at least 28 and a peak withstand of at least 2.7 x RMS break | 20/05/2025
|  | CS-08653 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 032473-032473 | 1.Construction of a new 4 bay indoor GIS double busbar 400kV substation at Yaxley; including two feeder bays, generator bay and bus coupler bay. 2. Replacement of the existing suspension tower with a new terminal tower, tee the new substation to the Bramford – Norwich Main double OHL circuits. 3. Install of cable sealing end compound to provide a duck tee connection underneath OHL. 4. Install an additional circuit breaker on the LV side of SGT3 at Norwich Main to maintain compliance with the SQSS circuit complexity guidance. | 20/05/2025
|  | CS-08652 | CONRAD (EYE) LIMITED | Yaxley 400kV Substation | 102518-205117 | 1. At Yaxley 400kV substation build, connect and commission the new connection bay including but not limited to 400kV circuit breaker, onto the busbars at Yaxley 400kV substation. 2. Associated P & C for a Synch Comp connection. 3. Settlement Metering | 20/05/2025
FAB Link Interconnector | PRO-000281 | CS-05672 | FAB LINK LIMITED | Exeter 400kV Substation | 32311O | Move SVC 5 isolator/disconnectors and extend substation busbars to the West to provide a skeletal bay to connect the HVDC interconnector. | 01/10/2027
|  | CS-05673 | FAB LINK LIMITED | Exeter 400kV Substation | 32311SI | Extend the substation busbar to the East to provide a skeletal bay to connect the HVDC interconnector. | 01/10/2027
Fallago Rig 2 | PRO-000526 | CS-04266 | EDF ENERGY RENEWABLES LIMITED | Fallago 400kV Substation | SPT-RI-125 Thornton Bridge to Torness 400kV Cable Upgrade | it is proposed that the Thornton Bridge / Torness 400kV cable will be uprated. This will be achieved by banking one of the redundant 400kV cables between Branxton / Torness that are to be decommissioned to the existing Thornton Bridge / Torness 400kV cable in order to give a circuit capacity of not less than 1,033MVA (approximately 1,200MVA pre-fault summer rating could be achieved). | 30/01/2028
|  | CS-04267 | EDF ENERGY RENEWABLES LIMITED | Fallago 400kV Substation | SPT-RI-204 Wishaw - Smeaton - Torness - Eccles Overload Protection Scheme | An overload protection scheme installed within Wishaw - Smeaton - Torness - Eccles 275kV and 400kV network in order to protect the system in compliant Category 2 Intertripping Scheme as defined by the Grid Code. The Interrtripping Scheme will disconnect the generation within the area following system outage conditions being met. | 30/01/2028
|  | CS-04268 | EDF ENERGY RENEWABLES LIMITED | Fallago 400kV Substation | SPT-RI-212 East - West 400kV Upgrade (Strathaven - Torness) | The existing Strathaven-Wishaw, Wishaw-Kaimes and Kaimes-Smeaton 275kV circuits will be reconfigured and uprated to 400kV operation. A second cable per phase will be installed on the Torness-Eccles 400kV circuits. | 30/01/2028
Fancott | PRO-002174 | CS-07828 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 101927-203938 | At Sundon 400kV: Replace circuit breakers X130, X510 and X710. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2031
|  | CS-07863 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 30/10/2031
|  | CS-07850 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 100952-201899 | 12. Reconductor EAST CLAYDON-LEIGHTON BUZZARD (ECLA4- LEIB4B- 1) 400kV circuit to achieve more than 2095MVA summer pre-fault rating. | 30/10/2031
|  | CS-07831 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 30/10/2031
|  | CS-07861 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 30/10/2031
|  | CS-07859 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 30/10/2031
|  | CS-07860 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 30/10/2031
|  | CS-07839 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 00468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 30/10/2031
|  | CS-07832 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 102011-204165 | 3. At Norwich Main 400kV: Replace circuit breakers X320, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2031
|  | CS-07835 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 30/10/2031
|  | CS-07833 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 102012-204166 | 4. At Rye House 400kV: Replace circuit breakers X130. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2031
|  | CS-07827 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 102046-204213 | Extend Sundon 400kV substation Main and Reserve 1 busbars for the provision of one User Bay | 30/10/2031
|  | CS-07864 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 30/10/2031
|  | CS-07855 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 101265 - 202507 | 12. Reconductor the Millbrook – Sundon 1 and 2 400 kV circuits | 30/10/2031
|  | CS-07834 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2031
|  | CS-07830 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 30/10/2031
|  | CS-07837 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 30/10/2031
|  | CS-07838 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm2 and 3M curlew 2x490mm2 @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm2 conductor | 30/10/2031
|  | CS-07862 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3820 MVA | 30/10/2031
|  | CS-07836 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 30/10/2031
|  | CS-07829 | SSE UTILITY SOLUTIONS LIMITED | Sundon 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 30/10/2031
Fasque Windfarm | PRO-001009 | CS-05674 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Fasque Wind Farm 132kV Substation | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 31/10/2028
|  | CS-05675 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Fasque Wind Farm 132kV Substation | Fasque H1 Works | The new 120MVA 132/33kV Grid Transformer will be connected to a new 132kV circuit switcher, installed within the substation compound. This will be connected to approximately 10km of wood pole overhead line towards Brechin 132kV Substation, terminating within a cable sealing end compound near the A90 dual carriageway. An approximately 4km length of cable shall be installed, continuing the 132kV circuit from the Cable Sealing End Compound to the Brechin 132kV substation. This is required to cross the A90 dual carriageway and under the XT1/XT2 double circuit 275kV tower line. | 31/10/2028
|  | CS-05676 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Fasque Wind Farm 132kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2028
|  | CS-05677 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Fasque Wind Farm 132kV Substation | SHET-RI-131 Brechin 132kV | Construct two new circuit breakers at Brechin Grid Supply point. | 31/10/2028
Faw Side Community Wind Farm | PRO-000297 | CS-05679 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | Faw Side Item 6 | Reinforce the Junction V to Harker 132kV circuit (from tower AL068 to Harker 132kV substation), to provide a minimum summer pre-fault continuous rating of 202MVA. | 31/10/2025
|  | CS-05680 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 31/10/2025
|  | CS-05681 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | Faw Side Item 1 | Establish a 132kV substation compound at Faw Side Community Wind Farm site. | 31/10/2025
|  | CS-05682 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | Faw Side Item 5 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of this Bilateral Connection Agreement | 31/10/2025
|  | CS-05683 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 31/10/2025
|  | CS-05684 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | Faw Side Item 3 | Install two approximately 5km of 132kV wood pole overhead line (with a minimum summer pre-fault continuous rating of 139MVA) from Faw Side Community Wind Farm substation, to the Gretna to Hawick 132kV tower line (V Route). | 31/10/2025
|  | CS-05685 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 31/10/2025
|  | CS-05686 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | SPT-RI-230 | It is proposed to reconductor approximately 36km of the 132kV overhead line existing Gretna to Hawick circuit (AL and V Route), between Gretna and the proposed Faw Side Community Wind Farm ‘T’ connection. It is proposed to utilise LARK HTLS conductor. NGET own a section of AL and V Route on this circuit and will have to reinforce to match the SPT proposals. | 31/10/2025
|  | CS-05687 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | Faw Side Item 2 | Install a 132kV busbar, two 132kV circuit breakers and associated disconnectors. | 31/10/2025
|  | CS-05688 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | NGET-100406-200937 | Reinforcement of Junction V to Harker 132kV circuit (from tower AL068 to Harker 132kV substation) and from Chapelcross to Harker in correspondence to SPT-RI-227, SPT-RI-230 and SPT-RI-233, including second ‘Tee’ at Junction V and second 132kV circuit to Harker 132kV substation. | 31/10/2025
|  | CS-05678 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | Faw Side Item 4 | On V Route, install a junction tower and appropriate length of 132kV cabling required to form a double ‘T’ connection for the Faw Side Community Wind Farm 132kV circuit onto the Gretna to Hawick 132kV circuits (both north and south circuits). | 31/10/2025
|  | CS-03700 | COMMUNITY WINDPOWER LIMITED | Faw Side Community Wind Farm Substation | SPT-RI-288 Hawick to Galashiels 132kV Reconfiguration | Hawick 132/33kV substation is currently supplied via two 132kV circuits from Gretna 400/132kV substation, with a 132kV circuit to Galashiels normally open at CB 205. With the proposed connection of Faw Side wind farm (250MW) it is proposed to reconfigure Hawick 132kV substation such that Hawick can be supplied from Galashiels and establish the Hawick / Galashiels 132kV circuit No.1 and No.2. Works at Galashiels will be required to terminate the double circuit from Hawick post reconfiguration. At Hawick, it is also proposed to install two new 132kV circuit breakers and a fourth 132kV circuit at Hawick with Poplar conductor:. The existing circuit breakers at Galashiels are of 600A and 800A. It is also proposed to replace the 600A circuit breakers 120 and 620 with a standard 2000A circuit breaker. | 31/10/2025
Feckenham | PRO-001600 | CS-05068 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 21/07/2029
|  | CS-05069 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 21/07/2029
|  | CS-05070 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 21/07/2029
|  | CS-05071 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor. | 21/07/2029
|  | CS-05072 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101284-202534 | Reconductor the existing 2x570mm2 conductor on the IronBridge- Legacy 2 and IronBridge Shrewsbury-Legacy 400 kV circuits with 2x570mm2 conductor at 90 deg. C to achieve a pre fault summer rating of 2490 MVA | 21/07/2029
|  | CS-05073 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 21/07/2029
|  | CS-05062 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 21/07/2029
|  | CS-05063 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 21/07/2029
|  | CS-05064 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 21/07/2029
|  | CS-05065 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 21/07/2029
|  | CS-05066 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 1820 MVA. | 21/07/2029
|  | CS-05067 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101316-202621 | Hotwire A881 East Claydon – Cowley 400kV circuit (36.3km, 4x400mm2 zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 21/07/2029
|  | CS-04699 | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation | 101496-202909 | Extension of the existing Feckenham 400kV Main and Reserve Busbars to accommodate the User's bay. | 21/07/2029
| PRO-002189 | CS-08908 | ENSO GREEN HOLDINGS LIMITED | Feckenham 400kV Substation | 102107-204301 | Extension of 400kV main and reserve busbar of Feckenham 400kV substation to accommodate the user’s new section. | 31/10/2033
|  | CS-08910 | ENSO GREEN HOLDINGS LIMITED | Feckenham 400kV Substation | 102092-204285 | Install static VAR compensation system and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation. | 31/10/2033
|  | CS-08909 | ENSO GREEN HOLDINGS LIMITED | Feckenham 400kV Substation | 102092-204283 | Install 400/66kV 180MVA SGT2 and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation | 31/10/2033
Feckenham Energy Park | PRO-002378 | CS-08865 | GREEN ENERGY MAB LTD | Feckenham 400kV Substation | 102092-204283 | Install 400/66kV 180MVA SGT2 and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation. | 31/10/2033
|  | CS-08863 | GREEN ENERGY MAB LTD | Feckenham 400kV Substation | 102092-204285 | Install static VAR compensation system and associated switchgear including 400kV circuit breaker to Feckenham 400kV substation. | 31/10/2033
|  | CS-08862 | GREEN ENERGY MAB LTD | Feckenham 400kV Substation | 102189-204410 | Extension of 400kV main and reserve busbar of Feckenham 400kV substation to accommodate the Users new section | 31/10/2033
Feckenham Green Energy Centre | PRO-001767 | CS-05361 | INNOVA RENEWABLES LIMITED | Feckenham 400kV Substation | 101361-202681 | At Feckenham 275 kV substation, a. Extension of Feckenham 275kV substation b. Extension of main and reserve busbar of Feckenham 275 kV substation | 30/10/2032
|  | CS-05362 | INNOVA RENEWABLES LIMITED | Feckenham 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2032
|  | CS-05363 | INNOVA RENEWABLES LIMITED | Feckenham 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2032
|  | CS-05364 | INNOVA RENEWABLES LIMITED | Feckenham 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2032
|  | CS-05365 | INNOVA RENEWABLES LIMITED | Feckenham 400kV Substation | 101431-202809 | Hotwire A842 Cowley-Didcot 400kV circuit (6.496km, 4x400mm2 zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA | 30/10/2032
|  | CS-05366 | INNOVA RENEWABLES LIMITED | Feckenham 400kV Substation | 101431-202809 | Hotwire A842 Cowley-Didcot 400kV circuit (6.496km, 4x400mm2 zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA | 30/10/2032
|  | CS-05367 | INNOVA RENEWABLES LIMITED | Feckenham 400kV Substation | 101431-202809 | Hotwire A842 Cowley-Didcot 400kV circuit (6.496km, 4x400mm2 zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA | 30/10/2032
Feckenham Greener Grid Park | PRO-001008 | CS-05061 | STATKRAFT UK LTD | Feckenham 400kV Substation | 100773-201565 | 1. Extend the 400kV AIS busbars to accommodate a new generator bay at Feckenham 400kV substation. 2. Upgrade the Substation Control System and protection. | 31/01/2026
Fell Wind Farm | PRO-001755 | CS-05258 | ENERGYFARM UK FELL LLP | Fell Wind Farm 132/33kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 30/10/2028
|  | CS-05259 | ENERGYFARM UK FELL LLP | Fell Wind Farm 132/33kV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 30/10/2028
|  | CS-05260 | ENERGYFARM UK FELL LLP | Fell Wind Farm 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/10/2028
|  | CS-05261 | ENERGYFARM UK FELL LLP | Fell Wind Farm 132/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 30/10/2028
|  | CS-05262 | ENERGYFARM UK FELL LLP | Fell Wind Farm 132/33kV Substation | SPT-RI-2165 | Whiteneuk to Glenlee 132kV OHL and substation works | 30/10/2028
|  | CS-05263 | ENERGYFARM UK FELL LLP | Fell Wind Farm 132/33kV Substation | Fell Wind Farm Enabling Works | At Whiteneuk substation, installation of one 132kV circuit breaker and associated disconnectors and install approximately 5km of 132kV trident wood pole OHL (Poplar) between Whiteneuk and Fell substations. At Fell wind farm substation, install one 132kV line isolator | 30/10/2028
Fenwick Solar Project | PRO-001915 | CS-07991 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 16/04/2032
|  | CS-07999 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 16/04/2032
|  | CS-07994 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 101855-203810 | Reconductoring of Macclesfield to Stalybridge line (A23A) with 1530MVA prefault rating during Summer | 16/04/2032
|  | CS-07989 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 101679-203342 | Extension of busbars at Thorpe Marsh 400kV DBB substation to provide connection point for Customer's bay including P&amp;C, database updates, Assurance, Operation and Commissioning works. | 16/04/2032
|  | CS-07995 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 101276-202522 | Reconductoring of Ryhall to Eaton Socon line (A484) with 3820MVA postfault rating during Winter | 16/04/2032
|  | CS-08001 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100944-201881 | Development and submission of DCO for - Grimsby West substation extension - New 400kV OHL Lincolnshire North section - New 400kV Substation Lincolnshire Coastal Node - New 400kV OHL Lincolnshire South section - New 400kV substation near Weston Marsh | 16/04/2032
|  | CS-07992 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 16/04/2032
|  | CS-08004 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 16/04/2032
|  | CS-07997 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100816-201651 | Reconductor Cottam- Grendon ZDA and ZA OHL with 3090MVA rating postfault during Winter | 16/04/2032
|  | CS-08000 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100944-201880 | Modifications to Grimsby West substation for the new Lincolnshire GREEN 400kV OHL | 16/04/2032
|  | CS-08003 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 16/04/2032
|  | CS-08005 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100944-201882 | Build a new 400kV Mablethorpe Substation with 6 Bays - 4 Feeder bays, 1 Coupler Bay, 2 Section Breakers Main and Reserve | 16/04/2032
|  | CS-08002 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 16/04/2032
|  | CS-07990 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 16/04/2032
|  | CS-07993 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 100903-201816 | Eggborough-Thorpe Marsh- circuit cable uprating to 2780MVA during Winter post fault rating | 16/04/2032
|  | CS-07996 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 101264-202506 | Cottam-Ryhall reconductoring with 3820MVA post-fault rating during Winter | 16/04/2032
|  | CS-07998 | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation | 101504-202965 | Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit to provide a post-fault summer rating of 3300 MVA:  Reconductor the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for the Drax – Keadby – Thorpe Marsh circuit. | 16/04/2032
Ferrybridge D | PRO-001020 | CS-05074 | KEADBY GENERATION LIMITED | Ferrybridge C 275kV Substation | 100049-200108 | 1. Provision of two skeletal bays for the User to connect at Ferrybridge ‘C’ 275kV substation. 2. To facilitate the User Works within the connection site. 3. SCS database changes and busbar protection modification at Ferrybridge ‘C’ 275kV substation. The existing generator skeletal bay assets are to be transferred to the User, subject to approval from The Authority If the existing disconnected bay assets cannot be transferred to the User, The Relevant Transmission Licensee will revise the construction works accordingly. | 06/10/2028
Ferrymuir Energy Storage | PRO-001352 | CS-06224 | FERRYMUIR ENERGY STORAGE LIMITED | Cupar GSP | SPT-RI-234 | Glenniston 132kV Substation Reinforcement and Associated Works to increase the thermal rating of the equipment: a. Glenniston 132kV T1 LVDOC Relay. b. Glenniston 132kV T2 LVDOC Relay. In addition, replacement of the 132kV disconnectors 124 and 128 and bus section circuit breaker 120 to achieve a minimum rating of 185MVA. | 31/10/2022
|  | CS-06225 | FERRYMUIR ENERGY STORAGE LIMITED | Cupar GSP | SPT-RI-1577 | Cupar GSP LV Protection Modifications - In order to remain within SPEN policy (PROT-01-107), the existing Alstom/Areva K-series LVDOC relays on the T1 and T2 and Cupar 132/33kV GSP are required to be replaced with a LVDOC relay which utilises a voltage controlled characteristic such that reverse power flow is only limited by the rating of the transformer (including emergency ratings). | 31/10/2022
Fetteresso Wind Farm | PRO-000927 | CS-05692 | FETTERESSO WIND LIMITED | Mid Hill GSP | No Enabling Works | No enabling works | 30/09/2026
Fferm Solar Pentir | PRO-001049 | CS-05075 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 032018-032019 | Reconductor the existing Pentir-Bodelwyddan Circuits 1 and 2 Increase Thermal Capability of A220 Pentir-Trawsfynydd circuit; | 01/05/2027
|  | CS-05076 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 033711-033711 | Uprating of current cable sections | 01/05/2027
|  | CS-05077 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 033708-033708 | Build second core per phase | 01/05/2027
|  | CS-05078 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 033712-033712 | Reconductor existing twin Sorbus OHL section to twin Araucaria. | 01/05/2027
|  | CS-05053 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 032018-032018 | Reconductor the existing Bodelwyddan - Connah’s Quay Circuits 1 and 2 | 01/05/2027
|  | CS-04646 | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation | 101039-202076 | 1. Install a tertiary cable box or bushings on the SGT 2. 2. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 5. Local works required to connect the User to the Pentir Operational Tripping Scheme as described in F3 to the Bilateral Connection Agreement. | 01/05/2027
Fiddes Battery Storage | PRO-001831 | CS-07245 | FIDDES BATTERY LIMITED | Fiddes GSP | Fiddes A1 Works | Within a new 275/33kV substation compound, install two new 120MVA 275/33kV transformers, 33kV circuit breakers and associated disconnector, and associated battery and protection schemes. From the new 33kV transformer circuit breakers, install two approximately 3km cable circuits (one per transformer circuit), four cores per phase, from the new transformer location back to the existing Fiddes GSP substation and connect into the existing 1T0 and 2T0 33kV metering circuit breakers | 31/10/2028
|  | CS-07246 | FIDDES BATTERY LIMITED | Fiddes GSP | Fiddes A1 Works | Installation of two new 275kV transformer circuit breakers, and associated disconnectors, connected to the new 275/33kV transformer arrangement. | 31/10/2028
|  | CS-07247 | FIDDES BATTERY LIMITED | Fiddes GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 31/10/2028
Fife Grid Services | PRO-000453 | CS-04634 | BLUEGRIDPOWER LTD | Fife Grid Services Facility 275kV Substation | SPT-RI-1745 | Kincardine to Fife Grid 275kV Switchgear and Cable Works - To facilitate the connection of contracted generation from the Relevant Transmission Licensee’s Fife Grid Services Facility 275kV substation to Kincardine 275kV substation, it is proposed to install a new 275kV busbar and associated 275kV disconnectors and approximately 0.9km of 275kV underground cable circuit to Kincardine 275kV substation. At Kincardine 275kV substation, install a new 275kV GIS switchgear and associated disconnectors and one 275kV line isolator. | 12/04/2024
Five Estuaries Offshore Wind Farm | PRO-000450 | CS-06342 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100874-201758 | Build a new 11 bay East Anglia Coastal 400 kV double busbar substation – 2off busbar couplers, 1 Main & Reserve section, 8 feeder bays | 31/10/2030
|  | CS-06343 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100879-201769 | Install 2-off 225 Mvar MSCs at Bramford 400 kV substation.Extension of Bramford 400 kV substation to accommodate the new MSCs. | 31/10/2030
|  | CS-06344 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100874-201760 | Build a new 400 kV double circuit between Sizewell 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter postfault. Extension of Sizewell 400 kV substation to accommodate 2 feeders from East Anglia Coastal 400 kV. | 31/10/2030
|  | CS-06345 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 31/10/2030
|  | CS-06346 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100875-201761 | Build a new 400 kV double circuit between Bramford 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter postfault. Extension of Bramford 400 kV substation to accommodate 2 feeders from East Anglia Coastal 400 kV substation. Run Bramford 400 kV substation 2-way vertical split. | 31/10/2030
|  | CS-06347 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100875-201762 | Build a second new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent | 31/10/2030
|  | CS-06348 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100596-201227 | Single Bay Extension at East Anglia Coastal 400 kV substation to facilitate the User’s connection. | 31/10/2030
|  | CS-06349 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 31/10/2030
|  | CS-06350 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation |  | FALSE | 31/10/2030
|  | CS-06351 | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 31/10/2030
Flash Solar Farm | PRO-001634 | CS-05079 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 100844-201689 | Reconductor Cottam – Staythorpe 1 circuit. | 01/08/2025
|  | CS-05080 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 100450-201015 | Uprate Cottam – Keadby OHL circuits 1 & 2. | 01/08/2025
|  | CS-05084 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 100591-201213 | Reconductor Ratcliffe – Staythorpe 400kV circuit; reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 2780MVA | 01/08/2025
|  | CS-05085 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 033946-033946 | At Keadby 400kV substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 01/08/2025
|  | CS-05086 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 101245-202485 | Reconductor the existing 4x400mm2 conductor on the Eaton Socon – Wymondley 2 400kV circuit with 2x850mm2 90oC conductor to achieve a pre fault summer rating of 2400 MVA | 01/08/2025
|  | CS-05087 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 01/08/2025
|  | CS-04685 | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 101565-203122 | Extend the busbar at Staythorpe 400kV substation to make provision for the User to connect their generator bay. | 01/08/2025
Fleet (Tertiary) | PRO-001087 | CS-05081 | CSE23 LIMITED | Fleet 400kV Substation | 100851-201705 | 1. Extend Mesh Corner 3 at Fleet 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new bus bar, 33kV substation at Fleet to be connected via new 400/33kV SGT. 4. Installation of an earthing transformer connecting onto the 33kV busbar. 5. Installation of new circuit breaker on HV side of SGT3A.* *The exact placement will be confirmed in the detailed design stage. | 31/10/2025
|  | CS-05088 | CSE23 LIMITED | Fleet 400kV Substation | 100298-200724 | Re-conductor Fleet - Lovedean OHL circuits to increase capacity. | 31/10/2025
|  | CS-05089 | CSE23 LIMITED | Fleet 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 31/10/2025
Fleet EGH (Tertiary) | PRO-000544 | CS-05090 | ENSO GREEN HOLDINGS LIMITED | Fleet 400kV Substation | 100901-201810 | 1. Install earthing transformer 2. Install a tertiary cable box or bushings on the SGT1A 3. Install 13kV cable (if required) from Tertiary cable box or bushings to the earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 5. Works required to connect the User to the Melksham Operational Tripping Scheme as described in Appendix F3 to the Bilateral Connection Agreement. | 31/10/2025
|  | CS-05092 | ENSO GREEN HOLDINGS LIMITED | Fleet 400kV Substation | 030572–030752 | . Creation of a new Melksham Operational Tripping Scheme. | 31/10/2025
|  | CS-05093 | ENSO GREEN HOLDINGS LIMITED | Fleet 400kV Substation | 100298-200724 | Re-conductor Fleet - Lovedean OHL circuits to increase capacity. | 31/10/2025
|  | CS-05094 | ENSO GREEN HOLDINGS LIMITED | Fleet 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 31/10/2025
Fleet Tertiary | PRO-000429 | CS-05095 | FLEET SOLAR LIMITED | Fleet 400kV Substation | 100851-201705 | 1. Extend Mesh Corner 3 at Fleet 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new bus bar, 33kV substation at Fleet to be connected via new 400/33kV SGT. 4. Installation of an earthing transformer connecting onto the 33kV busbar. 5. Installation of new circuit breaker on HV side of SGT3A.* *The exact placement will be confirmed in the detailed design stage. | 30/11/2025
|  | CS-05096 | FLEET SOLAR LIMITED | Fleet 400kV Substation | 030572–030752 | . Creation of a new Melksham Operational Tripping Scheme. | 30/11/2025
|  | CS-05098 | FLEET SOLAR LIMITED | Fleet 400kV Substation | 100298-200724 | Re-conductor Fleet - Lovedean OHL circuits to increase capacity. | 30/11/2025
|  | CS-05099 | FLEET SOLAR LIMITED | Fleet 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 30/11/2025
Flemyland Battery Storage | PRO-002360 | CS-08262 | Flemyland Battery Storage Ltd | Kilwinning | SPT-RI-2709 | CE Route Reconductoring and KILW-HUER Cable Replacement - It is proposed to reconductor the OHL route with 425mm2 ‘Totara’ AAAC @ 75°C to achieve a minimum rating of 220MVA per circuit In addition to the OHL works,it is also proposed to replace the existing ~3.2km of 132kV cable between KILW-HUNF and HUNF-HUER to achieve a similar 220MVA rating per circuit. | 26/10/2027
|  | CS-08263 | Flemyland Battery Storage Ltd | Kilwinning | SPT-RI-2710 | BU Route OHL Reconductor - As part of RIIO-T2 asset modernisation a number of assets across the transmission network have been identified for replacement. This TORI captures the asset modernisation work that is scheduled to be carried out on the 132kV OHL BU Route which runs between KILW-HUNF-HUNE at ~13km. The OHL circuit will be reconductored to achieve a minimum of 220MVA per circuit (Reconductor with 425mm2 ‘Totara’ AAAC @ 75°C) | 26/10/2027
Flooring Porter | PRO-003876 | CS-09055 | Flooring Porter Ltd | Tween Bridge 400kV | 102360-204779 | Uprating/Replacement of the following Circuit breakers at Creyke Beck 400kV substation X510, X130, X420, X430, X520, X620, X330, X1215, X905, X210, X1415, X320 | 29/11/2033
|  | CS-09058 | Flooring Porter Ltd | Tween Bridge 400kV | 101954-204035 | COTT4 X320, X430, X705 and X605 Circuit Breaker replacement to 63kA and with tested X/R at least 28 | 29/11/2033
|  | CS-09026 | Flooring Porter Ltd | Tween Bridge 400kV | 101865-203833 | 1. Build a new Tween Bridge 400kV double busbar AIS substation with 3 generator skeleton bay, 1 coupler bay and 2 feeder bays. 2. Establish a double turn in connection between the new Tween Bridge 400kV substation and Keadby-Drax-Thorpe Marsh line (A37C) | 29/11/2033
|  | CS-09028 | Flooring Porter Ltd | Tween Bridge 400kV | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 29/11/2033
|  | CS-09027 | Flooring Porter Ltd | Tween Bridge 400kV | 102391-204911 | Establish a new generator bay at new Tween Bridge 400kV substation including busbar extension and associate P&C and SCS modifications | 29/11/2033
|  | CS-09059 | Flooring Porter Ltd | Tween Bridge 400kV | 100597-201228 | THTO4 X405, X805, X230 and X705 Circuit Breaker replacement to 63kA. Establish an additional section breaker in place of X224 or X228 and add another section breaker in place of X428 or X424. | 29/11/2033
|  | CS-09035 | Flooring Porter Ltd | Tween Bridge 400kV | 102198-204418 | Construction of a new 400kV AIS substation at Thormanby comprising of 4 feeder bays, 1 generator bay, 1 bus coupler bay and a bus section bay | 29/11/2033
|  | CS-09048 | Flooring Porter Ltd | Tween Bridge 400kV | 100449-201014 | Uprate the Drax – Eggbrough 1 circuit to achieve a post fault summer rating of 2500MVA | 29/11/2033
|  | CS-09030 | Flooring Porter Ltd | Tween Bridge 400kV | 102356-204777 | Uprating/Replacement of the following Circuit breakers for a higher X/R ratio of 25 at Drax 400kV substations: X430, X630, X405. | 29/11/2033
|  | CS-09043 | Flooring Porter Ltd | Tween Bridge 400kV | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 29/11/2033
|  | CS-09053 | Flooring Porter Ltd | Tween Bridge 400kV | 0333496-0333496 | AD4, install a 2750MVA 16 Ohm Series Reactor on the KeadbyWest Burton 1 circuit | 29/11/2033
|  | CS-09032 | Flooring Porter Ltd | Tween Bridge 400kV | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 29/11/2033
|  | CS-09033 | Flooring Porter Ltd | Tween Bridge 400kV | 101705-203408 | Reconductor the Norton - Lackenby 400kV circuit and uprate the substation cable at the Lackenby substation. | 29/11/2033
|  | CS-09047 | Flooring Porter Ltd | Tween Bridge 400kV | 101504-202965 | Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit to provide a post-fault winter rating of 3820MVA: • Reconductor the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C • At Keadby 400kV substation, replace the X1005 feeder bay for the Drax – Keadby – Thorpe Marsh circuit | 29/11/2033
|  | CS-09052 | Flooring Porter Ltd | Tween Bridge 400kV | 101625-203259 | Uprate the Drax - Eggborough 2 circuit to achieve a post fault summer rating of 2500MVA. | 29/11/2033
|  | CS-09054 | Flooring Porter Ltd | Tween Bridge 400kV | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the KeadbyCreyke Beck/Killingholme circuit (A35E) (Keadby Leg) | 29/11/2033
|  | CS-09056 | Flooring Porter Ltd | Tween Bridge 400kV | 101041-202083 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +8 ohms along the Cottam – West Burton 1 (A413) 400kV circuit | 29/11/2033
|  | CS-09046 | Flooring Porter Ltd | Tween Bridge 400kV | 100903-201816 | Eggborough-Thorpe Marsh- circuit cable uprating to 2780MVA during Winter post fault rating | 29/11/2033
|  | CS-09049 | Flooring Porter Ltd | Tween Bridge 400kV | 100455-201020 | At Keadby 400kV substation: • Transpose the Cottam 1 circuit with the West Burton 1 circuit. Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax –Keadby – Thorpe Marsh 400 kV circuit | 29/11/2033
|  | CS-09050 | Flooring Porter Ltd | Tween Bridge 400kV | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3820MVA | 29/11/2033
|  | CS-09057 | Flooring Porter Ltd | Tween Bridge 400kV | 102056-204226 | Uprating/Replacement of the following Circuit breakers for a higher X/R ratio of 25 at West Burton 400kV substation X120, X320, X220 | 29/11/2033
|  | CS-09029 | Flooring Porter Ltd | Tween Bridge 400kV | 100452-201222 | At Drax 400kV Substation: Replace circuit breakers X420, X520 and X105. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 29/11/2033
|  | CS-09037 | Flooring Porter Ltd | Tween Bridge 400kV | 101807-203697 | New EDN2 Chesterfield – Ratcliffe-on-Soar 400kV double circuit | 29/11/2033
|  | CS-09045 | Flooring Porter Ltd | Tween Bridge 400kV | 100821-201989 | Uprating of the Creyke Beck - Humber Refinery – Keadby and Creyke Beck - Keadby – Killingholme circuits to achieve at least 3320MVA post fault summer - On 2KN and 2AC legs as required | 29/11/2033
|  | CS-09051 | Flooring Porter Ltd | Tween Bridge 400kV | 102358-204778 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +20ohms along the Drax-Thornton 2 400kV circuit | 29/11/2033
|  | CS-09031 | Flooring Porter Ltd | Tween Bridge 400kV | 102204-204427 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to 4ohms along the Lackenby-Thornton 1 400kV circuit. | 29/11/2033
|  | CS-09040 | Flooring Porter Ltd | Tween Bridge 400kV | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 29/11/2033
|  | CS-09041 | Flooring Porter Ltd | Tween Bridge 400kV | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 29/11/2033
|  | CS-09042 | Flooring Porter Ltd | Tween Bridge 400kV | 101386-202715 | Reconductor Lackenby –Thornton double circuit with 3 x 700mm2 at 90°C. Replace the disconnectors on both Thornton circuits at Lackenby substation, to equipment with an equal rating to provide a pre fault summer rating of 2790MVA | 29/11/2033
|  | CS-09044 | Flooring Porter Ltd | Tween Bridge 400kV | 100821-201659 | Uprate the Keadby legs and Creyke Beck legs of both Creyke Beck - Humber Refinery – Keadby 400kV and Creyke Beck -Keadby – Killingholme 400kV circuits to achieve a post fault summer rating of 2800MVA. | 29/11/2033
|  | CS-09034 | Flooring Porter Ltd | Tween Bridge 400kV | 102208-204431 | Uprating of OHL double cct from 2TW110 - 2TW169 and 4YR1 - 4YR40 which is part of the current Norton-Osbaldwick double circuit but will become the new Osbaldwick-Overton-Thormanby circuit | 29/11/2033
|  | CS-09036 | Flooring Porter Ltd | Tween Bridge 400kV | 030613-030613 | Uprate the Cottam - Staythorpe (2) circuit to provide a post-fault summer rating of 2800 MVA | 29/11/2033
|  | CS-09038 | Flooring Porter Ltd | Tween Bridge 400kV | 101706-203409 | Uprating of the Osbaldwick-Thornton 1 & 2 circuits to achieve a pre fault summer rating of 2500MVA | 29/11/2033
|  | CS-09039 | Flooring Porter Ltd | Tween Bridge 400kV | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 29/11/2033
Fordtown Battery Storage | PRO-000888 | CS-04469 | SUSI EELPOWER FORDTOWN LIMITED | Kintore GSP | Fordtown Enabling Works | The Relevant Transmission Licensee shall provide status signals to the Host Distribution Network Operator from the 33kV breakers 1TO, 2TO and 3TO, and the 132kV circuit breakers 1310, 110 and 210. This will also include the provision signals for a loss of mains scheme as requested by the Host Distribution Network Operator. | 01/07/2022
Forss BP Wind Turbine | PRO-000639 | CS-05702 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 31/08/2025
|  | CS-05703 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/08/2025
Fraserburgh Energy Plant | PRO-001820 | CS-07440 | FRASERBURGH ENERGY LTD | Fraserburgh GSP | Fraserburgh Enabling Works | 1. This scheme requires an intertrip for the loss of either of the Grid Transformers at Fraserburgh 132/33kV GSP. These signals will be provided to the User via a separate relay panel within the 33kV Switch room from the signals described below. Provision of status signals are required for the following: a. Status signals from the 33kV circuit breakers and disconnectors at Fraserburgh GSP b. Status signals from the 132kV circuit breakers and disconnectors at Fraserburgh GSP c. Status signals from the 132kV circuit breakers and disconnectors at St Fergus Switching Station 2. Modification to the existing LV Directional Overcurrent (DOC) protection settings at Fraserburgh 132/33kV substation will also be required. 3. A loss of mains scheme will also be configured at Fraserburgh GSP as requested by the Host Distribution Network Operator. | 20/09/2024
|  | CS-07441 | FRASERBURGH ENERGY LTD | Fraserburgh GSP | Fraserburgh Enabling Works | The Enabling Works Stage 2 comprise the completion of the One Off Works Stage 1 and the following: 1. An additional intertripping scheme is required for the loss of one of the 132kV circuits between St Fergus and Peterhead (VS1, VS2 and VS3). These signals will be provided to the User via a separate relay panel within the 33kV Switchroom from the signals described below. Provision of status signals are required for the following: a. Status signals from the 132kV circuit breakers and disconnectors at St Fergus Switching Station b. Status signals from the 132kV line circuit breakers and disconnectors at the Salamander tee in point. | 20/09/2024
Fraserburgh Energy Storage | PRO-002258 | CS-08859 | FLEXION ENERGY UK STORAGE LTD | Fraserburgh GSP | SHET-RI-150 | Inverguie Tee – Peterhead 132kV Reconductoring – Reconductor approximately 6.7km of 132kV OHL between the Inverguie Tee and Peterhead 132kV substation. The circuit should be reconductored with a conductor capable of a minimum summer pre-fault rating of 226MVA | 31/10/2027
|  | CS-08860 | FLEXION ENERGY UK STORAGE LTD | Fraserburgh GSP | SHET-RI-189 | Strichen-Fraserburgh to St Fergus 132kV OHL Reconductoring - Upgrade a section of the existing Strichen/Fraserburgh to St Fergus Switching Station 132kV SF1/SF2 OHL double circuit (approx. 6.2km) to have a minimum summer pre-fault rating of 231MVA. | 31/10/2027
|  | CS-08861 | FLEXION ENERGY UK STORAGE LTD | Fraserburgh GSP | SHET-RI-151 | Peterhead – St Fergus 132kV Line Works – Overhead line works to bring the 132kV circuit to ground, including any required modifications. Design and installation of one 132kV circuit breaker with three 132kV disconnectors and associated protection and control equipment for each of the two circuits. | 31/10/2027
Frodsham Solar Park | PRO-001952 | CS-08339 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 101468-202908 | Reconductor the Daines – Macclesfield 400kV with 2x780mm2 conductor | 30/12/2026
|  | CS-08336 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 30/12/2026
|  | CS-08337 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 400kV circuits and the Cellarhead – Macclesfield and Cellarhead – Daines 400kV circuits | 30/12/2026
|  | CS-08343 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 30/12/2026
|  | CS-08328 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 30/12/2026
|  | CS-08332 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor | 30/12/2026
|  | CS-08340 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm2 conductor | 30/12/2026
|  | CS-08338 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x780mm2 conductor or equivalent and uprating of the cable section of the circuit | 30/12/2026
|  | CS-08342 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 30/12/2026
|  | CS-08330 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with new 2750MVA unit. | 30/12/2026
|  | CS-08341 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 100425-200971 | Reconductor the Feckenham – Ironbridge 400kV circuit with 2x620mm2 conductor | 30/12/2026
|  | CS-08333 | PEEL NRE DEVELOPMENTS LIMITED | Frodsham 275kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor | 30/12/2026
Fron Goch | PRO-001563 | CS-04723 | NANT MITHIL ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 31/10/2026
|  | CS-04724 | NANT MITHIL ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | 1. Install and commission three Supergrid Transformer (SGT) bays at Pont Abraham 400kV substation. 2. Install and commission switchgear at Pont Abraham to include SGT HV and LV circuit breakers and associated bay assets. 3. Install and commission three 460MVA rated 400/132kV SGTs. 4. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. 5. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 31/10/2026
|  | CS-04725 | NANT MITHIL ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 31/10/2026
Gaerwen Wind Farm | PRO-001550 | CS-04483 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Gwyddelwern 400kV Substation | 101269-202512 | 1. Establish a new four bay 400kV double busbar substation1 adjacent to the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. Substation to comprise two feeder bays, a bus coupler bay and a skeletal bay for the User to connect their generator circuit 2. Connect the substation to the Main interconnected system via a turn in of the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. 3. Establish a CUSC Category 4 System to generator intertrip scheme to monitor the circuits between Pentir and Trawsfynydd and Trawsfynydd Gwyddelwern – Connahs Quay and Legacy 400kV substations | 01/06/2027
|  | CS-04484 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Gwyddelwern 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor. | 01/06/2027
|  | CS-05091 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Gwyddelwern 400kV Substation | 101267-202510 | Establish a CUSC Category 2 system to generator intertrip scheme to monitor the 400kV circuits between Pentir, Connahs Quay, Trawsfynydd, Gwyddelwern and Legacy. | 01/06/2027
|  | CS-05100 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Gwyddelwern 400kV Substation | 101006-202010 | 1. Uprating of the Bodelwyddan – Connahs Quay 1 and 2 400kV circuits | 01/06/2027
|  | CS-05101 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Gwyddelwern 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 01/06/2027
|  | CS-05102 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Gwyddelwern 400kV Substation | 101277-202523 | Installation of power electronics-based power flow control devices in the Pentir – Trawsfynydd 1 and 2 circuits 400kV circuits. | 01/06/2027
|  | CS-05103 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Gwyddelwern 400kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor triggered from R4 connection | 01/06/2027
|  | CS-05104 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Gwyddelwern 400kV Substation | 101284-202534 | Reconductor the existing 2x570mm2 conductor on the IronBridge- Legacy 2 and IronBridge Shrewsbury-Legacy 400 kV circuits with 2x570mm2 conductor at 90 deg. C to achieve a pre fault summer rating of 2490 MVA | 01/06/2027
|  | CS-05105 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Gwyddelwern 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 01/06/2027
Gallos | PRO-002734 | CS-09270 | Corio Generation Limited | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 06/12/2036
|  | CS-09274 | Corio Generation Limited | Alverdiscott 400kV Substation | 102692-205383 | 0 | 06/12/2036
|  | CS-09268 | Corio Generation Limited | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-09267 | Corio Generation Limited | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Hinkley (Shurton) – Taunton 1 & 2 400kV circuits (2x500mm2 Rubus at 90oC) with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 06/12/2036
|  | CS-09269 | Corio Generation Limited | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
|  | CS-09272 | Corio Generation Limited | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-09271 | Corio Generation Limited | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
|  | CS-09273 | Corio Generation Limited | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to triple Auriacuria 3 x 700mm2 at 90 degrees to achieve a summer pre-fault rating of 3000MVA | 06/12/2036
Gammidge PV & BESS Park | PRO-001649 | CS-07032 | CS UK HOLDINGS III LIMITED | Grendon 132kV Substation | 101103-202203 | Extension of the existing Grendon 132kV substation Main and Reserve Busbars to accommodate the User’s bay | 31/10/2024
Garbet Wind Farm | PRO-001813 | CS-07694 | ENERGYFARM UK GARBET LLP | Keith GSP | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 31/10/2026
Garn Fach Wind Farm | PRO-001157 | CS-04620 | EDF ENERGY RENEWABLES LIMITED | Garn Fach 132kV Substation | 101032-202058/ 101032-202059/ 101032-202069 | 1. Establish a new 400kV double busbar substation comprising 2 feeder bays, a bus coupler, a MSCDN bay and 4 SGT bays. 2. Establish a new 3.5kA continuous current rated 132kV double busbar substation comprising a bus coupler,4 SGT bays, an earthing transformer bay and 2 feeder bays. 3. Install a 225MVAr MSCDN at the 400kV substation. 4. Connect an earthing transformer to the 132kV substation 5. Install an earthing transformer at the 132kV substation. 6. Connect the 400kV substation to the 132kV substation via 4 240MVA rated SGT’s 7. Establish a system to generator operational intertripping scheme to perform as per the requirements of the TOF3 8. Connect the 400kV substation to the Legacy – Shrewsbury – Ironbridge and Legacy – Ironbridge circuits via a double tee arrangement. 9. Connect the new Cefn Coch – Lower Frankton 132kV double circuit to Lower Frankton 132kV substation | 01/05/2032
|  | CS-04621 | EDF ENERGY RENEWABLES LIMITED | Garn Fach 132kV Substation | 101032-202066 | Establish a new 132kV double circuit route between Lower Frankton and Cefn Coch | 01/05/2032
|  | CS-04622 | EDF ENERGY RENEWABLES LIMITED | Garn Fach 132kV Substation | 101032-202061 | 1.Establish a new 132kV substation comprising 4 feeder bays and space for User to connect their generator bay. 2. Connect the new Cefn Coch – Garn Fach 132kV double circuit to Garn Fach 132kV substation 3. Connect the new Garn Fach – Nant y Maen 132kV double circuit to Garn Fach 132kV substation | 01/05/2032
|  | CS-04623 | EDF ENERGY RENEWABLES LIMITED | Garn Fach 132kV Substation | 101032-202060 | 1. Establish a new 4 bay new 3.5kA continuous current rated 132kV double busbar substation comprising a bus coupler, 4 feeder bays, 2 SVC bays. 2. Installation of 2 SVC’s 3. Connect the Cefn Coch – Lower Frankton 132kV double circuit into Cefn Coch substation EdF (Nant Y Maen) ConsAg v1 Ref: A/NANTY/20/0503-1EN(0) Date: August 2020 4. Connect the new Garn Fach – Cefn Coch 132kV double circuit to Cefn Coch 132kV substation | 01/05/2032
|  | CS-04624 | EDF ENERGY RENEWABLES LIMITED | Garn Fach 132kV Substation | 101032-202067 | Establish a new 132kV double circuit route between Cefn Coch and Garn Fach | 01/05/2032
|  | CS-04625 | EDF ENERGY RENEWABLES LIMITED | Garn Fach 132kV Substation | 101032-202063 | 1. Establish a new 400kV single switch mesh substation 2. Reconnect the HV side of the existing Shrewsbury SGT to Mesh Corner 2 of the newly established mesh substation. 3. Install a circuit intertripping scheme | 01/05/2032
|  | CS-04626 | EDF ENERGY RENEWABLES LIMITED | Garn Fach 132kV Substation | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 01/05/2032
Garvary Wind Farm | PRO-001927 | CS-07156 | GARVARY WIND FARM LTD | Garvary 132kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 30/06/2028
|  | CS-07157 | GARVARY WIND FARM LTD | Garvary 132kV Substation | SHET-RI-133 Loch Buidhe SGT Upgrade | At Loch Buidhe substation remove the existing two 275/132kV 240MVA SGTs, replace with two new 275/132kV 480MVA SGTs and upgrade the 132kV switchboard | 30/06/2028
|  | CS-07155 | GARVARY WIND FARM LTD | Garvary 132kV Substation | Garvary Wind Farm Enabling Works | 1. The sole enabling works will include the construction of a new 4km single 132kV circuit 2. Beauly to Loch Buidhe 275kV OHL Reinforcement | 30/06/2028
Gateway Energy Centre Power Station | PRO-000045 | CS-05704 | GATEWAY ENERGY CENTRE LIMITED | Coryton South 400kV Substation | NGET-RI-21343-13 | New bus coupler to be installed at Raleigh Main 400kV substation and re-distribution of the ZT circuits such that Bradwell - Rayleigh circuit 1 is re-distributed to the Rayleigh main busbar 1. Involves moving the Rayleigh Main - Coryton South circuit southwards to allow room to extend Rayleigh Main. This work will be conducted at the same time as that associated with works at Rayleigh associated with the connection of a new Rayleigh - Bradwell 400kV double circuit. | 30/09/2025
|  | CS-05705 | GATEWAY ENERGY CENTRE LIMITED | Coryton South 400kV Substation | NGET-RI-21343-15 | Replace in situ existing OIBR bus section bay X120, bus coupler X130 and SGT1 and 4 bays X110, X410 respectively. | 30/09/2025
|  | CS-05706 | GATEWAY ENERGY CENTRE LIMITED | Coryton South 400kV Substation | NGET-RI-21343-23 | Installation of necessary equipment to provide provision for a generator intertripping scheme at Coryton South 400kV to manage local outage/fault combinations on the circuits connecting the Coryton South - Tilbury - Grain or X205 (at Coryton South) & Rayleigh - Coryton South or X605 (at Rayleigh). | 30/09/2025
|  | CS-05707 | GATEWAY ENERGY CENTRE LIMITED | Coryton South 400kV Substation | NGET-RI-21850 | Up-Rating of Rayleigh - Coryton South - Tilbury double circuit. | 30/09/2025
Gatroben Offshore Wind Farm | PRO-001675 | CS-05082 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 31/10/2031
|  | CS-05083 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 31/10/2031
|  | CS-05097 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 101504-202965 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-05106 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 101489-202941 | At Hawthorn Pit (New) 400kV Substation: Extend busbars to facilitate the OFTO bay and include the User Bay in the Eastern Link OTS | 31/10/2031
|  | CS-05107 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 100818-201654 | Establish a new 400kV circuit between Creyke Beck and Grimsby West 400kV substations | 31/10/2031
|  | CS-05108 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 100058-200133 | Tee in the Hartlepool - West Boldon circuit into Hawthorn Pit 275kV Substation (NOA WHTI) | 31/10/2031
|  | CS-05109 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 030317-030317 | Rebuild the existing Hawthorn Pit 400kV compound as a full double busbar substation. Uprate the existing Hawthorn Pit - Norton 275kV to a 400kV circuit. (NOA E2DC) | 31/10/2031
|  | CS-05110 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a post-fault winter rating of 3100MVA | 31/10/2031
|  | CS-05111 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 101553-203094 | Turn in the Cottam-Staythorpe 400KV circuit at High Marnham 400KV | 31/10/2031
|  | CS-05112 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-05113 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 100821-201659 | Uprate the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit to achieve a pre-fault summer rating of 2790MVA | 31/10/2031
|  | CS-05114 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 31/10/2031
|  | CS-05115 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 100459-201024 | Uprating of the Creyke Beck - Humber Refinery – Keadby and Creyke Beck - Keadby – Killingholme 4ZQ circuits to achieve a post-fault summer rating of 3420MVA | 31/10/2031
|  | CS-05116 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 03349-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 31/10/2031
|  | CS-05117 | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 31/10/2031
GF Upper Boat | PRO-003568 | CS-08526 | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 100424-200970 | Uprate the Bramley - Melksham 1 & 2 400kV circuits (81.6km, 2 x 400mm2 zebra conductor at 50oC on L2 towers with summer prefault rating of 931MVA) by reconductoring with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 31/05/2025
|  | CS-08527 | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 31/05/2025
|  | CS-08524 | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 102343-204505 | At Upperboat 275kV substation extend Mesh Corner 1 and install a CB/DCB. Works to include associated P&C. | 31/05/2025
|  | CS-08525 | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 102344-204506 | At Upperboat 275kV substation extend Mesh Corner 4 and install a CB/DCB. Works to include associate P&C. | 31/05/2025
GH DEVCO Gretna Green BESS | PRO-003096 | CS-09077 | Gresham House Devco Pipeline Limited | Gretna Green 132 kV Substation | NGET 101074 - 202154 | 2. New OHL reinforcement from Teviot Substation to Harker 400kV substation. (NGET 101074 – 202154) | 30/10/2032
|  | CS-09075 | Gresham House Devco Pipeline Limited | Gretna Green 132 kV Substation | NGET-101268-202511 | 0 | 30/10/2032
|  | CS-09072 | Gresham House Devco Pipeline Limited | Gretna Green 132 kV Substation | 132kV Disconnector | Installation of a 132kV disconnector at Gresham House Gretna BESS 400/132kV substation | 30/10/2032
|  | CS-09074 | Gresham House Devco Pipeline Limited | Gretna Green 132 kV Substation | SPT-RI-3022 | Gresham House Gretna 400/132kV substation - A new 400/132kV substation will be installed at the Gresham House Gretna Substation site. An extension of Gretna 400kV substation is required to accommodate a new feeder bay. At Gretna 400kV substation a new 400kV feeder bay and associated DBB switchgear (circuit breaker, line isolator and DBB disconnectors). From here a new 400kV UGC circuit will be laid to the Gresham House Gretna site. A new 400/132kV substation will be established with two 400/132kV 240MVA Super Grid Transformers installed. A new 132kV busbar will be established to accommodate the Gresham House Gretna BESS 400MW and GH DEVCO Gretna Green BESS 56MW | 30/10/2032
|  | CS-09076 | Gresham House Devco Pipeline Limited | Gretna Green 132 kV Substation | NGET -101268-202520 | 0 | 30/10/2032
|  | CS-09073 | Gresham House Devco Pipeline Limited | Gretna Green 132 kV Substation | SPT-RI-231 | 0 | 30/10/2032
GH DEVCO Kincardine BESS | PRO-003173 | CS-09472 | Gresham House Devco Pipeline Limited | Kincardine GSP | SPT-RI-3091 | Kincardine 275kV (Shared) GIS Switchgear - To facilitate the connection of new generation from BESS to Kincardine 275kV substation, it is proposed to install a new 275kV GIS switchgear and associated 275kV equipment at Kincardine 275kV GIS substation | 01/12/2028
Giants Burn Wind Farm | PRO-002232 | CS-09426 | STATKRAFT UK LTD | Dunoon GSP | SHET-RI-098 | Dunoon GL1-GL2 OHL Rebuild - Rebuild approximately 18km of double circuit overhead line between Dunoon substation and the SHET – SPT boundary. This project interfaces with Scottish Power Transmission (SPT), and any works required beyond the SHET-SPT boundary will be the responsibility of SPT. (SHET-RI-098) | 31/05/2030
|  | CS-09430 | STATKRAFT UK LTD | Dunoon GSP | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 31/05/2030
|  | CS-09425 | STATKRAFT UK LTD | Dunoon GSP | Ginats Burn Wind Farm H1 | Installation of two 132kV circuit breakers and associated disconnectors at the new Dunoon GSP to facilitate the connection of GL1 and GL2 circuits. Works shall also include the OHL diversion of GL1 and GL2 to new Dunoon GSP | 31/05/2030
|  | CS-09428 | STATKRAFT UK LTD | Dunoon GSP | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 31/05/2030
|  | CS-09427 | STATKRAFT UK LTD | Dunoon GSP | SPT-RI-2935 | CM Route Reinforcement- New generation at The Relevant Transmission Licensee’s New Dunoon 132kV substation necessitates an uprating of the 132kV shared circuit between New Dunoon and the tee into the Sloy-Windyhill circuit. The Relevant Transmission Licensee portion of the circuit runs between tower CM01 and mid span between CM13/14. The circuit presently uses 125mm2 ACSR Tiger conductor. It is proposed that SPT uprate the double circuit to Sycamore 280mm2 conductor (operated at 90℃) from CM1 to CM12. It is assumed SHETL will uprate over the boundary span between CM14 and CM13, terminating at tower CM12. (SPTRI-2935) | 31/05/2030
|  | CS-09429 | STATKRAFT UK LTD | Dunoon GSP | SPT-RI-2148 | WindyHill SGT Auto-close scheme - Installation of an auto-close scheme across the three 275/132kV supergrid transformers at Windyhill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. It is proposed to run SGT3 on open standby and for the loss/opening of SGT1 (CB1380) or SGT2 (CB1480) an instruction shall be issued to close the SGT3 circuit breaker (CB1080) in order to keep two SGTs in service at all times. The scope of works also makes inclusion for the replacement of the SCADA/HMI system in order to facilitate the installation of this auto-close scheme | 31/05/2030
|  | CS-09431 | STATKRAFT UK LTD | Dunoon GSP | SPT-RI-2784 | CL & CK Route Temperature Uprating - To alleviate overloads on the 132kV circuits on CL and CK Routes between Windyhill, Strathleven, Helensburgh and Sloy substations it is required to increase the operating temperature of the circuits from 50℃ to 65℃. This increase in operating temperature provides sufficient headroom to remove any intact overloads seen on the system. (SPT-RI-2784) | 31/05/2030
Gleann Eoghainn | PRO-001275 | CS-05711 | RENANTIS UK LIMITED | Edinbane 132/33kV Substation | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 31/10/2027
|  | CS-05712 | RENANTIS UK LIMITED | Edinbane 132/33kV Substation | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 31/10/2027
|  | CS-05713 | RENANTIS UK LIMITED | Edinbane 132/33kV Substation | Gleann Eoghainn item 1 | Replace the existing 33kV transformer circuit breaker 1TO located at Dunvegan 132/33kV GSP substation compound with the equivalent new equipment rated to a minimum of 1250A. This single 33kV circuit breaker will be owned and operated by the Relevant Transmission Licensee and represents the ownership boundary between the Relevant Transmission Licensee and the host Distribution Network Operator. | 31/10/2027
Glenchamber Wind Farm | PRO-000043 | CS-05730 | GLENCHAMBER WIND ENERGY LIMITED | Glenluce GSP | SPT-RI-147 | A new 275kV double circuit overhead line will be constructed between Kilmarnock South and Coylton 275kV substation having a minimum summer pre-fault rating 1500MVA per circuit. In addition, the existing 132V circuit between Kilmarnock South and the Coylton T will be removed to facilitate a line routing for the third Kilmarnock South to Coylton 275kV circuit. Moreover, the Coylton 275/132kV SGT1 and SGT2 120MVA transformers will be replaced with 240MVA units to provide sufficient export capacity for the contracted generation in the area. | 30/10/2022
Glendye Wind Farm | PRO-001389 | CS-07167 | GLENDYE WIND FARM LIMITED | Glendye Wind Farm Substation | Glendye Wind Farm Enabling Works | 1. Installation of a 132kV line disconnector at the User’s substation 2. Construction of approx. 20.75km of single 132kV circuit, comprising 0.75km of underground cable and 20km of overhead line from the User’s site to Fetteresso substation 3. Extension of 132kV busbar at Fetteresso substation and installation of a new 132kV busbar feeder bay 4. Installation of a new 132kV feeder protection and control scheme | 31/10/2028
|  | CS-07168 | GLENDYE WIND FARM LIMITED | Glendye Wind Farm Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2028
|  | CS-07169 | GLENDYE WIND FARM LIMITED | Glendye Wind Farm Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2028
Glen Etive Hydro | PRO-000630 | CS-05714 | Scottish Hydro Electric Power Distribution Plc | Kinlochleven GSP | SHET-RI-045b | 1. Fort Augustus–Fort William 132kV OHL Upgrade Phase 2 - Reconductor one side of the 132kV double circuit OHL between Fort Augustus and Fort William (FFE). The 132kV circuit OHL (FFE) is to be reconductored with a higher capacity conductor. This will have a minimum summer pre-fault rating of 208MVA per circuit. Replace the existing 132kV cables on FFE & FFW into Fort Augustus with new 132kV cables rated suitably for the increased capacity of the new OHL conductor. Reinstate the permanent connection of the 132kV Kinlochleven circuit (FV1) to FFE following the completion of FFE reconductoring work. (SHET-RI-045b) | 30/09/2021
Glenmuckloch Pumped Storage | PRO-000299 | CS-07396 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/06/2027
|  | CS-07397 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 30/06/2027
|  | CS-05731 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 30/06/2027
|  | CS-05732 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/06/2027
|  | CS-05733 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill Substation, heading east, to 132kV Black Hill Substation. Black Hill Substation will include three new 132kV circuit breaker (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 30/06/2027
|  | CS-05734 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-022 | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 30/06/2027
|  | CS-05735 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 30/06/2027
|  | CS-05736 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 30/06/2027
|  | CS-05737 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 30/06/2027
|  | CS-05738 | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/06/2027
Glenmuckloch Wind Farm | PRO-000300 | CS-05744 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 30/10/2026
|  | CS-05745 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 30/10/2026
|  | CS-05746 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 30/10/2026
|  | CS-05747 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/10/2026
|  | CS-05748 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/10/2026
|  | CS-05739 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 30/10/2026
|  | CS-05740 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/10/2026
|  | CS-05741 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill Substation, heading east, to 132kV Black Hill Substation. Black Hill Substation will include three new 132kV circuit breaker (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 30/10/2026
|  | CS-05742 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-022 | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 30/10/2026
|  | CS-05743 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 30/10/2026
|  | CS-05403 | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/10/2026
Glenshimmeroch Windfarm | PRO-000440 | CS-03720 | ENERGYFARM UK GLENSHIMMEROCH LLP | Quantans Hill 132kV | Glenshimmeroch H1 | Installation of a 132kV line isolator connecting onto a 132kV busbar at Glenshimmeroch collector substation. | 26/08/2027
|  | CS-03721 | ENERGYFARM UK GLENSHIMMEROCH LLP | Quantans Hill 132kV | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 26/08/2027
|  | CS-03722 | ENERGYFARM UK GLENSHIMMEROCH LLP | Quantans Hill 132kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 26/08/2027
|  | CS-03723 | ENERGYFARM UK GLENSHIMMEROCH LLP | Quantans Hill 132kV | SPT-RI-274 | Glenshimmeroch Collector Substation - On the New Cumnock / Blackcraig 132kV circuit, installation of a 132kV circuit breaker and associated disconnectors at Glenshimmeroch Collector Substation in South West Scotland. | 26/08/2027
|  | CS-03724 | ENERGYFARM UK GLENSHIMMEROCH LLP | Quantans Hill 132kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 26/08/2027
|  | CS-03725 | ENERGYFARM UK GLENSHIMMEROCH LLP | Quantans Hill 132kV | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 26/08/2027
|  | CS-03726 | ENERGYFARM UK GLENSHIMMEROCH LLP | Quantans Hill 132kV | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 26/08/2027
|  | CS-03727 | ENERGYFARM UK GLENSHIMMEROCH LLP | Quantans Hill 132kV | SPT-RI-296 | Glenshimmeroch collector substation 132kV overhead line uprating - Due to an increase in the generation contracted in the area, it is proposed to uprate a section of the overhead line between the proposed Glenshimmeroch collector substation to the cable end on the New Cumnock 132kV circuit. This is approximately 11km. This will be achieved by replacing the existing UPAS conductor with LARK conductor on the existing wood pole system. | 26/08/2027
Glenside Farm BESS | PRO-004368 | CS-09475 | GPC 1211 Ltd | Denny GSP | SPT-RI-2083 | Kincardine North – Wishaw 400kV reinforcement (DWUP)- Establish 400kV infrastructure through the centre of the network following the East Coast 400kV onshore incremental (ECUP) reinforcement, but in advance of the completion of existing Denny to Wishaw 400kV reinforcement (DWNO). The scope of this TORI will be aligned with the ‘DWUP’ option submitted to the 2021/22 Network Options Assessment (NOA) process. It is proposed to reconfigure and update existing 275kV single circuit between the Kincardine and Wishaw to 400kV operation to establish a new Kincardine North – Wishaw 400kV circuit. | 31/05/2028
Glentaggart 42MW BESS | PRO-001595 | CS-09803 | GLENTAGGART WIND LIMITED | Glentaggart WF 33kV Substation | SPT-RI-3547 | Redshaw 132kV to Glentaggart / Hare Craig – It is proposed to connect Glentaggart 42MW BESS and Hare Craig WF into Redshaw 132kV GIS substation (‘A’ board) via a shared solution. The shared assets proposed for this solution are covered under this TORI, which entail the following works: • Installation of a new 132kV double busbar bay and associated circuit breaker at Redshaw 132kV GIS (‘A’ board). • Installation of a new 132/33kV 120MVA GT unit at Redshaw 132kV GIS (‘A’ board). • Installation of a 33kV circuit breaker associated with the 3 panel switchboard. (SPT-RI-3547) | 31/10/2027
|  | CS-04297 | GLENTAGGART WIND LIMITED | Glentaggart WF 33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 31/10/2027
|  | CS-04298 | GLENTAGGART WIND LIMITED | Glentaggart WF 33kV Substation | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 31/10/2027
Glentarken Wind Farm | PRO-003627 | CS-09662 | SSE RENEWABLES SERVICES (UK) LIMITED | Killin GSP | SHET-RI-034 | Inverarnan 132kV QBs - Install 2 x 132kV 240MVA QBs at Inverarnan substation in series with the two 275/132kV SGTs connected to the Dalmally – Windyhill 275kV line. (SHET-RI-034) | 30/11/2031
|  | CS-09663 | SSE RENEWABLES SERVICES (UK) LIMITED | Killin GSP | SHET-RI-243 - Killin - Inverarnan 132kV Double Circuit Rebuild | Rebuild the Killin - Inverarnan 132kV double circuit tower line, including replacement of the 132kV underground cable sections, with higher rated 132kV assets. | 30/11/2031
Glen Ullinish Extension | PRO-001346 | CS-06240 | GLEN ULLINISH WF 2 LTD | Glen Ullinish Extension 132/33kV Substation | Glen Ullinish Extension - Enabling Works | 1. Construction of approximately 5km of single circuit 132kV overhead line from the connection site to a new bay on the Edinbane 132kV busbars, via the required 132kV switchgear. | 01/04/2027
|  | CS-06241 | GLEN ULLINISH WF 2 LTD | Glen Ullinish Extension 132/33kV Substation | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 01/04/2027
|  | CS-06242 | GLEN ULLINISH WF 2 LTD | Glen Ullinish Extension 132/33kV Substation | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 01/04/2027
|  | CS-06243 | GLEN ULLINISH WF 2 LTD | Glen Ullinish Extension 132/33kV Substation | SHET-RI-135 | 4. Broadford – Edinbane Reinforcement (SHET-RI-135) | 01/04/2027
Glen Ullinish Wind Farm | PRO-000298 | CS-05717 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | SHET-RI-125 | Broadford-Dunvegan Reinforcement: Construct a new 132kV double circuit OHL from Broadford to Dunvegan | 31/10/2026
|  | CS-05718 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm H1 Works Item 4 | Modify the tower near the new 132/33kV windfarm substation and erect a new terminal tower and down droppers to the new substation compound. | 31/10/2026
|  | CS-05719 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm H1 Works Item 3 | Install 2 x 132kV line isolating switches (103 and 203) along with associated busbar extensions and support structures within the substation compound. Isolators to be located on either side of the single teed 132kV infeed to the substation. | 31/10/2026
|  | CS-05720 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm H1 Works Item 2 | Install 1 x 132kV transformer circuit breaker (115) along with associated busbar extensions and support structures. | 31/10/2026
|  | CS-05721 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm H1 Works Item 1 | Modify the existing protection and telecommunication equipment's at Fort Augustus and the new 132kV substation near Dunvegan. | 31/10/2026
|  | CS-05722 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 31/10/2026
|  | CS-05723 | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 31/10/2026
Golticlay Wind Farm | PRO-000370 | CS-06657 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 30/04/2025
|  | CS-05752 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-037 | Fyrish 275/132kV Substation – Establish a new 275kV/132kV Fyrish substation close to the existing Alness 132kV OHL Teed location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. Two new 132kV underground cables will be installed to link the new 275kV/132kV Fyrish substation with the existing Alness GSP. (SHET-RI-037) | 30/04/2025
|  | CS-05753 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/04/2025
|  | CS-05754 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 30/04/2025
|  | CS-05755 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 30/04/2025
|  | CS-05756 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-032b | Spittal – Mybster 132kV Reinforcement — This consists of a new higher capacity 132kV OHL and substation works between Spittal and Mybster substation. (SHET-RI-032b) | 30/04/2025
|  | CS-05757 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 30/04/2025
|  | CS-05758 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 30/04/2025
|  | CS-05759 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 30/04/2025
|  | CS-05760 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Mybster 132/33kV Substation | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 30/04/2025
Grain North Power Station | PRO-001524 | CS-07433 | GRAIN NORTH POWER LIMITED | Grain North 132kV Substation | 101251-202492 | 1. Installation of a new 3 bay 132kV single busbar substation 2. Splitting of the existing 4.2km 132kV cable between Grain SGT7 and Grain LNG 132kV, approximately 700m from Grain LNG 132kV 3. Installation of 2 x 132kV cable joints and 2 x 132kV cable spans running to the new Grain North 132kV substation 4. Installation of 2 x 132kV cable sealing ends 5. Installation of 2 x 132kV disconnectors connecting to 2 x 132kV bays at the new Grain North 132kV substation 6. Installation of a new 132kV disconnector for the User’s Connection | 30/06/2023
Grain South Power Station | PRO-000449 | CS-04360 | Grain South Power Limited | Grain South 132kV Substation | 100804-201624 | 1. Installation of a new 3 bay 132kV single busbar substation. 2. Splitting of the existing 4.2km 132kV cable between Grain SGT5 and Grain LNG 132kV, 3. Installation of 2 x 132kV cable joints and 2 x 132kV cable spans running to the new Grain South 132kV substation. approximately 700m from Grain LNG 132kV. 4. Installation of 2 x 132kV cable sealing ends. 5. Installation of 2 x 132kV disconnectors connecting to 2 x 132kV bays at the new Grain South 132kV substation. 6. Installation of a new 132kV disconnector for the User’s Connection. | 30/10/2023
Greenburn Mixed Technology | PRO-001006 | CS-05767 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 31/10/2027
|  | CS-05768 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | Greenburn Mixed Technology Item 1 | At New Cumnock substation on Board C, install a new 132kV switch bay and associated equipment and apparatus. | 31/10/2027
|  | CS-05769 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | Greenburn Mixed Technology Item 3 | Installation of a 132kV cable system from New Cumnock 132kV substation to an appropriate location where the 132kV wood pole overhead line will be constructed. | 31/10/2027
|  | CS-05770 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 31/10/2027
|  | CS-05771 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | Greenburn Mixed Technology Item 2 | Installation of approximately 8km of 132kV wood pole overhead line between New Cumnock and Greenburn Mixed Technology 132kV Substation. | 31/10/2027
|  | CS-05772 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | Greenburn Mixed Technology Item 4 | At the Greenburn Mixed Technology Substation, install one 132kV line isolator. | 31/10/2027
|  | CS-05773 | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 31/10/2027
Greenland Wind Farm | PRO-002293 | CS-08203 | Greenland Wind Farm Limited | Greenland 132kV/33kV Substation | SHET-RI-158 | Beauly to Loch Buidhe 275kV OHL Reinforcement - reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. | 31/10/2034
|  | CS-08204 | Greenland Wind Farm Limited | Greenland 132kV/33kV Substation | SPT-RI-028 | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | 31/10/2034
|  | CS-08199 | Greenland Wind Farm Limited | Greenland 132kV/33kV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 31/10/2034
|  | CS-08197 | Greenland Wind Farm Limited | Greenland 132kV/33kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2034
|  | CS-08196 | Greenland Wind Farm Limited | Greenland 132kV/33kV Substation | Greenland Sole | 1. Install a new 132kV double busbar feeder bay, consisting of 2x 132kV busbar disconnectors, 1x 132kV circuit breaker and 1x 132kV circuit disconnector, located at the new 132kV double busbar at Carradale substation, installed as part of TORI SHET-RI-158. 2. Establishment of a new 132kV single circuit connection between Carradale 132kV substation and the new Greenland Wind Farm 132kV substation. This will comprise 16.5km of 132kV wood pole overhead line and 0.5km of 132kV underground cable. This circuit will terminate onto a new 132kV line disconnector switch located at the Greenland Wind Farm 132kV substation. | 31/10/2034
|  | CS-08200 | Greenland Wind Farm Limited | Greenland 132kV/33kV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2034
|  | CS-08198 | Greenland Wind Farm Limited | Greenland 132kV/33kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2034
|  | CS-08201 | Greenland Wind Farm Limited | Greenland 132kV/33kV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 31/10/2034
|  | CS-08202 | Greenland Wind Farm Limited | Greenland 132kV/33kV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 31/10/2034
Green Volt Offshore Windfarm | PRO-001469 | CS-04283 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2029
|  | CS-04284 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-025d | North East Reinforcement | 31/10/2029
|  | CS-04285 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2029
|  | CS-04286 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2029
|  | CS-04287 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2029
|  | CS-04288 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2029
|  | CS-04289 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2029
|  | CS-04290 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2029
|  | CS-04291 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2029
|  | CS-04292 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2029
|  | CS-04293 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2029
|  | CS-04294 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2029
|  | CS-04295 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2029
|  | CS-04296 | FLOTATION ENERGY PLC | New Deer 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2029
Grendon Solar & BESS | PRO-001568 | CS-05118 | ISLAND GREEN POWER UK LIMITED | Grendon 400kV Substation | 100952-201899 | Uprate all three downdroppers on the East Claydon - Leighton Buzzard - Sundon circuit to provide a pre-fault summer rating of 2400MVA | 01/07/2029
|  | CS-05120 | ISLAND GREEN POWER UK LIMITED | Grendon 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 01/07/2029
|  | CS-05121 | ISLAND GREEN POWER UK LIMITED | Grendon 400kV Substation | 030652-030652 | Reconductor and turn in Elstree – Sundon circuit 2 A608 into Elstree. Modify the existing circuit 2 (A608) that run from Sundon 400kV to Elstree 275kV by turning it in at Elstree 400kV. This will create two separate circuits: 1) From Sundon to Elstree 400kV circuit. To this will be added a new series reactor 2) Elstree 400kV to Elstree 275kV substation via existing interbus transformer (F608). No change to this element except connecting into new 400kV bay instead of to A608. | 01/07/2029
|  | CS-04720 | ISLAND GREEN POWER UK LIMITED | Grendon 400kV Substation | 101259-202500 | Extension of the existing Grendon 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 01/07/2029
Gresham House Branxton BESS | PRO-002208 | CS-08137 | BRAXBESS LTD | Branxton 400kV Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 30/04/2028
|  | CS-08141 | BRAXBESS LTD | Branxton 400kV Substation | SPT-RI-204 Wishaw - Smeaton - Torness - Eccles Overload Protection Scheme | An overload protection scheme installed within Wishaw - Smeaton - Torness - Eccles 275kV and 400kV network in order to protect the system in compliant Category 2 Intertripping Scheme as defined by the Grid Code. The Interrtripping Scheme will disconnect the generation within the area following system outage conditions being met. | 30/04/2028
|  | CS-08138 | BRAXBESS LTD | Branxton 400kV Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 30/04/2028
|  | CS-08139 | BRAXBESS LTD | Branxton 400kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 30/04/2028
|  | CS-08140 | BRAXBESS LTD | Branxton 400kV Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 30/04/2028
Gresham House Cockenzie BESS | PRO-002209 | CS-07746 | COCKENZIE STORAGE LIMITED | Cockenzie GSP | Gresham House Cockenzie BESS - Disconnector/Circuit Breaker | Installation of 400kV disconnector/circuit breaker | 31/07/2026
|  | CS-07745 | COCKENZIE STORAGE LIMITED | Cockenzie GSP | Gresham House Cockenzie BESS - Tee off | Works to tee off the 400kV OHL tower ZA001A | 31/07/2026
|  | CS-07744 | COCKENZIE STORAGE LIMITED | Cockenzie GSP | SPT-RI-1742 Cockenzie LMS (Cat 2) | 4. Cockenzie Load Management Scheme (Cat 2) – An overload protection scheme is proposed to be installed within the Cockenzie – Smeaton – Kaimes – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following defined system outage conditions. (SPT-RI-1742) | 31/07/2026
Gresham House Connagill BESS | PRO-003434 | CS-09611 | Gresham House Devco Pipeline Limited | Connagill 275kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/10/2030
|  | CS-09616 | Gresham House Devco Pipeline Limited | Connagill 275kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2030
|  | CS-09615 | Gresham House Devco Pipeline Limited | Connagill 275kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2030
|  | CS-09613 | Gresham House Devco Pipeline Limited | Connagill 275kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 31/10/2030
|  | CS-09610 | Gresham House Devco Pipeline Limited | Connagill 275kV Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90 degrees Celsius to increase the continuous current rating of the circuit | 31/10/2030
|  | CS-09614 | Gresham House Devco Pipeline Limited | Connagill 275kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2030
|  | CS-09617 | Gresham House Devco Pipeline Limited | Connagill 275kV Substation | SHET-RI-238 | 0 | 31/10/2030
|  | CS-09612 | Gresham House Devco Pipeline Limited | Connagill 275kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 31/10/2030
Gresham House Dalmarnock BESS | PRO-002809 | CS-08550 | Gresham House Devco Pipeline Limited | Dalmarnock GSP | Suspension Tower - Gresham House Dalmarnock BESS | Installation of 2 x suspension towers | 30/04/2030
|  | CS-08551 | Gresham House Devco Pipeline Limited | Dalmarnock GSP | Terminal Tower - Gresham House Dalmarnock BESS | Installation of 1 x terminal tower | 30/04/2030
|  | CS-08552 | Gresham House Devco Pipeline Limited | Dalmarnock GSP | SPT-RI-2957 | Dalmarnock SGT1 & Charlotte Street 1 DCBs – To comply with SQSS circuit complexity as per Appendix B and accommodate a new generation and demand connection within the Dalmarnock area of the network, there is a requirement to replace the H13A disconnector at Dalmarnock 275/132kV substation with a DCB. Additionally, there is also a requirement to replace the H13B disconnector at Dalmarnock 275/132kV substation with a DCB | 30/04/2030
|  | CS-08553 | Gresham House Devco Pipeline Limited | Dalmarnock GSP | 275kV Line Disconnector - Gresham House Dalmarnock BESS | Installation of 275kV Line Disconnector | 30/04/2030
Gresham House Gretna BESS | PRO-002367 | CS-08211 | ENERGYHUBDEVELOPMENTS LIMITED | Gretna 400kV Substation | SPT-RI-231 | 0 | 31/10/2031
Gresham House Mossmoran BESS | PRO-002395 | CS-08554 | Gresham House Asset Management Limited | Mossmoran 275kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 30/10/2030
Greta III | PRO-001803 | CS-06894 | GRETA III LIMITED | Drakelow 400kV Substation | 101615-203248 | Extension of the existing Drakelow 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 30/10/2029
|  | CS-06895 | GRETA III LIMITED | Drakelow 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm2 conductor on the CellarheadDaines 1 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2800 MVA | 30/10/2029
|  | CS-06896 | GRETA III LIMITED | Drakelow 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2029
|  | CS-06897 | GRETA III LIMITED | Drakelow 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2029
|  | CS-06898 | GRETA III LIMITED | Drakelow 400kV Substation | 101329-202649 | Hotwire Enderby – Ratcliffe 400kV circuits 1 and 2 to 65 deg. C to achieve a pre-fault summer rating of 2500MVA. | 30/10/2029
|  | CS-06899 | GRETA III LIMITED | Drakelow 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2029
|  | CS-06900 | GRETA III LIMITED | Drakelow 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2029
|  | CS-06901 | GRETA III LIMITED | Drakelow 400kV Substation | 101616-203249 | Hotwire Drakelow – Hams Hall 400kV circuit 1 to 90 deg. C to achieve a pre-fault summer rating of 1680MVA. | 30/10/2029
|  | CS-06902 | GRETA III LIMITED | Drakelow 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 1820 MVA. | 30/10/2029
Gridlink Interconnector | PRO-000287 | CS-05775 | GRIDLINK INTERCONNECTOR LIMITED | Kingsnorth 400kV Substation | 33748 | Kinsnorth Works, including: - Provide the customer with a spare bay at Kingsnorth 400kV substation (spare bay 3). - Kingsnorth circuit breaker foundation (Xl 05, Xli 0, X140, X205, X21 0 X705 X805 and X1090) updating works - Installation of a new coupler breaker with associated bay works between main busbar 3 and circuit breaker X220. | 31/03/2029
GT R4 Wind Farm | PRO-000563 | CS-06361 | GT R4 LIMITED | Weston Marsh 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 30/11/2030
|  | CS-06362 | GT R4 LIMITED | Weston Marsh 400kV Substation | 100929-201859 | Extend Wylfa 400kV substation in order to facilitate the connection of the GIGL offshore windfarm | 30/11/2030
|  | CS-06363 | GT R4 LIMITED | Weston Marsh 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 30/11/2030
|  | CS-06364 | GT R4 LIMITED | Weston Marsh 400kV Substation | 100974-201953 | Construct a second double circuit between Pentir 400kV substation and the Wylfa 400kV substation (circuits No. 3 & 4) | 30/11/2030
Gwynt Alwen WF | PRO-001545 | CS-05125 | WIND 2 LIMITED | Gwyddelwern 400kV Substation | 101006-202010 | 1. Uprating of the Bodelwyddan – Connahs Quay 1 and 2 400kV circuits | 30/04/2027
|  | CS-05127 | WIND 2 LIMITED | Gwyddelwern 400kV Substation | 101267-202510 | Establish a Category 2 system to generator intertrip scheme to monitor the 400kV circuits between Pentir, Connahs Quay, Trawsfynydd, Gwyddelwern and Legacy | 30/04/2027
|  | CS-05130 | WIND 2 LIMITED | Gwyddelwern 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/04/2027
|  | CS-05131 | WIND 2 LIMITED | Gwyddelwern 400kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor triggered from R4 connection | 30/04/2027
|  | CS-05132 | WIND 2 LIMITED | Gwyddelwern 400kV Substation | 101277-202523 | Installation of power electronics-based power flow control devices in the Pentir – Trawsfynydd 1 and 2 circuits 400kV circuits. | 30/04/2027
|  | CS-05133 | WIND 2 LIMITED | Gwyddelwern 400kV Substation | 101284-202534 | Reconductor the existing 2x570mm2 conductor on the IronBridge- Legacy 2 and IronBridge Shrewsbury-Legacy 400 kV circuits with 2x570mm2 conductor at 90 deg. C to achieve a pre fault summer rating of 2490 MVA | 30/04/2027
|  | CS-05134 | WIND 2 LIMITED | Gwyddelwern 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 30/04/2027
|  | CS-04728 | WIND 2 LIMITED | Gwyddelwern 400kV Substation | 101212-202434 | 1. Establish a new four bay 400kV double busbar substation1 adjacent to the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. Substation to comprise two feeder bays, a bus coupler bay and a skeletal bay for the User to connect their generator circuit 2. Connect the substation to the Main interconnected system via a turn in of the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. | 30/04/2027
|  | CS-04729 | WIND 2 LIMITED | Gwyddelwern 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor. | 30/04/2027
Gwynt Glas Offshore Wind Farm 2 | PRO-002480 | CS-08286 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
|  | CS-08282 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 06/12/2036
|  | CS-08288 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 06/12/2036
|  | CS-08283 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-08287 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-08289 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 102225-204458 | Infrastructure works for the generation connection of Gwynt Glas offshore wind farm 2. | 06/12/2036
|  | CS-08285 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 06/12/2036
|  | CS-08284 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
Hagshaw Hill Phase 1 | PRO-000490 | CS-05776 | HAGSHAW HILL REPOWERING LTD | Coalburn 132/33kV Substation | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 30/05/2024
|  | CS-05777 | HAGSHAW HILL REPOWERING LTD | Coalburn 132/33kV Substation | SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 30/05/2024
|  | CS-05778 | HAGSHAW HILL REPOWERING LTD | Coalburn 132/33kV Substation | SPT-RI-238 - Cumberhead WF 132kV Collector substation | The collector substation will require the installation of a 132kV busbar section with two line disconnectors and short sections of underground cable (~0.2km each) to connect into the existing Coalburn to Galawhistle 132kV underground cable. From the 132kV busbar section a 132kV circuit breaker, with associated disconnectors, will be installed and connected to a 132/33kV 120MVA transformer with a shared 33kV busbar section. The works to establish this collector substation will include the construction of the substation platform as well as a control building to house SPT’s protection and control equipment. | 30/05/2024
Hagshaw Hill Phase 2 | PRO-000514 | CS-05779 | HAGSHAW HILL REPOWERING LTD | Coalburn 132/33kV Substation | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 30/05/2024
|  | CS-05780 | HAGSHAW HILL REPOWERING LTD | Coalburn 132/33kV Substation | SPT-RI-251 | Coalburn to Douglas West 132kV Cable Reinforcement | 30/05/2024
|  | CS-05781 | HAGSHAW HILL REPOWERING LTD | Coalburn 132/33kV Substation | SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 30/05/2024
|  | CS-05782 | HAGSHAW HILL REPOWERING LTD | Coalburn 132/33kV Substation | SPT-RI-240 | Douglas West Wind Farm 132kV Substation | 30/05/2024
|  | CS-06522 | HAGSHAW HILL REPOWERING LTD | Coalburn 132/33kV Substation | SPT-RI-300 | Douglas North Collector Grid Transformer - Establish a 132/33kV 120MVA transformer at Douglas North Collector substation in place of the 90MVA and 60MVA units | 30/05/2024
Hagshaw Wind Farm Repowering 2 | PRO-002306 | CS-07964 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | 132kV Circuit (OHL/Cable) - HPhase 3 | Installation of a new 132kV circuit between Redshaw 132kV and Hagshaw Repowering Ph3 132kV substation comprising of both 132kV cable and OHL. The indicative length of the circuit is 10km. | 26/04/2029
|  | CS-07961 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 26/04/2029
|  | CS-07962 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | SPT-RI-2139 | Redshaw 400/132kV SGT2 - a new 360MVA 400/132kV supergrid transformer and associated 400kV and 132kV circuit breakers will be installed. This will increase the thermal capacity of Redshaw 132kV substation. | 26/04/2029
|  | CS-07963 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | AIS Feeder Bay - HPhase 3 | Installation of a new 132kV AIS feeder bay at Redshaw 132kV substation with associated main and reserve busbar disconnectors and line disconnector. | 26/04/2029
|  | CS-07965 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | 132kV Line Disconnector | Installation of a 132kV line disconnector at Hagshaw Repowering Ph3 132kV substation. | 26/04/2029
|  | CS-07960 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 26/04/2029
Hall Ings Solar Farm (DNO) | PRO-002643 | CS-08447 | NORTHERN POWERGRID (YORKSHIRE) PLC | Creyke Beck GSP | 102675-205361 | Construct a new 400kV double busbar substation including all necessary works required to connect it to the Main Interconnected Transmission System. | 30/10/2034
Hams Hall Green Energy Centre | PRO-001765 | CS-05349 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 101355-202675 | Extension of the existing Hams Hall 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 30/10/2028
|  | CS-05350 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2028
|  | CS-05351 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2028
|  | CS-05352 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 101329-202649 | Hotwire Enderby – Ratcliffe 400kV circuits 1 and 2 to 65 deg. C to achieve a pre-fault summer rating of 2260MVA. | 30/10/2028
|  | CS-05353 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2028
|  | CS-05354 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2028
|  | CS-05355 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2028
|  | CS-05356 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 1820 MVA. | 30/10/2028
|  | CS-05357 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2028
|  | CS-05358 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor triggered by R4 connection | 30/10/2028
|  | CS-05359 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 101284-202534 | Reconductor the existing 2x570mm2 conductor on the IronBridge- Legacy 2 and IronBridge Shrewsbury-Legacy 400 kV circuits with 2x570mm2 conductor at 90 deg. C to achieve a pre fault summer rating of 2490 MVA | 30/10/2028
|  | CS-05360 | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/10/2028
Hare Craig Wind Farm | PRO-000940 | CS-04523 | ENERGYFARM UK HARE CRAIG LLP | Hare Craig 33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 31/10/2027
|  | CS-04524 | ENERGYFARM UK HARE CRAIG LLP | Hare Craig 33kV Substation | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 31/10/2027
Hare Hill Repowering | PRO-003963 | CS-09152 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 31/10/2029
|  | CS-09155 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | 132kV OHL - Hare Hill | Installation of a 132kV OHL circuit out to the User’s WF substation. OHL circuit should be capable of 127MVA | 31/10/2029
|  | CS-09153 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | 132kV Line Disconnector - Hare Hill | At Hare Hill Repowering substation install one 132kV line disconnector | 31/10/2029
|  | CS-09151 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 31/10/2029
|  | CS-09150 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 31/10/2029
|  | CS-09149 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 31/10/2029
|  | CS-09154 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation | 132kV AIS Switch Bay - Hare Hill | Installation of a 132kV AIS bay at Glenmuckloch 132kV substation. | 31/10/2029
Hareshaw Rig Wind Farm | PRO-000543 | CS-05609 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-191 | The thermal capacity of the 132kV circuit between Gretna 132kV substation and Ewe Hill Wind Farm 132kV Collector Substation (works detailed in SPT-RI-017), will be increased by re-conductoring the 132kV overhead line utilising “Lark” High Temperature Low Sag (HTLS) conductor (~16km), and installing an additional 800mm2 Al XLPE 132kV underground cable in parallel with the existing cable(~0.3km), to give a minimum summer continuous rating of 224MVA. This is to accommodate additional generation connecting at the Ewe Hill Wind Farm 132kV Collector Substation. | 30/11/2026
|  | CS-05610 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 30/11/2026
|  | CS-05611 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 30/11/2026
|  | CS-06329 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-294 | Ewe Hill to Hopsrig collector substations 132kV circuit | 30/11/2026
|  | CS-06332 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | NGET-RI-32105 | Reinforce the Junction V to Harker 132kV circuit (from tower AL068 to Harker 132kV substation), to provide a minimum summer pre-fault continuous rating of 202MVA. (NGET-RI-32105 | 30/11/2026
|  | CS-06333 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 30/11/2026
|  | CS-06334 | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation | Hareshaw Rig H1 Works | At Hopsrig Collector Substation, install one 132kV line isolator and tee connect onto the Hopsrig – Ewe Hill 132kV circuit. | 30/11/2026
Harker Green Energy Centre | PRO-001709 | CS-05123 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101284-202534 | Reconductor the existing 2x570mm2 conductor on the IronBridge- Legacy 2 and IronBridge Shrewsbury-Legacy 400 kV circuits with 2x570mm2 conductor at 90 deg. C to achieve a pre fault summer rating of 2490 MVA | 30/10/2028
|  | CS-05126 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 30/10/2028
|  | CS-05128 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101348-202668 | 1x225MVAR MSC at Carrington 400kV substation | 30/10/2028
|  | CS-05129 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/10/2028
|  | CS-05136 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 008645-ON0066 | The offline build and commissioning of a new Harker 132kV GIS substation. The decommissioning and removal of the existing Harker 132kV AIS substation. Develop and commission a new Harker 132kV Auto Close Scheme and a new Harker 132kV Overload Protection Scheme at the Harker substation. | 30/10/2028
|  | CS-05137 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101347-202667 | 2x225MVAR MSC at Penwortham 400kV substation | 30/10/2028
|  | CS-05138 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x760mm2 conductor or equivalent and uprating of the cable section of the circuit | 30/10/2028
|  | CS-05139 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2028
|  | CS-05140 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor triggered by R4 connection | 30/10/2028
|  | CS-05141 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2028
|  | CS-05142 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 30/10/2028
|  | CS-04739 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101268-202511 | 1. The offline build and commissioning of a new Harker 400kV GIS substation. 2. The decommissioning and removal of the existing Harker 400kV substation | 30/10/2028
|  | CS-04740 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 101351-202671 | Extend the Main and Reserve Busbar 3 to make provision for connection of generator bay (User Works). | 30/10/2028
|  | CS-04741 | INNOVA RENEWABLES LIMITED | Harker 400kV Substation | 100118-200309 | The replacement of the existing four 275/132kV 120MVA SGTs with four 400/132 240MVA SGTs at Harker substation. | 30/10/2028
Harlaston | PRO-003814 | CS-08917 | SSE DE SOLAR HOLDCO LIMITED | Harlaston 400kV Substation | 101907-203905 | Reconductor the Drakelow – Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault summer rating of 2490 MVA | 31/10/2033
|  | CS-08916 | SSE DE SOLAR HOLDCO LIMITED | Harlaston 400kV Substation | 102484-205070 | 1. Construct a new 400kV AIS double busbar substation with a minimum of two feeder bays, a generator bay and a bus coupler. 2. Provide a single turn in of the Drakelow-Hams Hall 400kV circuit for the new substation. 3. Works to facilitate the Category 4 Operational Tripping Scheme as described in Appendix F3 to the Bilateral Connection Agreement | 31/10/2033
Harting Rig Wind Farm | PRO-000303 | CS-05785 | KYPE EXTENSION WIND WARM LIMITED | Harting Rig 132/33kV Substation | SPT-RI-218 Coalburn 132kV Bus Coupler Auto-Close Scheme | An auto-close scheme will be installed at Coalburn 132kV substation, to close CB 1030 if either of the two supergrid transformers, supplying the coupled MAIN 1 or RESERVE 132kV busbars, is disconnected due to an unplanned outage. | 30/10/2024
|  | CS-05786 | KYPE EXTENSION WIND WARM LIMITED | Harting Rig 132/33kV Substation | SPT-RI-181 | Installation of one 132kV line isolator at Kype Muir Wind Farm Collector Substation. At Coalburn 132kV substation, install a 132kV circuit breaker disconnectors and associated apparatus to create the 132kV bay for the Kype Muir Wind Farm Collector Substation circuit. At Kype Muir Wind farm Collector Substation install a 132kV circuit breaker and associated apparatus to terminate the 132kV cable circuit from Coalburn Substation. | 30/10/2024
Hawkwood Wind Farm | PRO-003450 | CS-08393 | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation | SPT-RI-2139 | Redshaw 400/132kV SGT2 - a new 360MVA 400/132kV supergrid transformer and associated 400kV and 132kV circuit breakers will be installed. This will increase the thermal capacity of Redshaw 132kV substation. | 30/04/2030
|  | CS-08394 | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation | SPT-RI-2826 | Hagshaw Tee to Bankend Rig III Collector Substation -Install a new 132kV trident wood pole circuit between the tee off with Hagshaw Hill Ph3 Wind Farm and the Bankend Rig III collector. The circuit capacity required for this overhead line circuit is 126MVA. The chosen conductor system for the desktop exercise is AAAC UPAS conductor. The circuit length is approximately 18km. At the Hawkwood substation a new 132/33kV substation shall be created with a 132kV circuit breaker and line disconnector being installed alongside a 132/33kV 120MVA transformer . A 33kV 3 Panel board shall be installed with one feeder being captured under this TORI and the remaining two being allocated to Hawkwood WF and Hawkwood Wind Farm. | 30/04/2030
|  | CS-08391 | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 30/04/2030
|  | CS-08395 | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation | SPT-RI-2827 | Redshaw to Hagshaw Tee 132kV Circuit - Construct a new 132kV double busbar bay at Redshaw 132kV substation and from here install a new 132kV cable/OHL circuit to an appropriate point at which a tee off shall be established for the Bankend Rig III Collector substation and Hagshaw Hill Ph3 WF connections. | 30/04/2030
|  | CS-08392 | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 30/04/2030
Heathland Wind Farm | PRO-001156 | CS-06203 | EDF ENERGY RENEWABLES LIMITED | Heathland 132/33kV Substation | Heathland H1 Works | 1. At Wishaw 275/132kV substation, installation of one 132kV circuit breaker and associated disconnectors. This will be teed connect onto the LV side of the supergrid T3 (SGT3) at Wishaw substation. 2. Installation of approximately 18km of 132kV circuit (comprising ~17km of wood pole overhead line and ~1km (sections) of underground cable) from Wishaw substation to Heathland wind farm site. 3. At Heathland wind farm 132kV substation, installation of one 132kV line isolator. | 31/03/2027
Heights Wind Farm | PRO-000792 | CS-06380 | SP Distribution plc | Bathgate (SPD) GSP | SPT-RI-1659 | Bathgate to Bonnybridge 132kV No.1 and No.2 cable uprate | 30/09/2026
Helen Street BESS | PRO-003168 | CS-09487 | Vital Energi Solutions Limited | Govan GSP | SPT-RI-3211 | NEIL BRAP-GOVA-HAGR LMS – A Load Management Scheme (LMS) is required to manage connections in the Neilston – Paisley/Braehead Park, Neilston – Paisley/Govan/Haggs Road 132 kV group to prevent overloads on these circuits. Any overload will be removed by the LMS managing the appropriate non-firm connections via the SPD interface with the connection. The signals will be sent in 3 stages and have the following intended actions: • Stage 1 Signal (95% of circuit pre-fault rating): Provides an alarm to the connection warning of impending overload condition • Stage 2 Signal (100% of circuit pre-fault rating): Trips connections associated with this TORI as per queue order • Stage 3 Signal (120% of circuit pre-fault rating): Trips all connections regardless of queue order (SPT-RI-3211) | 30/06/2026
|  | CS-09486 | Vital Energi Solutions Limited | Govan GSP | SPT-RI-243 - Devol Moor-Erskine-Braehead Park Circuit LMS | A Load Management Scheme (LMS) is required to manage connections in the Neilston – Devol Moor 132 kV group to prevent overloads on the Devol Moor-Erskine-Braehead Park Circuit. The overload will be removed by the LMS tripping the appropriate non-firm connections. | 30/06/2026
Hesta Head Wind Farm | PRO-000308 | CS-05787 | HESTA HEAD WIND FARM LIMITED | Hesta Head 132/33kV Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/10/2028
|  | CS-05788 | HESTA HEAD WIND FARM LIMITED | Hesta Head 132/33kV Substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 30/10/2028
|  | CS-05789 | HESTA HEAD WIND FARM LIMITED | Hesta Head 132/33kV Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 30/10/2028
|  | CS-05790 | HESTA HEAD WIND FARM LIMITED | Hesta Head 132/33kV Substation | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 30/10/2028
|  | CS-05791 | HESTA HEAD WIND FARM LIMITED | Hesta Head 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 30/10/2028
|  | CS-05792 | HESTA HEAD WIND FARM LIMITED | Hesta Head 132/33kV Substation | SHET-RI-019 | Establish a 220kV HVAC circuit over a distance of approximately 68km between the 275kV GIS substation at Dounreay on the mainland and the new 132kV substation in the vicinity of Finstown on Orkney. The HVAC circuit comprises of approximately 15km of land cable and 53km of subsea cable. Voltage Compensation devices will be installed at both cable ends within the substation compounds at Dounreay and Finstown. | 30/10/2028
Heysham Green Energy Centre | PRO-001710 | CS-05146 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 30/10/2028
|  | CS-05147 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 101347-202667 | 2x225MVAR MSC at Penwortham 400kV substation | 30/10/2028
|  | CS-05148 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 101348-202668 | 1x225MVAR MSC at Carrington 400kV substation | 30/10/2028
|  | CS-05149 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x760mm2 conductor or equivalent and uprating of the cable section of the circuit | 30/10/2028
|  | CS-05150 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2028
|  | CS-05151 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/10/2028
|  | CS-05152 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor triggered by R4 connection | 30/10/2028
|  | CS-05153 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 400kV circuits and the Cellarhead – Macclesfield and Cellarhead – Drakelow 400kV circuits | 30/10/2028
|  | CS-05154 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor triggered from R4 connection | 30/10/2028
|  | CS-05155 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 30/10/2028
|  | CS-04643 | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation | 101603 – 203226 | At Heysham 400kV Substation: 1. Make provision for the new connection of the User 2. Local works to connect the User into Heysham Intertripping Scheme | 30/10/2028
High Constellation Windfarm | PRO-000416 | CS-06381 | HIGH CONSTELLATION WINDFARM LIMITED | Crossaig 132kV Substation | SPT-RI-028 | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | 30/04/2025
|  | CS-05794 | HIGH CONSTELLATION WINDFARM LIMITED | Crossaig 132kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 30/04/2025
|  | CS-05795 | HIGH CONSTELLATION WINDFARM LIMITED | Crossaig 132kV Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 30/04/2025
|  | CS-05793 | HIGH CONSTELLATION WINDFARM LIMITED | Crossaig 132kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 30/04/2025
Highland BESS | PRO-003845 | CS-09753 | GPC Battery Ltd | Boat of Garten GSP | SHET-RI-235 | Knocknagael 275kV - Reserve bus section circuit breaker – Install a reserve bus section circuit breaker at Knocknagael 275kV substation. | 30/05/2030
|  | CS-09754 | GPC Battery Ltd | Boat of Garten GSP | SHET-RI-249 | Highland BESS 132kV Substation and Cable Works –Construction of the new Highland BESS 132kV substation and a 132kV 1km double cable circuit, connecting into the Tomatin – Boat of Garten 132kV circuit in a "turn in" arrangement. This construction arrangement will turn this into a Tomatin – Highland BESS – Boat of Garten 132kV circuit. | 30/05/2030
HIGH MARNHAM | PRO-001769 | CS-05156 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 100450-201015 | Uprate the Cottam - Keadby 1 and 2 circuits to achieve a post fault winter rating of 3300MVA. | 01/06/2029
|  | CS-05157 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 01/06/2029
|  | CS-05158 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 01/06/2029
|  | CS-05159 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 101593-203208 | Reconductor Cottam-Staythorpe 400kV circuit 1 to achieve a post summer rating of 2960 MVA | 01/06/2029
|  | CS-05160 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 101483-202930 | Uprate Brinsworth to Thurcroft 1 cct | 01/06/2029
|  | CS-05161 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 030613-030613 | Reconductor Cottam-Staythorpe 400kV circuit 2 to achieve a post winter fault rating 3100 MVA. | 01/06/2029
|  | CS-05162 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 01/06/2029
|  | CS-05163 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 100844-201689 | Uprating of Cottam - Staythorpe 1 to achieve a post fault winter rating of 2650MVA | 01/06/2029
|  | CS-05164 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 01/06/2029
|  | CS-05165 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 100171-200449 | Reconductoring the 2x400mm2 sections of the Thorpe Marsh – West Melton circuit 1 for operation at 65 degrees provide a post-fault winter rating of 1090MVA | 01/06/2029
|  | CS-05166 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 100821-201659 | Hotwire Creyke Beck - Keadby - Killingholme(Keadby leg) 400kV circuit to achieve a pre summer rating of 2500 MVA | 01/06/2029
|  | CS-05167 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 01/06/2029
|  | CS-05168 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 101594-203209 | Reconductor the Neepsend-Pitsmoor 275kV cable section to achieve a post summer fault of 500 MVA | 01/06/2029
|  | CS-05169 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 01/06/2029
|  | CS-05170 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 101482-202929 | Uprate Aldwarke to Brinsworth -Thurcroft cct 1 | 01/06/2029
|  | CS-04756 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 100907-201823 | Uprate High Marnham – Thurcroft – West Melton (High Marnham Leg) | 01/06/2029
|  | CS-04757 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 101586-203198 | Extension of the existing High Marnham 275kV substation busbars to accommodate the User’s bay | 01/06/2029
|  | CS-04758 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 101480-202927 | Uprate High Marnham – Thurcroft – West Melton (West Melton Leg) | 01/06/2029
|  | CS-04759 | TRANQUILITY ENERGY LIMITED | High Marnham GSP | 101481-202928 | Uprate High Marnham – Thurcroft – West Melton (Thurcroft Leg) | 01/06/2029
High Marnham (Tertiary) | PRO-000531 | CS-06207 | ENSO GREEN HOLDINGS K LIMITED | High Marnham 400kV Substation | 100957-201908 | 1. Install a tertiary cable box or bushings on SGT 2. 2. Install a 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 30/09/2025
High Marnham 400 | PRO-002194 | CS-08932 | ENSO GREEN HOLDINGS LIMITED | High Marnham 400kV Substation | 102048-204215 | Extend High Marnham 400kV substation and make provision for the connection of the User’s bay. | 31/10/2033
|  | CS-08933 | ENSO GREEN HOLDINGS LIMITED | High Marnham 400kV Substation | 101873-203846 | Construct new High Marnham 400kV substation with 20 bays for network reinforcement. | 31/10/2033
High Mathernock Battery Storage | PRO-002273 | CS-08088 | Forestry Finance Ltd | Devol Moor 132kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 17/10/2029
|  | CS-08089 | Forestry Finance Ltd | Devol Moor 132kV Substation | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 17/10/2029
Highview Hunterston East Cryobattery | PRO-001348 | CS-06639 | HVS GRIDCO LTD | Hunterston East 400kV Substation | SPT-RI-1857 | Hunterston East to Highview Hunterston 400kV Switchgear and Cable Works | 30/06/2024
Hill of Lybster Wind Generating Station | PRO-000667 | CS-06261 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 30/04/2023
|  | CS-06262 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-006 | Install two x 240MVA 220kV 3.6km underground cable circuits from a transition joint near Ardneil bay to Hunterston. Develop a new transformer compound at Hunterston comprising 2 x 400/220kV 240MVA transformers, each equipped with tertiary connected 60MVAr shunt reactors. Install two new feeder bays of 400kV GIS double busbar switchgear at Hunterston East 400kV Substation and establish 400kV connections to the new transformer compound. Complete Associated civil works and other miscellaneous works including installation/modification of associated protection, control, telecommunications and metering equipment. | 30/04/2023
|  | CS-06263 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 30/04/2023
|  | CS-06264 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 30/04/2023
|  | CS-06265 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-005 | Extend both the 275kV and 132kV busbars and install a second 275/132kV interbus auto-transformer at Dounreay substation. Upgrade the existing 150MVA interbus auto-transformer at Dounreay to 240MVA. | 30/04/2023
|  | CS-06266 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/04/2023
|  | CS-06267 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 30/04/2023
|  | CS-06268 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 30/04/2023
|  | CS-06269 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 30/04/2023
|  | CS-06270 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 30/04/2023
|  | CS-06271 | Scottish Hydro Electric Power Distribution Plc | Dounreay GSP | SHET-RI-037 | Fyrish 275/132kV Substation – Establish a new 275kV/132kV Fyrish substation close to the existing Alness 132kV OHL Teed location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. Two new 132kV underground cables will be installed to link the new 275kV/132kV Fyrish substation with the existing Alness GSP. (SHET-RI-037) | 30/04/2023
Hill of Towie 2 Wind Farm | PRO-000938 | CS-05796 | Renewable Energy Systems Limited | Keith GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 27/06/2025
|  | CS-05797 | Renewable Energy Systems Limited | Keith GSP | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 27/06/2025
Hinkley Point C | PRO-000142 | CS-05798 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-21132S | Swaps the Hinkley Point – Melksham 2 circuit and the Bramley Melksham 2 circuit line entries at Melksham 400kV substation. | 09/02/2026
|  | CS-05799 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-20832S | Installation of a new 18-bay 400kV GIS double busbar substation at Hinkley Point, consisting of eight feeder bays, two bus couplers, four bus sections, two skeletal generator bays and two skeletal station transformer bays. | 09/02/2026
|  | CS-05800 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-20898 | Connecting new Hinkley Point - Seabank 1 circuit to the existing SGT4 bay. Tee-connect new Hinkley Point – Seabank 2 circuit to the existing Seabank – Melksham circuit at very close proximity to Seabank 400kV substation | 09/02/2026
|  | CS-05801 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-21132L | Construction of a short section of new OHL between the line entries of above two circuits at Melksham 400kv substation (approx 800m). | 09/02/2026
|  | CS-05802 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-20832L | Decommissioning the 2 Bridgwater feeder bays at Hinkley Point 275kV substation and re-configure all 6 of the existing 400kV and 275kV feeder circuits at Hinkley Point to facilitate a new connection between Hinkley point and Seabank. | 09/02/2026
|  | CS-05803 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-20897L1 | Breaking into the existing Hinkley Point - Melksham OHL route near M5 motorway and teeing it into the Hinkley Point - Bridgwater circuit by a short (4km) section of new OHL. Install 3 x 700mm² (Araucaria) or 2 x 850mm² (Redwood) conductors on the new build section of the OHL, operating at 90°C. | 09/02/2026
|  | CS-05804 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-20897L2 | Build a new circuit between the Hinkley Point leg of the broken Hinkley Point - Melksham OHL route and Seabank 400kV substation (~47km). Install 3 x 700mm² (Araucaria) or 2 x 850mm² (Redwood) conductors operating at 90°C. | 09/02/2026
|  | CS-05805 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-21535S, NGET-RI-21535C & NGET-RI-21535T1, 21535T2 | A new GSP at Sandford to supply WPD as a consequence of taking over WPD's 132kV 'F' route to construct the new Hinkley Point - Seabank OHL. | 09/02/2026
|  | CS-05806 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-20897L4 | Uprating the 275kV Hinkley Point - Bridgwater VQ route to 400kV operation and reconductoring from the tee point to Hinkley Point with GAP equivalent conductor. | 09/02/2026
|  | CS-05807 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-20897Q | The work associated with the removal of the existing fluid fill cables at Hinkley Point site between the terminal tower of the VQ route and the Hinkley Point A substation (275kV). | 09/02/2026
|  | CS-05808 | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation | NGET-RI-20899 & 20899C | Replacing the 275kV disconnectors, earth switches, post insulators, CVTs and busbars at Bridgwater with 400kV equipment. Replacing the two 275/132kV SGTs at Bridgwater with two 400/275kV SGTs including associated protection. | 09/02/2026
Hirfynydd and Mynydd Drumaur | PRO-001899 | CS-07403 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation | 101829-203753 | 0 | 31/10/2028
|  | CS-07404 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation | 101614-203242 | Extension of South Wales Operational Tripping Scheme | 31/10/2028
|  | CS-07405 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation |  | FALSE | 31/10/2028
|  | CS-07406 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 31/10/2028
|  | CS-07407 | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation | 020903-020903 | Uprating/replacement of the Cowley – Walham and Cowley - Minety 400kV circuits cables sections to achieve 1193MVA or greater prefault Summer rating. | 31/10/2028
Hirwaun Power Station | PRO-000309 | CS-05809 | HIRWAUN POWER LIMITED | Rhigos 400kV Substation | 032601-032601 | Extend the existing Rhigos 400kV substation busbar for the connection of the User. Install one bus coupler bay and modify the existing bus coupler circuit breaker to operate as a bus section breaker. | 30/09/2023
Holdsworth Road | PRO-002338 | CS-08675 | MAS 002 LIMITED | Bradford West 275kV Substation | 101719-203428 | Uprate the Norton leg of the new Norton- Osbaldwick/ Poppleton 400 kV circuits to provide a pre-fault summer rating of 2350 MVA | 24/10/2036
|  | CS-08674 | MAS 002 LIMITED | Bradford West 275kV Substation | 101599-203218 | Reconductor the Padiham-Penwortham 1 circuit to achieve a Summer prefault rating of 2110MVA. | 24/10/2036
|  | CS-08678 | MAS 002 LIMITED | Bradford West 275kV Substation | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x780mm2 conductor or equivalent and uprating of the cable section of the circuit | 24/10/2036
|  | CS-08679 | MAS 002 LIMITED | Bradford West 275kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 24/10/2036
|  | CS-08684 | MAS 002 LIMITED | Bradford West 275kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 24/10/2036
|  | CS-08672 | MAS 002 LIMITED | Bradford West 275kV Substation | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400kV circuit with 2x760mm2 conductor. Uprate the cable on the Daines-Macclesfield 400kV circuit | 24/10/2036
|  | CS-08677 | MAS 002 LIMITED | Bradford West 275kV Substation | 101915-203912 | Uprate Carrington - Penworthham 400kV ZQ OHL Line to 620mm2 Matthew Gap conductor. | 24/10/2036
|  | CS-08682 | MAS 002 LIMITED | Bradford West 275kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 24/10/2036
|  | CS-08671 | MAS 002 LIMITED | Bradford West 275kV Substation | 102459-205024 | Construct a new double busbar 275kV Substation at Bradford Wes | 24/10/2036
|  | CS-08683 | MAS 002 LIMITED | Bradford West 275kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 24/10/2036
|  | CS-08670 | MAS 002 LIMITED | Bradford West 275kV Substation | 102458-205022 | Make provision for connection of user bay at Bradford West 275kV Substation | 24/10/2036
|  | CS-08680 | MAS 002 LIMITED | Bradford West 275kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with new 2750MVA unit. | 24/10/2036
|  | CS-08681 | MAS 002 LIMITED | Bradford West 275kV Substation | 102100-204294 | 2x225MVAR MSC at Carrington 400kV substation | 24/10/2036
|  | CS-08676 | MAS 002 LIMITED | Bradford West 275kV Substation | 102102-204297 | Reconductor the Carrington – Daines 400kV double circuit achieve a Summer pre fault of 3100MVA (cct 3&amp;4). Reconductor the Carrington - Daines 400kV circuit with 3x700mm2 AAAC at 90ºC (3160MVA). L6/5 | 24/10/2036
|  | CS-08673 | MAS 002 LIMITED | Bradford West 275kV Substation | 101939-203974 | Reconductor the Drakelow – Rugeley 400kV (~21km) circuit with 2x620mm2 conductor GZTACSR conductor or equivalent (Not effective but because of overload) | 24/10/2036
Hollandmey Renewable Energy Development | PRO-001094 | CS-05810 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation | Hollandmey H1 Works | Establish a new 132kV double busbar GIS feeder bay at the new Gills Bay 132kV switching station, complete with 132kV busbar selector disconnectors, 132kV line circuit breaker and 132kV line disconnector. 2. The Sole Secured Enabling Works also include the installation of approximately 3.5km of 132kV overhead line from the Gills Bay 132kV feeder to the new 132/33kV substation building at the User’s windfarm. At the windfarm substation, the 132kV overhead line will terminate to a new 132kV cable sealing end. Installation of an underground cable to connect the overhead line to a new 132kV AIS switch bay within the windfarm substation building. | 01/05/2029
|  | CS-05811 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation | SHET-RI-028 Thurso to Gills Bay | Gills Bay – Thurso South 132kV Double Circuit - It is proposed to construct a new 132kV GIS double busbar arrangement substation at a suitable location around Gills Bay (west of John O’Groats) and connect in two OHL radial circuits from Thurso south. (SHET-RI-028). | 01/05/2029
|  | CS-05812 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 01/05/2029
|  | CS-05813 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 01/05/2029
|  | CS-05814 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 01/05/2029
Holmston Farm Battery Energy Storage System | PRO-002359 | CS-08327 | Renewable Energy Systems Limited | Ayr 275/33 kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/06/2025
Hopsrig Wind Farm | PRO-000318 | CS-06335 | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 30/11/2026
|  | CS-06336 | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-294 | Ewe Hill to Hopsrig collector substations 132kV circuit | 30/11/2026
|  | CS-06337 | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 30/11/2026
|  | CS-05815 | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-191 | The thermal capacity of the 132kV circuit between Gretna 132kV substation and Ewe Hill Wind Farm 132kV Collector Substation (works detailed in SPT-RI-017), will be increased by re-conductoring the 132kV overhead line utilising “Lark” High Temperature Low Sag (HTLS) conductor (~16km), and installing an additional 800mm2 Al XLPE 132kV underground cable in parallel with the existing cable(~0.3km), to give a minimum summer continuous rating of 224MVA. This is to accommodate additional generation connecting at the Ewe Hill Wind Farm 132kV Collector Substation. | 30/11/2026
|  | CS-05816 | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-232 | Ewe Hill Substation Transformer 132/33kV - Installation of a new 132/33kV 90MVA transformer at Ewe Hill Wind Farm Substation. This will create a new 33kV busbar to allow new generation to connect. (SPT-RI-232). | 30/11/2026
Hornsea Power Station 3 | PRO-000434 | CS-05182 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 01/10/2026
|  | CS-05183 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 033750-033750 | Uprate the circuit bay Busbar, CT and Circuit Breaker attached to existing A654 circuit (BRFO-PELH) and uprate the circuit bay Busbar, CT, Circuit Breaker, disconnector and main protection system on the newly formed second Bramford – Pelham circuit (currently part of A646 BRFO-BRAI circuit) to achieve a post fault winter rating of 3820MVA | 01/10/2026
|  | CS-05184 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 100709-201476 | Extension of the existing Norwich Main 400 kV substation by 2 bays to accommodate a new double circuit Bramford - Norwich Main | 01/10/2026
|  | CS-05185 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 100709-201478 | Extend Bramford 400kV Substation by 2 bays to accommodate a new double circuit Bramford - Norwich Main | 01/10/2026
|  | CS-05176 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 032452-032452 | Connection of an OFTO bay into existing spare bay. Extension of the existing Norwich Main 400 kV substation on the East side to accommodate a new fully populated bus coupler circuit breaker and reconfiguration of SGT5 bay. | 01/10/2026
|  | CS-05177 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 032452-201027 | Extension of the existing Norwich Main 400 kV substation on the West side to accommodate the connection of an OFTO bay, a new fully populated bus coupler circuit breaker bay, fully populated section circuit breaker bay with circuit breakers on both Main and Reserve busbar and a new feeder bay to accommodate the transposed Norwich Main – Bramford 1 circuit. | 01/10/2026
|  | CS-05178 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 032452-201482 | Provision and installation of a new 400 kV section circuit breaker in the existing section on the Reserve busbar of Norwich Main 400kV substation. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement to accommodate both OFTO bays. | 01/10/2026
|  | CS-05179 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 100637-201311 | Uprate the Rayleigh Main – Tilbury 400 kV circuit to a post fault winter rating of 2210MVA | 01/10/2026
|  | CS-05180 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 01/10/2026
|  | CS-05181 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 01/10/2026
|  | CS-05825 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 32452 | Extension of the existing Norwich Main 400 kV substation to accommodate the connection of 2 skeletal bays, a new busbar coupler circuit breaker bay and a new reserve busbar section circuit breaker bay. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement. | 01/10/2026
|  | CS-05826 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Offshore Platform 3 Substation | 11630I | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 01/10/2026
Hornsea Power Station 3A-2 (formerly 3B) | PRO-000433 | CS-05827 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Platform 3B Offshore Substation | 32452 | Extension of the existing Norwich Main 400 kV substation to accommodate the connection of 2 skeletal bays, a new busbar coupler circuit breaker bay and a new reserve busbar section circuit breaker bay. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement. | 01/10/2023
|  | CS-05828 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Platform 3B Offshore Substation | 11630I | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 01/10/2023
Hornsea Power Station 4 | PRO-000435 | CS-05186 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 033837-033837 | At Creyke Beck 400kV Substation: Extend Main 1 and Reserve 1 busbars for a Main 3 and Reserve 3 Section Breaker, one Hornsea P4 First Bay and one feeder bay (Interconnector 1 to Creyke Beck 400kV Main and Reserve busbars 4). | 01/04/2027
|  | CS-05187 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 01/04/2027
|  | CS-05188 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 01/04/2027
|  | CS-05189 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. New Circuit Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/04/2027
|  | CS-05190 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 033837-201012 | At Creyke Beck 400kV Substation: Build a new 400kV GIS double busbar compound with 2 feeders bay, 1 coupler bay, 1 section bay and connect 2 new interconnectors to Creyke Beck 400kV substation. | 01/04/2027
|  | CS-05191 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 033837-201648 | At Creyke Beck 400kV Substation: Move Creyke Beck - Thornton 2 circuit and Creyke Beck - Humber Refinery - Keadby circuit to the new GIS Creyke Beck 400kV Compound. | 01/04/2027
|  | CS-05192 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 01/04/2027
|  | CS-05193 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 033837-201649 | At Creyke Beck 400kV Substation: Install an 8 Ohm series reactor, utilising the vacated Creyke Beck – Humber Refinery – Keadby feeder bay, with an additional feeder bay to be established by extension of Main and Reserve busbar 3. | 01/04/2027
|  | CS-05194 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm2 conductor | 01/04/2027
|  | CS-05195 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/04/2027
|  | CS-05196 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 01/04/2027
|  | CS-05197 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100206-200545 | Installation of a 225MVAr MSC at West Burton 400kV substation | 01/04/2027
|  | CS-05198 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm2 cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm2 cable. | 01/04/2027
|  | CS-05199 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100460-201025 | At Creyke Beck 400kV Substation: Extend Main & Reserve busbars 5 to allow one Hornsea P4 Second Bay. Extend the OTS to include Hornsea P4 Second Bay. | 01/04/2027
|  | CS-05200 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100450-201015 | Hotwire the 4x400mm2 sections of the Cottam - Keadby 1 and 2 circuits to an operating temperature of 75°C and reconductor the 2x500mm2 AAAC sections of the circuits with 2×620mm2 GZTACSR conductor. | 01/04/2027
|  | CS-05201 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 01/04/2027
|  | CS-05202 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100816-201651 | Reconductor Cottam - Grendon ZDA & ZA route to 2x570mm2 conductor to achieve a post fault winter rating of 2310MVA. | 01/04/2027
|  | CS-05203 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 01/04/2027
|  | CS-05204 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/04/2027
|  | CS-05205 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100161-200456 | At Eggborough 400kV: Replace circuit breakers X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/04/2027
|  | CS-05206 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100909-201825 | Uprate the existing bays in the Creyke Beck – Thornton 2 circuit (A323) to achieve a post fault summer rating of 3300MVA. | 01/04/2027
|  | CS-05207 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 100987-201984 | Uprate the existing bays in the Creyke Beck – Thornton 1 circuit to achieve a post fault summer rating of 3300MVA. | 01/04/2027
|  | CS-05829 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 33837-3 | Installation of a series reactor at Creyke Beck, utilising the vacated Thornton circuit bay can be used as one of the bay, with an additional bay to be established byextension of Main Bar 2 and Reserve Bar 2. | 01/04/2027
|  | CS-05830 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 33837-2 | Installation of a new feeder bay on the new bus section and transfer of one of the Thornton circuits into this bay. | 01/04/2027
|  | CS-05831 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 33837-4 | Provision of a skeletal bay in new bus section at Creyke Beck 400kV substation to allow connection of the offshore transmission cicuit. | 01/04/2027
|  | CS-05832 | ORSTED HORNSEA PROJECT FOUR LIMITED | Hornsea Offshore Platform 4 Substation | 33837-1 | Installation of a new section switch in both Main Bar 1 and Reserve busbar 1 at Creyke Beck 400kV substation substation. | 01/04/2027
Hornsea Power Station Project 3B-1 (formerly 3C) | PRO-000458 | CS-05833 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Platform 3C Offshore Substation | 32452 | Extension of the existing Norwich Main 400 kV substation to accommodate the connection of 2 skeletal bays, a new busbar coupler circuit breaker bay and a new reserve busbar section circuit breaker bay. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement. | 01/04/2024
|  | CS-05834 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Platform 3C Offshore Substation | 11630I | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 01/04/2024
Hornsea Power Station Project 3B-2 (formerly 3D) | PRO-000457 | CS-05835 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Platform 3D Offshore Substation | 32452 | Extension of the existing Norwich Main 400 kV substation to accommodate the connection of 2 skeletal bays, a new busbar coupler circuit breaker bay and a new reserve busbar section circuit breaker bay. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement. | 01/10/2024
|  | CS-05836 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Hornsea Platform 3D Offshore Substation | 11630I | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 01/10/2024
Househill BESS | PRO-001499 | CS-08111 | HOUSEHILL BESS LIMITED | Nairn GSP | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 31/10/2027
Housham PV & BESS | PRO-002254 | CS-07913 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 102070-204246 | Extension of the newly built Navenby 400kV substation busbars to accommodate the User’s bay | 30/05/2033
|  | CS-07915 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 30/05/2033
|  | CS-07924 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 30/05/2033
|  | CS-07926 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 30/05/2033
|  | CS-07925 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 30/05/2033
|  | CS-07920 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100451-201016 | Reconductor the 2x500mm2 sections of the High Marnham – West Burton 400kV circuit with 2x570mm2 conductor and replace the cable section. | 30/05/2033
|  | CS-07922 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100590-201212 | Reconductor the 2x500mm2 sections of the Ratcliffe – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 30/05/2033
|  | CS-07927 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100798-201612 | At Cottam 400kV Substation: Uprate feeder bay disconnector and circuit breaker on the Cottam - West Burton circuit to provide a post fault summer rating of 3060MVA | 30/05/2033
|  | CS-07921 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100459-201024 | Reconductor the 2x500mm2 section of the High Marnham – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 30/05/2033
|  | CS-07912 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101687-203363 | Establish a double turn in connection between the new 400kV substation and the West Burton – Bicker Fen 400kV circuit 1 and 2 | 30/05/2033
|  | CS-07911 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101687-203362 | Build a new Navenby 400kV Double Busbar Substation with 4 Feeder bays, and 1 Coupler Bay in the vicinity of tower 4ZM508. | 30/05/2033
|  | CS-07914 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 30/05/2033
|  | CS-07923 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 30/05/2033
|  | CS-07916 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 30/05/2033
|  | CS-07917 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 30/05/2033
|  | CS-07918 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 30/05/2033
|  | CS-07919 | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 30/05/2033
Howmuir PV | PRO-001234 | CS-06245 | Scottish Hydro Electric Power Distribution Plc | Lunanhead GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 30/11/2021
Hunterston Battery Storage Facility | PRO-001155 | CS-04308 | FLEXIBLEGRIDPOWER2 LTD | Ayrshire Grid 400kV Substation | SPT-RI-1566 | Hunterston East to Ayrshire Grid 400kV switchgear and cable works - It is proposed to extend the GIS double busbar and install a new 400kV switchbay at Hunterston East 400kV GIS substation, install approximately 900m of 400kV underground cable from the Hunterston East 400kV GIS substation to a new collector substation (Ayrshire Grid 400kV collector substation). At the collector substation, a new outdoor 400kV busbar and three isolators shall be installed. | 16/12/2024
Hunterston Energy Storage Facility | PRO-001644 | CS-04467 | ENERGYGRIDPOWER2 LTD | Ayrshire Grid 400kV Substation | SPT-RI-1566 | Hunterston East to Ayrshire Grid 400kV switchgear and cable works - It is proposed to extend the GIS double busbar and install a new 400kV switchbay at Hunterston East 400kV GIS substation, install approximately 900m of 400kV underground cable from the Hunterston East 400kV GIS substation to a new collector substation (Ayrshire Grid 400kV collector substation). At the collector substation, a new outdoor 400kV busbar and three isolators shall be installed. | 16/12/2024
Hunterston Wind Farm | PRO-003165 | CS-09332 | GALILEO 01 LIMITED | Hunterston Farm GSP | Hunterston WF Circuit | Installation of approx. 5km of 132kV circuit (OHL/UGC) from Hunterston East 132kV substation to Hunterston Windfarm 132k | 30/08/2030
|  | CS-09331 | GALILEO 01 LIMITED | Hunterston Farm GSP | Hunterston WF Feeder Bay | Installation of a new 132kV GIS DBB feeder bay and associated switchgear (circuit breaker and DBB disconnectors) | 30/08/2030
|  | CS-09330 | GALILEO 01 LIMITED | Hunterston Farm GSP | SPT-RI-2832 | New Hunterston East 132kV GIS Substation - existing Hunterston 132kV indoor switchboard be replaced with a new GIS building which shall accommodate 11 bays of non-SF6 gas insulated switchgear bays with 2 x SGT transformer bays (SGT1 and SGT2), 3 x Feeder bays (Hunterston Farm1-Kilwinning, Hunterston Farm2-Saltcoats and Kilwinning-Saltcoats), 1 x Bus-coupler bay, 1 x Bus-section bay and future provision for 4 x spare feeder bay | 30/08/2030
|  | CS-09333 | GALILEO 01 LIMITED | Hunterston Farm GSP | Hunterston WF Disconnector | Installation of a 132kV line disconnector at the Hunterston Windfarm substation | 30/08/2030
Icewind Blyth | PRO-001717 | CS-05222 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 101548-203088 | At Blyth 400kV Substation: Extend Main and Reserve bar section to accommodate a User bay, install 2 new section breakers in both Main and Reserve busbar, create a new feeder bay and transfer the Blyth-Eccles - Stella West 2 circuit and install a generator intertripping scheme. | 31/10/2031
|  | CS-05223 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-05224 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 31/10/2031
|  | CS-05225 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 101369-202689 | Reconductor the Blyth legs of the Blyth – Eccles – Stella West 1 and Blyth – Eccles – Stella West 2 circuits with GAP conductor and replace the cable sections of both circuits. | 31/10/2031
|  | CS-05226 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a post-fault winter rating of 3100MVA | 31/10/2031
|  | CS-05227 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 101386-202715 | Reconductor the 2x700mm2 sections of the Lackenby-Thornton 1+2 circuit with 2x850mm2 conductor. Reconductor the 4x400mm2 sections with 2x850mm2 conductor. Uprate the cable section of this circuit. (2850MVA). | 31/10/2031
|  | CS-05228 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 101370-202690 | At Blyth 400kV / 275kV substation: Install 2 new 1100MVA rated interbus transformers. | 31/10/2031
|  | CS-05229 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 101540-203059 | Reconductor the South Shields – West Boldon 275kV circuit with 1x525mm2 Curlew conductor. | 31/10/2031
|  | CS-05230 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 31/10/2031
|  | CS-05231 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 101385-202714 | At Blyth 275kV substation: Replace busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. | 31/10/2031
|  | CS-05232 | Hecate Offshore Wind Limited | Blyth 400kV Substation | SPT- Icewind Blyth H1 | a. Reconfiguration and/ or replacement of Main Protections at Eccles 400kV Substation on the Eccles – Stella West/ Blyth 400kV circuits. The final scope of protection and control works will be subject to detailed engineering design and studies, the scope of which shall include ‘hardware-in-the-loop’ transient testing, to be performed by real time simulation using relays provided by the Relevant Transmission Licensees, and with a suitable and sufficient representation of the User’s DC Converters and system, their controls, reactive compensation and filter equipment to be provided by the User. b. Modification of Series Compensation Equipment at Eccles 400kV Substation on the Eccles – Stella West/ Blyth 400kV circuits as required. The final scope of series compensation related works will be subject to a detailed engineering design and studies to be completed by the series compensation equipment Original Equipment Manufacturer. | 31/10/2031
|  | CS-05233 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-05234 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 31/10/2031
|  | CS-05235 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 100818-201654 | Establish a new 400kV circuit between Creyke Beck and Grimsby West 400kV substations | 31/10/2031
|  | CS-05236 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 101553-203094 | Turn in the Cottam-Staythorpe 400KV circuit at High Marnham 400KV | 31/10/2031
|  | CS-05237 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 100110-200299 | Install three new 225MVAr MSCs at Norton, Osbaldwick and Stella West 400kV substations. (NOA NEMS). | 31/10/2031
|  | CS-05238 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 033463-033463 | Uprate the Norton - Osbaldwick 1 OHL circuit to achieve at least a post-fault Winter rating of 2550MVA. | 31/10/2031
|  | CS-05239 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 31/10/2031
|  | CS-05240 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 31/10/2031
|  | CS-05241 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 020669-020669 | Lackenby – Norton 1 circuit reconductor the 2x570mm2 sections with 2x620mm2 GZTACSR conductor. Replace the cable section of the circuit. | 31/10/2031
|  | CS-05242 | Hecate Offshore Wind Limited | Blyth 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 31/10/2031
Icewind Connah's Quay | PRO-001719 | CS-04497 | Hecate Offshore Wind Limited | Connah's Quay 400kV Substation | 101513-202982 | Infrastructure works for the connection of the IceWind offshore wind farm at Connah’s Quay 400kV substation. Busbar extension and associated database and protection changes. | 01/11/2033
|  | CS-04498 | Hecate Offshore Wind Limited | Connah's Quay 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 01/11/2033
|  | CS-04499 | Hecate Offshore Wind Limited | Connah's Quay 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 01/11/2033
|  | CS-04500 | Hecate Offshore Wind Limited | Connah's Quay 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 01/11/2033
|  | CS-04501 | Hecate Offshore Wind Limited | Connah's Quay 400kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 01/11/2033
|  | CS-04502 | Hecate Offshore Wind Limited | Connah's Quay 400kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 01/11/2033
Icewind Hawthorn Pit | PRO-001718 | CS-05243 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 101550-203090 | At Hawthorn Pit 400kV Substation: Extend busbars to facilitate the User’s generator bay. | 31/10/2031
|  | CS-05244 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 030317-030317 | Rebuild the existing Hawthorn Pit 400kV compound as a full double busbar substation. Uprate the existing Hawthorn Pit - Norton 275kV to a 400kV circuit. (NOA E2DC) | 31/10/2031
|  | CS-05245 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 100058-200133 | Tee in the Hartlepool - West Boldon circuit into Hawthorn Pit 275kV Substation (NOA WHTI) | 31/10/2031
|  | CS-05246 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 31/10/2031
|  | CS-05247 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 31/10/2031
|  | CS-05248 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 31/10/2031
|  | CS-05249 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-05250 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm2 conductor | 31/10/2031
|  | CS-05251 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 31/10/2031
|  | CS-05252 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 101553-203094 | Turn in the Cottam-Staythorpe 400KV circuit at High Marnham 400KV | 31/10/2031
|  | CS-05253 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a post-fault winter rating of 3100MVA | 31/10/2031
|  | CS-05254 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-05255 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 100818-201654 | Establish a new 400kV circuit between Creyke Beck and Grimsby West 400kV substations | 31/10/2031
|  | CS-05256 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 31/10/2031
|  | CS-05257 | Hecate Offshore Wind Limited | Hawthorn Pit 400kV Substation | 101576-203163 | Uprate the Norton - Osbaldwick 2 OHL circuit to achieve a post-fault winter rating of 2550MVA (NOA NOR4 | 31/10/2031
Icewind Hinkley Point | PRO-001720 | CS-04489 | Hecate Offshore Wind Limited | Hinkley Point 400kV Substation | 020903-020903 | Uprating of the Cowley - Walham 400kV circuit cables to achieve 1500MVA post-fault summer rating. | 01/11/2028
|  | CS-04490 | Hecate Offshore Wind Limited | Hinkley Point 400kV Substation | 101364-202684 | Install a smart wire power control device on the Feckenham - Minety circuit to mitigate to 1431MVA pre-fault Summer rating. | 01/11/2028
|  | CS-04491 | Hecate Offshore Wind Limited | Hinkley Point 400kV Substation | 101514-202983 | Infrastructure works for the connection of the IceWind (Hinkley Point) offshore wind farm connecting into the Hinkley Point B 400kV substation | 01/11/2028
|  | CS-04492 | Hecate Offshore Wind Limited | Hinkley Point 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 01/11/2028
|  | CS-04493 | Hecate Offshore Wind Limited | Hinkley Point 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 01/11/2028
|  | CS-04494 | Hecate Offshore Wind Limited | Hinkley Point 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 01/11/2028
|  | CS-04495 | Hecate Offshore Wind Limited | Hinkley Point 400kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 01/11/2028
|  | CS-04496 | Hecate Offshore Wind Limited | Hinkley Point 400kV Substation | 033769-033769 | Reconductor the Taunton - Hinkley Point - Exeter 400kV circuits to achieve a 3100MVA post fault winter rating. Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating | 01/11/2028
Inchbean Energy Park | PRO-002453 | CS-08258 | RNA-ENERGY LTD | Kilmarnock Town GSP | SPT-RI-517 | Kilmarnock Town GSP asset replacement, fault level mitigation | 30/06/2025
|  | CS-08257 | RNA-ENERGY LTD | Kilmarnock Town GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/06/2025
Inch Cape Offshore Wind Farm Platform 1 | PRO-000348 | CS-06887 | INCH CAPE OFFSHORE LIMITED | Cockenzie 275kV Substation | Inch Cape Offshore Wind Farm H1 Works Item 3 | Provision of communications, alarms, indications and metering, as described in Appendix F and OF of the relevant Bilateral Connection Agreement. | 01/04/2025
|  | CS-06247 | INCH CAPE OFFSHORE LIMITED | Cockenzie 275kV Substation | SPT-RI-1742 Cockenzie LMS (Cat 2) | 4. Cockenzie Load Management Scheme (Cat 2) – An overload protection scheme is proposed to be installed within the Cockenzie – Smeaton – Kaimes – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following defined system outage conditions. (SPT-RI-1742) | 01/04/2025
|  | CS-05838 | INCH CAPE OFFSHORE LIMITED | Cockenzie 275kV Substation | Inch Cape Offshore Wind Farm H1 Works Item 1 | Installation of 275kV plant and apparatus at Cockenzie 275kV Substation which will form the connections to the two Transmission Interface Points, including busbars, disconnectors, earth switches, surge arresters, current and voltage transformers | 01/04/2025
|  | CS-05839 | INCH CAPE OFFSHORE LIMITED | Cockenzie 275kV Substation | Inch Cape Offshore Wind Farm H1 Works Item 2 | IModification of existing Bay No.2 and Bay No. 5 at Cockenzie 275kV Substation, including removal, relocation and replacement of existing assets as required. | 01/04/2025
Inch Cape Offshore Wind Farm Platform 2 | PRO-000349 | CS-06888 | INCH CAPE OFFSHORE LIMITED | Inch Cape Platform 2 220/66kV Offshore Substation | Inch Cape Offshore Wind Farm H1 Works Item 3 | Provision of communications, alarms, indications and metering, as described in Appendix F and OF of the relevant Bilateral Connection Agreement. | 01/04/2025
|  | CS-06248 | INCH CAPE OFFSHORE LIMITED | Inch Cape Platform 2 220/66kV Offshore Substation | SPT-RI-1742 Cockenzie LMS (Cat 2) | 4. Cockenzie Load Management Scheme (Cat 2) – An overload protection scheme is proposed to be installed within the Cockenzie – Smeaton – Kaimes – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following defined system outage conditions. (SPT-RI-1742) | 01/04/2025
|  | CS-05840 | INCH CAPE OFFSHORE LIMITED | Inch Cape Platform 2 220/66kV Offshore Substation | Inch Cape Offshore Wind Farm H1 Works Item 1 | Installation of 275kV plant and apparatus at Cockenzie 275kV Substation which will form the connections to the two Transmission Interface Points, including busbars, disconnectors, earth switches, surge arresters, current and voltage transformers | 01/04/2025
|  | CS-05841 | INCH CAPE OFFSHORE LIMITED | Inch Cape Platform 2 220/66kV Offshore Substation | Inch Cape Offshore Wind Farm H1 Works Item 2 | IModification of existing Bay No.2 and Bay No. 5 at Cockenzie 275kV Substation, including removal, relocation and replacement of existing assets as required. | 01/04/2025
Indian Queens Energy Centre | PRO-001371 | CS-05208 | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 31/05/2025
|  | CS-05209 | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation | 033539- 033539 | Hot wiring of the Hinkley Point – Melksham 1 and 2 circuits to increase their thermal rating | 31/05/2025
|  | CS-05210 | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 &amp; 2 Circuits to provide a post fault winter rating of 3140MVA. | 31/05/2025
|  | CS-05842 | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation | 100443-200993 | Connection | 31/05/2025
|  | CS-05843 | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 31/05/2025
Innerwick BESS | PRO-002828 | CS-09562 | ENERGYHUBDEVELOPMENTS LIMITED | Branxton 132kV | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 31/07/2028
|  | CS-09567 | ENERGYHUBDEVELOPMENTS LIMITED | Branxton 132kV | Disconnector - Branxton BESS Collector | Installation of a 132kV line disconnector at Branxton BESS 400/132kV Collector substation for the Innerwick BESS connection | 31/07/2028
|  | CS-09561 | ENERGYHUBDEVELOPMENTS LIMITED | Branxton 132kV | SPT-RI-124 | 400kV GIS substation in Torness Area - A new 23 Bay double busbar 400kV GIS substation will be installed at a site yet to be determined in the Torness Area of East Lothian. This new substation is currently named as “Branxton 400kV Substation”. (SPT-RI-124 | 31/07/2028
|  | CS-09564 | ENERGYHUBDEVELOPMENTS LIMITED | Branxton 132kV | SPT-RI-131 | ZT route overhead line uprating works (Branxton- Eccles) | 31/07/2028
|  | CS-09563 | ENERGYHUBDEVELOPMENTS LIMITED | Branxton 132kV | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 31/07/2028
|  | CS-09565 | ENERGYHUBDEVELOPMENTS LIMITED | Branxton 132kV | SPT-RI-2963 | Branxton to Eccles Further Uprating – In order to alleviate the overloads identified as part of the system studies conducted it is necessary to reconductor both sides of the Branxton to Eccles circuits with twin HTLS “Curlew” conductor. This conductor shall give a summer pre-fault rating on the circuit of 2590MVA | 31/07/2028
|  | CS-09566 | ENERGYHUBDEVELOPMENTS LIMITED | Branxton 132kV | SPT-RI-3148 | Branxton BESS Collector Substation – Install a new 400kV GIS bay at Branxton substation to accommodate the connection of these two battery storage connections. From here a new 400kV circuit shall be installed out to the new shared substation indicatively named Branxton BESS 400/132kV Collector substation. At this shared substation a 400kV line disconnector shall be installed alongside two 400kV transformer circuit breakers and two 400/132kV 360MVA transformers will be installed with each transformer requiring its own 132kV circuit breaker. This forms the scope of SPT-RI-3148 which this connection shall be contingent on. A 132kV shared busbar will be installed alongside three individual metering circuit breakers for the local connections. | 31/07/2028
Iron Acton | PRO-000455 | CS-06813 | HD000ACT LTD | Iron Acton 275kV Substation | 100810-201635 | 1. Works to facilitate the use of Iron Acton 132kV substation’s spare bay for the User’s connection. 2. Installation of a new Category 2 Operational Tripping Scheme | 30/06/2025
Iron Acton | PRO-000491 | CS-05844 | IRON ACTON GREEN LIMITED | Iron Acton 275kV Substation | 100900-201809 | Attributable | 30/09/2024
Ironbridge | PRO-001629 | CS-04541 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101484-202931 | Extension of the existing Ironbridge 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 30/10/2029
|  | CS-04542 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2029
|  | CS-04543 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2029
|  | CS-04544 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2029
|  | CS-04545 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2029
|  | CS-04546 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor. | 30/10/2029
|  | CS-04547 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2029
|  | CS-04548 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 30/10/2029
|  | CS-04549 | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/10/2029
Ironbridge Green Energy Centre | PRO-001711 | CS-04696 | INNOVA RENEWABLES LIMITED | Ironbridge 400kV Substation | 101484-202931 | Extension of the existing Ironbridge 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 30/10/2029
|  | CS-06818 | INNOVA RENEWABLES LIMITED | Ironbridge 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2029
|  | CS-06819 | INNOVA RENEWABLES LIMITED | Ironbridge 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2029
|  | CS-06820 | INNOVA RENEWABLES LIMITED | Ironbridge 400kV Substation | 100425-200972 | 3. Reconductor the existing 2x500mm2 conductor on the FeckenhamIronbridge 400kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA | 30/10/2029
|  | CS-06821 | INNOVA RENEWABLES LIMITED | Ironbridge 400kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor triggered by R4 connection | 30/10/2029
|  | CS-06822 | INNOVA RENEWABLES LIMITED | Ironbridge 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2029
|  | CS-06823 | INNOVA RENEWABLES LIMITED | Ironbridge 400kV Substation | 101284-202534 | Reconductor the existing 2x570mm2 conductor on the IronBridge- Legacy 2 and IronBridge Shrewsbury-Legacy 400 kV circuits with 2x570mm2 conductor at 90 deg. C to achieve a pre fault summer rating of 2490 MVA | 30/10/2029
|  | CS-06824 | INNOVA RENEWABLES LIMITED | Ironbridge 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/10/2029
Isenau Two | PRO-003091 | CS-09733 | Isenau Energy Storage Resources Two Limited | Tealing 132kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2033
|  | CS-09734 | Isenau Energy Storage Resources Two Limited | Tealing 132kV Substation | SHET-RI-147 | Tealing 400kV Substation - Establish a new 400kV substation close to the existing Tealing 275kV substation. | 31/10/2033
|  | CS-09735 | Isenau Energy Storage Resources Two Limited | Tealing 132kV Substation | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 31/10/2033
|  | CS-09738 | Isenau Energy Storage Resources Two Limited | Tealing 132kV Substation | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 31/10/2033
|  | CS-09740 | Isenau Energy Storage Resources Two Limited | Tealing 132kV Substation | SPT-RI-2095 | Kincardine North 400kV Substation - The scope of works at Kincardine North 400kV Substation (ref. NOA Code LWUP) is summarised as follows. The new Kincardine North 400kV GIS Substation will initially connect the following circuits: SHE Transmission Alyth No.1 400kV, SHE Transmission Alyth No.2 400kV, Denny North No.1 400kV, Denny North No.2 400kV, Kincardine No.1 400kV, and Kincardine No.2 400kV. The substation will be equipped with two bus section circuit breakers and two bus coupler circuit breakers | 31/10/2033
|  | CS-09739 | Isenau Energy Storage Resources Two Limited | Tealing 132kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 31/10/2033
|  | CS-09732 | Isenau Energy Storage Resources Two Limited | Tealing 132kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-09736 | Isenau Energy Storage Resources Two Limited | Tealing 132kV Substation | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 31/10/2033
|  | CS-09737 | Isenau Energy Storage Resources Two Limited | Tealing 132kV Substation | SHET-RI-185 | Kintore - Tealing 400kV circuit – Establish a new 400 kV double circuit overhead line between Kintore 400 kV substation and Tealing 400 kV substation. | 31/10/2033
Isle of Man Offshore Wind Farm | PRO-003698 | CS-08690 | Orsted Isle of Man (UK) Limited | Penwortham 400kV Substation | 102450-205004 | 0 | 30/10/2037
Iver | PRO-001141 | CS-05211 | PIVOTED POWER LLP | Iver 275kV Substation | NGET-RI-100278-200770 (Infra) | 1. Install earthing transformer on 13kV Tertiary connection 2. Install 13kV cable to motorised disconnector from tertiary connection 3. Install 13kV disconnector connecting tertiary to connection assets for Users connection | 31/10/2023
Jamesfield Farm Battery Storage | PRO-001237 | CS-05846 | HARMONY JF LIMITED | Abernethy GSP | SHET-RI-111 (Abernethy Mesh Corner) | Development of the 132kV Abernethy Mesh Corner - At Abernethy 132/33kV substation, install a four circuit breaker mesh corner. This will be connected to the existing Burghmuir – Charleston 132kV double circuit overhead line. | 31/10/2022
|  | CS-05847 | HARMONY JF LIMITED | Abernethy GSP | Abernethy GSP Works | The installation of two 132kV isolators as part of the mesh corner and 2 short sections of 132kV cables. This will further connect to the new grid transformers and the mesh corner at Abernethy 132/33kV Grid Supply Point substation | 31/10/2022
Jamesfield Farm Phase 2 Battery Storage | PRO-001236 | CS-05848 | HARMONY JF LIMITED | Abernethy GSP | SHET-RI-111 (Abernethy Mesh Corner) | Development of the 132kV Abernethy Mesh Corner - At Abernethy 132/33kV substation, install a four circuit breaker mesh corner. This will be connected to the existing Burghmuir – Charleston 132kV double circuit overhead line. | 31/10/2022
|  | CS-05849 | HARMONY JF LIMITED | Abernethy GSP | Jamesfield 2 BES Enabling part 1 | installation of two 132kv isolators as part of the mesh corner and 2 short sections of 132 kv cables. | 31/10/2022
|  | CS-05850 | HARMONY JF LIMITED | Abernethy GSP | SHET-RI-121 | Charleston - Abernethy 132kv reconductoring; approx 25km of 132 kv ohl between abernrethy substation and Charleston. | 31/10/2022
JBM Solar 12 - Shrewsbury Solar | PRO-001146 | CS-06825 | JBM SOLAR PROJECTS 12 LIMITED | Shrewsbury GSP | 100754-201558 | 1. Install a tertiary cable box or bushings on the SGT 3. 2. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 30/10/2024
JBM Solar 13 - Melksham | PRO-000495 | CS-07308 | JBM SOLAR PROJECTS 13 LIMITED | Melksham 400kV Substation | 100776 - 201571 | 0 | 30/06/2026
|  | CS-07310 | JBM SOLAR PROJECTS 13 LIMITED | Melksham 400kV Substation | 101305-202589 | 0 | 30/06/2026
Jersey Farm BESS | PRO-002264 | CS-09366 | CSE39 LIMITED | Exeter 400kV Substation | 102075-204256 | Replacement, or modification, of existing towers and associated OHL works to facilitate a single Tee-Point connection to Jersey Farm via the Exeter – Taunton 2 overhead line circuit. Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks, and associated infrastructure. Construction of 400kV Busbar to accommodate the OHL turn-In connection and the User’s Generator Bay. Local works to facilitate the extension of the Melksham Operational Tripping Scheme. | 25/10/2032
JG Pears | PRO-000250 | CS-05845 | JG PEARS GRID CONNECTION LIMITED | High Marnham GSP | 33237I | Provision of the skeletal bay for the User to connect. The existing SGT1 skeletal bay assets are to be transferred to the User. | 06/09/2019
Kearsley | PRO-001064 | CS-05212 | PIVOTED POWER LLP | Kearsley 400kV Substation | 100578-201127 | 1. Extend the Kearsley site as required to facilitate the transmission works 2. Install a tertiary cable box or bushings on the SGT 4 3. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer 4. Install an earthing transformer 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 31/10/2028
Kearsley North Green Energy Centre | PRO-001793 | CS-07306 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 101618-203252 | 0 | 31/10/2028
|  | CS-07307 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x760mm2 conductor or equivalent and uprating of the cable section of the circuit | 31/10/2028
|  | CS-07309 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 101618-203251 | 0 | 31/10/2028
|  | CS-07311 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 31/10/2028
|  | CS-07312 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 100425-200971 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 31/10/2028
|  | CS-07313 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 31/10/2028
|  | CS-07314 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 31/10/2028
|  | CS-07315 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 400kV circuits and the Cellarhead – Macclesfield and Cellarhead – Drakelow 400kV circuits | 31/10/2028
|  | CS-07316 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 101278-202528 | Reconductor the Legacy legs of both Connah’s Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor. | 31/10/2028
|  | CS-07317 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 101347-202667 | 2x225MVAR MSC at Penwortham 400kV substation | 31/10/2028
|  | CS-07318 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor triggered from R4 connection | 31/10/2028
|  | CS-07319 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 31/10/2028
|  | CS-07320 | INNOVA RENEWABLES LIMITED | Kearsley GSP | 101627-203263 - DUPLICATE | 0 | 31/10/2028
Kedrum Solar Farm | PRO-003444 | CS-09469 | Rosside Energy Limited | Blackhillock 275kV Substation | SHET-RI-178 | 0 | 30/05/2030
|  | CS-09470 | Rosside Energy Limited | Blackhillock 275kV Substation | SHET-RI-236 | Blackhillock - Cairnford 275kV Line Works - Establish a new 275kV tee point of the Blackhillock to Cairnford 275kV HCD2 circuit. This will require 3x 275kV line disconnectors and 1x 275kV line circuit breaker. This tee point will be adjacent to that seen from SHET-RI-178, and therefore this new TORI will be dependent on SHET-RI-178 to create the land/compound required for this new switchgear | 30/05/2030
|  | CS-09468 | Rosside Energy Limited | Blackhillock 275kV Substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 30/05/2030
|  | CS-09471 | Rosside Energy Limited | Blackhillock 275kV Substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50oC operation to 275kV 65oC operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65oC,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 30/05/2030
Keith 275kV Greener Grid Park | PRO-001525 | CS-06499 | KEITH STORAGE SOLUTIONS LIMITED | Keith 275KV Substation | SHET-RI-167 | Keith 275kV SGT1 works | 01/08/2024
Keith Battery Storage | PRO-001742 | CS-07121 | KEITH RENEWABLE LIMITED | Keith 1 132/33kV GSP Substation | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 31/10/2026
Keith BESS Station | PRO-003565 | CS-09585 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 31/10/2033
|  | CS-09587 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-09579 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-09580 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-09584 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-09588 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-09589 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-09594 | IB VOGT UK LTD | Blackhillock substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 31/10/2033
|  | CS-09593 | IB VOGT UK LTD | Blackhillock substation | SPT-RI-004 | Denny –Kincardine Reinforcement (East Coast Phase 1 Reinforcement and Re-Profiling) – Uprating of the existing Kincardine - Tealing/Kintore (XL) overhead line route from 275kV 50oC operation to 275kV 65oC operation between Kincardine and the SP Transmission/ SHE Transmission border; Protection and control works at Kincardine 275kV Substation associated with the development of the Alyth 275kV Substation; Increasing the maximum operating temperature of the Longannet – Mossmorran – Westfield - Tealing 275kV overhead line routes to 65oC,and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating; and Terminate the existing Windyhill – Lambhill - Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill - Lambhill - Denny North and Denny North - Longannet No.2 275kV circuits | 31/10/2033
|  | CS-09581 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-09582 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-09583 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-09586 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-09578 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 31/10/2033
|  | CS-09592 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-199 | Blackhillock 2 400kV Substation - Establish a new 400kV substation close to Blackhillock 400kV substation and tie in the proposed 400kV circuits as part of the NOA BBNC/BPNC upgrade. (SHETRI-199) | 31/10/2033
|  | CS-09591 | IB VOGT UK LTD | Blackhillock substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
Keith Solar Farm | PRO-002699 | CS-07368 | KEITH SOLAR PV LIMITED | Keith Solar Farm 275kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2028
|  | CS-07369 | KEITH SOLAR PV LIMITED | Keith Solar Farm 275kV Substation | SHET-RI-178 | 0 | 31/10/2028
|  | CS-07370 | KEITH SOLAR PV LIMITED | Keith Solar Farm 275kV Substation | Keith Solar Item | 0 | 31/10/2028
Kelloe Mains | PRO-002425 | CS-08538 | TBC 003 LIMITED | Kelloe Mains 400kV Substation | SPT-RI-131 | ZT route overhead line uprating works (Branxton- Eccles) | 22/11/2029
|  | CS-08537 | TBC 003 LIMITED | Kelloe Mains 400kV Substation | SPT-RI-2825 OHL | 0 | 22/11/2029
|  | CS-08536 | TBC 003 LIMITED | Kelloe Mains 400kV Substation | SPT-RI-2825 SS | Kelloe Mains 400kV Substation | 22/11/2029
Kennoxhead Wind Farm | PRO-000319 | CS-05857 | ORSTED ONSHORE UK LIMITED | Kennoxhead GSP | SPT-RI-218 Coalburn 132kV Bus Coupler Auto-Close Scheme | An auto-close scheme will be installed at Coalburn 132kV substation, to close CB 1030 if either of the two supergrid transformers, supplying the coupled MAIN 1 or RESERVE 132kV busbars, is disconnected due to an unplanned outage. | 27/02/2024
|  | CS-05858 | ORSTED ONSHORE UK LIMITED | Kennoxhead GSP | SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 27/02/2024
|  | CS-05859 | ORSTED ONSHORE UK LIMITED | Kennoxhead GSP | Kennoxhead Wind Farm Sole Enabling Works | 1. Installation of one 132kV line isolator at Kennoxhead wind farm substation. 2. Installation of approximately 2km of 132kV XLPE cable out of Coalburn 132kV substation. 3. Installation of approximately 15.4km 132kV wood pole overhead line between Kennoxhead wind farm substation and Coalburn substation. 4. At Coalburn substation, install a new 132kV bay including circuit breaker, isolator, surge arrester and associated switchgear to connect the new line connecting to Kennoxhead wind farm substation. | 27/02/2024
Kilbraur North Wind Farm | PRO-003987 | CS-09689 | EDF ENERGY RENEWABLES LIMITED | Kilbraur Wind Farm Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2031
|  | CS-09691 | EDF ENERGY RENEWABLES LIMITED | Kilbraur Wind Farm Substation | SPT-RI-252 | Works required at Mossmoran 132 KV ss to remove fault level limitations introduced by 8 GEC FC1 circuit breakers (1983) | 31/10/2031
|  | CS-09685 | EDF ENERGY RENEWABLES LIMITED | Kilbraur Wind Farm Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90 degrees Celsius to increase the continuous current rating of the circuit | 31/10/2031
|  | CS-09684 | EDF ENERGY RENEWABLES LIMITED | Kilbraur Wind Farm Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/10/2031
|  | CS-09690 | EDF ENERGY RENEWABLES LIMITED | Kilbraur Wind Farm Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2031
|  | CS-09686 | EDF ENERGY RENEWABLES LIMITED | Kilbraur Wind Farm Substation | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 31/10/2031
|  | CS-09687 | EDF ENERGY RENEWABLES LIMITED | Kilbraur Wind Farm Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 31/10/2031
|  | CS-09688 | EDF ENERGY RENEWABLES LIMITED | Kilbraur Wind Farm Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 31/10/2031
Killoch BESS | PRO-004171 | CS-09802 | Renewable Energy Systems Limited | Killoch BESS 275kV substation | SPT-RI-3569 SS | 0 | 30/09/2030
|  | CS-09800 | Renewable Energy Systems Limited | Killoch BESS 275kV substation | Killoch A1 SS | 0 | 30/09/2030
|  | CS-09799 | Renewable Energy Systems Limited | Killoch BESS 275kV substation | Killoch A1 OHL | 0 | 30/09/2030
|  | CS-09801 | Renewable Energy Systems Limited | Killoch BESS 275kV substation | SPT-RI-284 SS | 0 | 30/09/2030
Kilmarnock BESS | PRO-001836 | CS-05442 | KILMARNOCK FLEXPOWER LTD | Kilmarnock Town 275/33kV Substation | kilmarnock BESS | Installation of a new 400kV double busbar GIS bay at Kilmarnock South 400kV substation including a 400kV circuit breaker and associated equipment. Installation of a new 400kV cable circuit (approx. 2.6km) between Kilmarnock South 400kV substation and the User’s site. Installation of a 400kV line disconnector at the User’s site. | 31/07/2025
|  | CS-05443 | KILMARNOCK FLEXPOWER LTD | Kilmarnock Town 275/33kV Substation | SPT-RI-1854 | At Kilmarnock South 400kV GIS substation install a bus coupler to run the substation in double busbar arrangements. (SPT-RI-1854. Protection and control modifications as required. Associated civil works. Miscellaneous and minor works | 31/07/2025
|  | CS-05444 | KILMARNOCK FLEXPOWER LTD | Kilmarnock Town 275/33kV Substation | SPT-RI-2249 | Kilmarnock South 275kV Fault Level Uprating - To allow the connection of a battery storage connection at Kilmarnock South 400kV substation, the short circuit rating of Kilmarnock South 275kV substation equipment needs to be increased from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 31/07/2025
Kilmarnock South Battery Storage | PRO-001809 | CS-05401 | WEAVER POWER LIMITED | Kilmarnock South GSP | SPT-RI-1854 | At Kilmarnock South 400kV GIS substation install a bus coupler to run the substation in double busbar arrangements. (SPT-RI-1854. Protection and control modifications as required. Associated civil works. Miscellaneous and minor works | 30/04/2027
|  | CS-05402 | WEAVER POWER LIMITED | Kilmarnock South GSP | SPT-RI-2249 | Kilmarnock South 275kV Fault Level Uprating - To allow the connection of a battery storage connection at Kilmarnock South 400kV substation, the short circuit rating of Kilmarnock South 275kV substation equipment needs to be increased from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 30/04/2027
Kilmux Farm | PRO-001195 | CS-09763 | SP Distribution plc | Leven GSP | SPT-RI-3384 | Glenniston to Westfield 132kV Circuit Uprating | 31/05/2032
|  | CS-09765 | SP Distribution plc | Leven GSP | SPT-RI-3420 | Redhouse toWestfield 132kV Circuit Uprating (AG Route) | 31/05/2032
|  | CS-09764 | SP Distribution plc | Leven GSP | SPT-RI-3385 | Glenniston 132kV Substation Works | 31/05/2032
Kincardine Battery Storage Facility | PRO-000856 | CS-04309 | SPECTRUMRESERVE LTD | Fife Grid Services Facility 275kV Substation | SPT-RI-1745 | Kincardine to Fife Grid 275kV Switchgear and Cable Works - To facilitate the connection of contracted generation from the Relevant Transmission Licensee’s Fife Grid Services Facility 275kV substation to Kincardine 275kV substation, it is proposed to install a new 275kV busbar and associated 275kV disconnectors and approximately 0.9km of 275kV underground cable circuit to Kincardine 275kV substation. At Kincardine 275kV substation, install a new 275kV GIS switchgear and associated disconnectors and one 275kV line isolator. | 12/04/2024
Kincardine Energy Storage Facility | PRO-001653 | CS-04466 | ENERGYGRIDPOWER3 LTD | Fife Grid Services Facility 275kV Substation | SPT-RI-1745 | Kincardine to Fife Grid 275kV Switchgear and Cable Works - To facilitate the connection of contracted generation from the Relevant Transmission Licensee’s Fife Grid Services Facility 275kV substation to Kincardine 275kV substation, it is proposed to install a new 275kV busbar and associated 275kV disconnectors and approximately 0.9km of 275kV underground cable circuit to Kincardine 275kV substation. At Kincardine 275kV substation, install a new 275kV GIS switchgear and associated disconnectors and one 275kV line isolator. | 12/04/2024
Kingfisher Farm | PRO-002555 | CS-08651 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 102208-204431 | Uprating of OHL double cct from 2TW110 - 2TW169 and 4YR1 - 4YR40 which is part of the current Norton-Osbaldwick double circuit but will become the new Osbaldwick-Overton-Thormanby circuit | 02/06/2036
|  | CS-08648 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 02/06/2036
|  | CS-08650 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 102080-204268 | Replant of Overton 275kV substation with higher rated equipment. | 02/06/2036
|  | CS-08649 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 031380-031380 | Hotwire the 4x400mm2 sections of the Lackenby – Thornton 400kV 1 and 2 circuits for operation at 75°C. | 02/06/2036
|  | CS-08636 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 02/06/2036
|  | CS-08634 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 02/06/2036
|  | CS-08640 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101511-202976 | Hotwire the 2x400mm2 sections of the Elland – Stalybridge circuit 275kV to an operating temperature of 75°C | 02/06/2036
|  | CS-08641 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm2 sections with 2x620mm2 GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 02/06/2036
|  | CS-08633 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 100455-201020 | At Keadby 400kV substation: Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby –Thorpe Marsh 400kV circuit | 02/06/2036
|  | CS-08638 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101509-202974 | Replace the existing Ferrybridge C 275kV substation, new substation to be established as an offline build with phased circuit transfers. | 02/06/2036
|  | CS-08639 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm2 sections of the circuits with 2x570 mm2 strung to an operating temperature of 75°C. Hotwire the 2x570 mm2 sections to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A. | 02/06/2036
|  | CS-08635 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 02/06/2036
|  | CS-08642 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101610-203236 | Reconductor the 2x500mm2 sections of the Carrington – Kearsley circuit with 2x620mm2 GAP conductor | 02/06/2036
|  | CS-08644 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101627-203263 | Cable uprate on the Kearsley - Whitegate 275 kV circuit 1 to achieve a pre fault summer rating of 400 MVA | 02/06/2036
|  | CS-08637 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101504-202965 | Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit to provide a post-fault winter rating of 3820MVA: • Reconductor the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. • At Keadby 400kV substation, replace the X1005 feeder bay for the Drax – Keadby – Thorpe Marsh circuit. Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit to provide a post-fault winter rating of 3820MVA: • Reconductor the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. • At Keadby 400kV substation, replace the X1005 feeder bay for the Drax – Keadby – Thorpe Marsh circuit. | 02/06/2036
|  | CS-08629 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 033513-033513 | Uprate Keadby-West Burton 2 (4TM 1-81) with 3420MVA post-fault rating during Winter | 02/06/2036
|  | CS-08631 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 100171-200449 | Uprate the Thorpe Marsh – West Melton Circuit 2 to achieve a post fault summer rating of 1000MVA. | 02/06/2036
|  | CS-08630 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 02/06/2036
|  | CS-08643 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101616-203249 | Reconductor 400kV Drakelow to Hams Hall line from Rubus 500sqmm to Rubus 500sqmm at 90deg C to have summer pre fault rating of 1660MVA | 02/06/2036
|  | CS-08627 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101899-204096 | Replace circuit breakers L85 and L45 at Monk Fryston 275kV with 40kA-rated circuit breaker tested to the appropriate X/R ratio | 02/06/2036
|  | CS-08626 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101508-202973 | Replace circuit breakers S10 and L25 at Monk Fryston 275kV substation with a 40kA-rated circuit breaker tested to the appropriate X/R ratio | 02/06/2036
|  | CS-08628 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 02/06/2036
|  | CS-08623 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 102462-205035 | Make provision for connection of generator bay at Monk Fryston 275kV substation | 02/06/2036
|  | CS-08632 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 02/06/2036
|  | CS-08647 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101855-203810 | Reconductoring of Macclesfield to Stalybridge line (A23A) with 1590MVA pre-fault rating during Summer. | 02/06/2036
|  | CS-08646 | CSWE 6 LIMITED | Monk Fryston 275kV Substation | 101807-203697 | New EDN2 Chesterfield – Ratcliffe-on-Soar 400kV double circuit | 02/06/2036
Kinmuck PV and BESS Station | PRO-001700 | CS-04336 | IGP SOLAR 24 LIMITED | Peterhead GSP | Kinmuck PV & BESS H1 Works | Installation of 2 x 275kV disconnectors at the User’s site, on the Network side of the circuit breaker. | 31/05/2027
|  | CS-04337 | IGP SOLAR 24 LIMITED | Peterhead GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/05/2027
|  | CS-04338 | IGP SOLAR 24 LIMITED | Peterhead GSP | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/05/2027
|  | CS-04339 | IGP SOLAR 24 LIMITED | Peterhead GSP | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/05/2027
|  | CS-04340 | IGP SOLAR 24 LIMITED | Peterhead GSP | SHET-RI-025d | North East Reinforcement | 31/05/2027
|  | CS-04341 | IGP SOLAR 24 LIMITED | Peterhead GSP | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/05/2027
|  | CS-04342 | IGP SOLAR 24 LIMITED | Peterhead GSP | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/05/2027
|  | CS-04343 | IGP SOLAR 24 LIMITED | Peterhead GSP | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/05/2027
|  | CS-04344 | IGP SOLAR 24 LIMITED | Peterhead GSP | SHET-RI-155 | Peterhead – Persley Tee 275kV Line Works – Overhead line works to bring the VP 275kV overhead line circuit to ground, including any required tower modifications. Design and installation of one 275kV bus bar including a circuit breaker with four 275kV disconnectors and associated protection and control equipment. | 31/05/2027
Kintore BESS | PRO-002518 | CS-09804 | Conrad Energy (Developments) II Limited | Kintore GSP | SHET-RI-245 | Kintore – Craigiebuckler/Tarland Tee Point Upgrade – Kintore to Craigiebuckler-Tarland Tee Point Overhead line 132kV Upgrade | 31/10/2031
|  | CS-09805 | Conrad Energy (Developments) II Limited | Kintore GSP | Kintore BESS | 1. Installation of an intertrip scheme based on unavailability, due to planned or unplanned outage conditions, of either of the Kintore to Craigiebuckler 132kV XCN/XCS circuits to prevent an overload on the local 132kV network. 2. A loss of mains scheme will be configured at Kintore GSP as requested by the host Distribution Network Operator. 3. Installation of a new 132kV double busbar switch bay at Kintore 132kV substation. The switch bay will include 2x 132kV busbar selection switches, 1x 132kV circuit breaker and 1x 132kV line disconnector. 4. Installation of a 120MVA 132/33kV grid transformer, a 33kV metering circuit breaker and a 33kV disconnector on a suitable level platform at the new Kintore 2 132/33kV GSP substation compound. | 31/10/2031
Kintradwell Energy Park | PRO-001377 | CS-06354 | Renewable Energy Systems Limited | Kintradwell 132/33kV Substation | Kintradwell H1 Works | Remove an existing 132kV steel lattice tower on the Loch Buidhe - Spittal 132kV double circuit OHL and replace with a new 132 kV steel lattice tower to facilitate a 132kV tee-off connection point for the Kintradwell 132/33kV substation. | 30/06/2027
|  | CS-06355 | Renewable Energy Systems Limited | Kintradwell 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 30/06/2027
|  | CS-06356 | Renewable Energy Systems Limited | Kintradwell 132/33kV Substation | no Scheme | 0 | 30/06/2027
|  | CS-06357 | Renewable Energy Systems Limited | Kintradwell 132/33kV Substation |  | FALSE | 30/06/2027
|  | CS-06358 | Renewable Energy Systems Limited | Kintradwell 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 30/06/2027
|  | CS-06353 | Renewable Energy Systems Limited | Kintradwell 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 30/06/2027
Kirkby | PRO-001084 | CS-04482 | HD001KIR LTD | Kirkby 275kV Substation | 100506-201132 | 1. Install a tertiary cable box or bushings on SGT1A 2. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer at the 13kV side. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 30/09/2025
Kirkby (Tertiary) | PRO-001083 | CS-05214 | PIVOTED POWER LLP | Kirkby 275kV Substation | 100763-201870 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to Disconnecting Circuit Breaker (DCB). 3. Install Disconnecting Circuit Breaker (DCB) at the 13kV side connecting tertiary to connection assets for Users connection. | 31/10/2025
Kirkby Green Energy Centre | PRO-001869 | CS-07138 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 101697-203380 | Extend the Main and Reserve Busbar 2 to make provision for connection of generator bay (User Works). | 30/10/2028
|  | CS-07139 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 30/10/2028
|  | CS-07140 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 101697-203383 | Hotwire the 2x400mm2 conductor on the Bredbury – South Manchester circuits | 30/10/2028
|  | CS-07141 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with new 2750MVA unit. | 30/10/2028
|  | CS-07142 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor | 30/10/2028
|  | CS-07143 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 101284-202534 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 400kV circuits and the Cellarhead – Macclesfield and Cellarhead – Daines 400kV circuits | 30/10/2028
|  | CS-07144 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor | 30/10/2028
|  | CS-07145 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x780mm2 conductor or equivalent and uprating of the cable section of the circuit | 30/10/2028
|  | CS-07146 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 101468-202908 | Reconductor the Daines – Macclesfield 400kV with 2x780mm2 conductor | 30/10/2028
|  | CS-07147 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm2 conductor | 30/10/2028
|  | CS-07148 | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation | 100425-200971 | Reconductor the Feckenham – Ironbridge 400kV circuit with 2x620mm2 conductor | 30/10/2028
Kirk Hill | PRO-000320 | CS-07394 | KIRK HILL WIND FARM LIMITED | Maybole GSP | SPT-RI-224 | At Coylton substation, the existing SGT1 and SGT2 275/132kV 120MVA transformers will be replaced (on line) with 240MVA units. | 15/12/2023
|  | CS-07395 | KIRK HILL WIND FARM LIMITED | Maybole GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 15/12/2023
|  | CS-05868 | KIRK HILL WIND FARM LIMITED | Maybole GSP | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 15/12/2023
|  | CS-05869 | KIRK HILL WIND FARM LIMITED | Maybole GSP | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 15/12/2023
Kirklands Farm BESS | PRO-003499 | CS-09478 | GPC Battery Ltd | Westfield GSP | SHET-RI-185 | Kintore - Tealing 400kV circuit – Establish a new 400 kV double circuit overhead line between Kintore 400 kV substation and Tealing 400 kV substation. | 31/10/2031
|  | CS-09479 | GPC Battery Ltd | Westfield GSP | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 31/10/2031
|  | CS-09477 | GPC Battery Ltd | Westfield GSP | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 31/10/2031
|  | CS-09476 | GPC Battery Ltd | Westfield GSP | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 31/10/2031
Kirkton Solar PV | PRO-001262 | CS-05870 | EEB 19 LIMITED | Peterhead Grange GSP | Kirkton enabling works item 1 | At Peterhead Grange 132/33kV GSP remove the 2 existing 45 mva transformers and install 2 new 90 mva transformers and ancillary equipment. The transformers will be enclosed within new acoustic enclosures. The works will include metering, protection and control equipment. The Transfromers will be installed within the existing substation location and cabled to the existing 33 kV switchboard | 31/03/2024
Knockcronal Wind Farm | PRO-001801 | CS-07029 | Knockcronal Wind Farm Limited | Knockcronal Wind Farm 33kV Substation | Knockcronal Wind Farm | 1. At Carrick collector substation, installation of one 275kV line isolator connecting onto the Carrick 275kV busbar. Provision of communications, alarms, indications and metering from the User site | 30/10/2028
|  | CS-07030 | Knockcronal Wind Farm Limited | Knockcronal Wind Farm 33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/10/2028
|  | CS-07031 | Knockcronal Wind Farm Limited | Knockcronal Wind Farm 33kV Substation | SPT-RI-293 | Carrick 275kV Substation - A new 275kV substation will be installed on the Coylton-Mark Hill 275kV circuit (YY route) approximately 25km northeast of Mark Hill substation. The YY route will be turned in to the new substation with a 275kV circuit breaker on each circuit. The new circuit breakers will maintain the single-phase high-speed auto reclose capability which currently exists on the YY route. (SPT-RI-293) | 30/10/2028
Knockkippen Energy Park | PRO-001826 | CS-05440 | Naturalis Energy Developments Ltd | Ayr 275/33 kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/09/2026
|  | CS-05441 | Naturalis Energy Developments Ltd | Ayr 275/33 kV Substation |  | FALSE | 30/09/2026
Knockodhar Wind Farm | PRO-000483 | CS-06252 | REG KNOCKODHAR LIMITED | Mark Hill 275kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/04/2028
|  | CS-06253 | REG KNOCKODHAR LIMITED | Mark Hill 275kV Substation | SPT-RI-282 | Markhill SGT4 | 30/04/2028
|  | CS-06254 | REG KNOCKODHAR LIMITED | Mark Hill 275kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/04/2028
|  | CS-05871 | REG KNOCKODHAR LIMITED | Mark Hill 275kV Substation | Knockodhar Enabling Works items 1-4 | 1. At Mark Hill substation install a new 132kV switch bay and associated equipment and apparatus. 2. Installation of a 132kV cable system from Mark Hill 132kV substation to an appropriate location where the 132kV wood pole overhead line will be constructed. 3. Installation of approximately 3km of 132kV wood pole overhead line between Mark Hill and Knockodhar 132kV Substation. 4. At Knockodhar Substation, one 132kV line isolator will be installed. 9. Provision of a Control Scheme to manage the network in South West Scotland. Detailed information shall be provided by The Company in the detailed design phase. | 30/04/2028
Kulizumboo Interconnector | PRO-001290 | CS-05872 | KULIZUMBOO LIMITED | Canterbury North 400kV Substation | 31867 | Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent. | 31/10/2027
|  | CS-05873 | KULIZUMBOO LIMITED | Canterbury North 400kV Substation | 100250-200637 | Provision of 1 bay for Kulizumboo interconnector at Canterbury 400 kV GIS Substation. Extension of Sellindge 400 kV OTS to Kulizumboo connection. | 31/10/2027
|  | CS-05874 | KULIZUMBOO LIMITED | Canterbury North 400kV Substation | 020865-020865 | Kemsley to Longfield Tee 400 kV circuit - Reconductor to achieve a 2800MVA post-fault rating. Littlebrook to Longfield Tee 400 kV circuit - Reconductor to achieve a 2800MVA post-fault rating. | 31/10/2027
|  | CS-05875 | KULIZUMBOO LIMITED | Canterbury North 400kV Substation | 031339-031339 | South Coast STATCOMS and MSCs. | 31/10/2027
KXP Alpha One | PRO-002348 | CS-07885 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 100424-200970 | Uprate the Bramley - Melksham 1 & 2 400kV circuits (81.6km, 2 x 400mm2 zebra conductor at 50oC on L2 towers with summer prefault rating of 931MVA) by reconductoring with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 24/10/2036
|  | CS-07887 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 24/10/2036
|  | CS-07877 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 102136-204339 | Uprate the Mannington – Nursling section (NASP Code: A84D) of the Lovedean – Mannington - Nursling circuit to summer pre fault rating of 3160MVA Reconductor to Triple Araucaria and hotwire to 90°C Note: Under scheme 101387 the Lovedean – Mannington –Nursling circuit will become two circuits Lovedean – Nursling and Mannington – Nursling | 24/10/2036
|  | CS-07881 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 24/10/2036
|  | CS-07883 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 101498-202953 | Uprate the double circuits between the Exeter, Axminster & Chickerell substations by reconductoring the 4 x 400mm2 Zebra conductor sections with 3 x 700mm2 Araucaria conductor at 75°C and hotwiring the existing 3 x 700mm2 Araucaria conductor sections at 50°C to 75°C to achieve a pre-fault summer rating of 2790MVA. | 24/10/2036
|  | CS-07886 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 24/10/2036
|  | CS-07888 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 101033-202065 | Installation of stability OTS for the South West, driven by multiple generation customers | 24/10/2036
|  | CS-07878 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 102127-204336 | Uprate the Lovedean - Nursling section (NASP Code: A84E) of the Lovedean – Mannington – Nursling circuit to summer pre fault rating of 2570MVA Reconductor to Triple Araucaria and hotwire to 75°C. Note: Under scheme 101387 the Lovedean - Mannington - Nursling circuit will become two circuits: Lovedean - Nursling and Mannington - Nursling | 24/10/2036
|  | CS-07882 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 101833-203761 | Uprate the Chickerell - Mannington double circuit (NASP Code: A851 and A830) by hotwiring the existing 3 x 700mm2 Araucaria conductor at 50°C to 90°C to achieve a pre-fault summer rating of 3160MVA | 24/10/2036
|  | CS-07884 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 101562-203112 | Reconductor Taunton - Exeter 1 & 2 400kV circuits (2 x 500mm2 Rubus at 75oC) with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MV | 24/10/2036
|  | CS-07880 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 24/10/2036
|  | CS-07879 | KXP ALPHA I LIMITED | Fawley 132kV Substation | 102135-204339 | Uprate the Fawley – Mannington circuit (NASP Code: A837) to summer pre fault rating of 3160MVA Reconductor to Triple Araucaria and hotwire to 90°C Note: Under scheme 101387 the Fawley – Mannington circuit will become Fawley – Nursling and Nursling – Mannington. | 24/10/2036
KXP Alpha Three | PRO-002351 | CS-07876 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 101033-202065 | Installation of stability OTS for the South West, driven by multiple generation customers | 24/10/2036
|  | CS-07871 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 101498-202953 | Uprate the double circuits between the Exeter, Axminster & Chickerell substations by reconductoring the 4 x 400mm2 Zebra conductor sections with 3 x 700mm2 Araucaria conductor at 75°C and hotwiring the existing 3 x 700mm2 Araucaria conductor sections at 50°C to 75°C to achieve a pre-fault summer rating of 2790MVA. | 24/10/2036
|  | CS-07868 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 24/10/2036
|  | CS-07869 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 24/10/2036
|  | CS-07872 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 101562-203112 | Reconductor Taunton - Exeter 1 & 2 400kV circuits (2 x 500mm2 Rubus at 75oC) with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MV | 24/10/2036
|  | CS-07873 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 100424-200970 | Uprate the Bramley - Melksham 1 & 2 400kV circuits (81.6km, 2 x 400mm2 zebra conductor at 50oC on L2 towers with summer prefault rating of 931MVA) by reconductoring with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 24/10/2036
|  | CS-07867 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 102135-204339 | Uprate the Fawley – Mannington circuit (NASP Code: A837) to summer pre fault rating of 3160MVA Reconductor to Triple Araucaria and hotwire to 90°C Note: Under scheme 101387 the Fawley – Mannington circuit will become Fawley – Nursling and Nursling – Mannington. | 24/10/2036
|  | CS-07875 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 24/10/2036
|  | CS-07874 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 24/10/2036
|  | CS-07870 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 101833-203761 | Uprate the Chickerell - Mannington double circuit (NASP Code: A851 and A830) by hotwiring the existing 3 x 700mm2 Araucaria conductor at 50°C to 90°C to achieve a pre-fault summer rating of 3160MVA | 24/10/2036
|  | CS-07866 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 102127-204336 | Uprate the Lovedean - Nursling section (NASP Code: A84E) of the Lovedean – Mannington – Nursling circuit to summer pre fault rating of 2570MVA Reconductor to Triple Araucaria and hotwire to 75°C. Note: Under scheme 101387 the Lovedean - Mannington - Nursling circuit will become two circuits: Lovedean - Nursling and Mannington - Nursling | 24/10/2036
|  | CS-07865 | KXP ALPHA III LIMITED | Fawley 132kV Substation | 102136-204339 | Uprate the Mannington – Nursling section (NASP Code: A84D) of the Lovedean – Mannington - Nursling circuit to summer pre fault rating of 3160MVA Reconductor to Triple Araucaria and hotwire to 90°C Note: Under scheme 101387 the Lovedean – Mannington –Nursling circuit will become two circuits Lovedean – Nursling and Mannington – Nursling | 24/10/2036
KXP Alpha Two | PRO-002349 | CS-08352 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 100424-200970 | Uprate the Bramley - Melksham 1 & 2 400kV circuits (81.6km, 2 x 400mm2 zebra conductor at 50oC on L2 towers with summer prefault rating of 931MVA) by reconductoring with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 24/10/2036
|  | CS-08350 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 101498-202953 | Uprate the double circuits between the Exeter, Axminster & Chickerell substations by reconductoring the 4 x 400mm2 Zebra conductor sections with 3 x 700mm2 Araucaria conductor at 75°C and hotwiring the existing 3 x 700mm2 Araucaria conductor sections at 50°C to 75°C to achieve a pre-fault summer rating of 2790MVA. | 24/10/2036
|  | CS-08354 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 24/10/2036
|  | CS-08348 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 24/10/2036
|  | CS-08349 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 101833-203761 | Uprate the Chickerell - Mannington double circuit (NASP Code: A851 and A830) by hotwiring the existing 3 x 700mm2 Araucaria conductor at 50°C to 90°C to achieve a pre-fault summer rating of 3160MVA | 24/10/2036
|  | CS-08346 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 102135-204339 | Uprate the Fawley – Mannington circuit (NASP Code: A837) to summer pre fault rating of 3160MVA Reconductor to Triple Araucaria and hotwire to 90°C Note: Under scheme 101387 the Fawley – Mannington circuit will become Fawley – Nursling and Nursling – Mannington. | 24/10/2036
|  | CS-08345 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 102127-204336 | Uprate the Lovedean - Nursling section (NASP Code: A84E) of the Lovedean – Mannington – Nursling circuit to summer pre fault rating of 2570MVA Reconductor to Triple Araucaria and hotwire to 75°C. Note: Under scheme 101387 the Lovedean - Mannington - Nursling circuit will become two circuits: Lovedean - Nursling and Mannington - Nursling | 24/10/2036
|  | CS-08347 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 24/10/2036
|  | CS-08351 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 101562-203112 | Reconductor Taunton - Exeter circuits 1 and 2 to achieve 2680MVA pre-fault summer rating. | 24/10/2036
|  | CS-08355 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 101033-202065 | Installation of stability OTS for the South West, driven by multiple generation customers | 24/10/2036
|  | CS-08344 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 102136-204339 | Uprate the Mannington – Nursling section (NASP Code: A84D) of the Lovedean – Mannington - Nursling circuit to summer pre fault rating of 3160MVA Reconductor to Triple Araucaria and hotwire to 90°C Note: Under scheme 101387 the Lovedean – Mannington –Nursling circuit will become two circuits Lovedean – Nursling and Mannington – Nursling | 24/10/2036
|  | CS-08353 | KXP ALPHA II LIMITED | Fawley 132kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 24/10/2036
L48 BESS Glen App | PRO-003058 | CS-09432 | Lower 48 Energy BESS Limited | L48 BESS Glen App | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 31/10/2028
Lairg II Wind Farm | PRO-001434 | CS-04468 | ENERGYFARM UK LAIRG LLP | Lairg GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2026
|  | CS-04470 | ENERGYFARM UK LAIRG LLP | Lairg GSP | Lairg II H1 Works | Construction of a Tee off connection to the Shin 132kV OHL constructing 1.6km of 132kV trident line to the Lairg II windfarm substation | 31/10/2026
|  | CS-06679 | ENERGYFARM UK LAIRG LLP | Lairg GSP | SHET-RI-052 - Lairg – Loch Buidhe 132kV Reinforcement | Establish a new 132kV double busbar at Lairg (Dalchork substation) and construct approximately 17km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. | 31/10/2026
Lakeside Energy Drax | PRO-001522 | CS-06826 | LAKESIDE ENERGY STORAGE LIMITED | Drax GSP | 101242-202471 | 1. Extend Main and Reserve busbar 2 at Drax 132kV substation. 2. . Carry out a civil infrastructure survey to evaluate the bay infrastructure ratings of the bus coupler and bus section circuit breakers (120 and 130) at Drax 132 kV substation. Dependant on the outcome, reinforcement of the bay infrastructure may be required. | 29/03/2024
|  | CS-06827 | LAKESIDE ENERGY STORAGE LIMITED | Drax GSP | 100171-200448/ 100171-200449 | Uprate the Thorpe Marsh – West Melton 1 275kV circuit by reconductoring the circuit 2x500mm conductor operating at 90 degrees and uprating the cable sections. | 29/03/2024
Laleham | PRO-001063 | CS-05271 | PIVOTED POWER LLP | Laleham 275kV Substation | 100770-200764 | 1. Extend the existing Laleham 132kV busbar to accommodate a new GIS generator bay to enable connection of User plant. 2. Substation control modification and busbar protection. | 01/11/2025
Lamford Hill | PRO-001481 | CS-06658 | Benbrack Wind Farm Limited | Lamford Hill 132kV/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/10/2026
|  | CS-06659 | Benbrack Wind Farm Limited | Lamford Hill 132kV/33kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 30/10/2026
|  | CS-06660 | Benbrack Wind Farm Limited | Lamford Hill 132kV/33kV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 30/10/2026
|  | CS-06661 | Benbrack Wind Farm Limited | Lamford Hill 132kV/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 30/10/2026
|  | CS-06662 | Benbrack Wind Farm Limited | Lamford Hill 132kV/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/10/2026
|  | CS-06663 | Benbrack Wind Farm Limited | Lamford Hill 132kV/33kV Substation | SPT-RI-1851 | Benbrack 132kV overhead line and substation works - A new collector substation will be established at Benbrack wind farm with a 132/33kV 120MVA transformer. An overhead line (Poplar 124MVA) will tee into the New Cumnock – Blackcraig – Glenlee 132kV circuit. This circuit will provide the ratings as outlined below: Pre-fault continuous: Winter- 615A, 140MVA; Autumn- 590A, 134MVA; Summer- 540A, 124MVA Post-fault continuous: Winter- 730A, 167MVA; Autumn- 700A, 160MVA; Summer- 645A, 147MVA | 30/10/2026
Lanarkshire BESS | PRO-002183 | CS-08260 | CARLTON POWER LIMITED | Strathaven 400kV | SPT-RI-2537 | Strathaven 400kV Compound Extension | 30/04/2027
|  | CS-08261 | CARLTON POWER LIMITED | Strathaven 400kV | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 30/04/2027
Land at Rothienorman | PRO-002073 | CS-07567 | ANESCO LIMITED | Rothienorman GSP | Loss of Mains - LoR | A loss of mains scheme will also be configured at Rothienorman GSP as requested by the host Distribution Network Operator | 31/10/2024
|  | CS-07565 | ANESCO LIMITED | Rothienorman GSP | Intertrip Scheme - Land at Rothienorman | This scheme requires an intertrip for the loss of one of the grid transformers at Rothienorman 400/33kV GSP. These signals will be provided to the Host Distribution Network Operator to trip the User via a separate relay panel within the 33kV Switch room from the signals described below | 31/10/2024
|  | CS-07566 | ANESCO LIMITED | Rothienorman GSP | Protection Settings - LoR | Modification to the existing LV Directional Overcurrent (DOC) protection settings at Rothienorman 400/33kV Substation will also be required | 31/10/2024
Landulph | PRO-001131 | CS-05272 | PIVOTED POWER LLP | Landulph 400kV Substation | NGET-Rl-100278-200771 (Infra) | 1. Install earthing transformer on 13 kV tertiary connection 2. Install 13kV disconnector connecting tertiary to connection assets for Users connection 3. Works required to connect the User to the South West Operational Tripping Scheme (OTS), as described in Appendix F3 | 31/10/2022
|  | CS-05273 | PIVOTED POWER LLP | Landulph 400kV Substation | NGET RI-33539 | 1. Hotwiring of the Hinkley Point — Melksham 1 and 2 circuits to increase their thermal rating | 31/10/2022
|  | CS-05274 | PIVOTED POWER LLP | Landulph 400kV Substation | NGET-Rl-31671-2 | 2. Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. | 31/10/2022
|  | CS-05275 | PIVOTED POWER LLP | Landulph 400kV Substation | NGET-Rl-31671-I | 3. Re-conductor the Bramley - Fleet OHL circuits to increase capacity | 31/10/2022
|  | CS-05276 | PIVOTED POWER LLP | Landulph 400kV Substation | NGET-Rl-30752 | 4. Creation of a new South West Operational Tripping Scheme (OTS) at Taunton | 31/10/2022
Lan Fawr Energy Park | PRO-001609 | CS-06828 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 11/09/2028
|  | CS-06829 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 11/09/2028
|  | CS-06830 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 11/09/2028
|  | CS-06831 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 11/09/2028
|  | CS-06832 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 033769-033769 | Reconductor the Exeter – Hinkley Point – Taunton 400kV circuits to achieve a 2787MVA pre-fault summer rating. | 11/09/2028
|  | CS-06833 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 100424-200970 | Reconductor the Bramley – Melksham 400kV circuits 1 and 2 to achieve a pre-fault summer rating of 1581MVA. | 11/09/2028
|  | CS-06834 | LAN FAWR ENERGY PARK LIMITED | Pont Abraham GSP | 101052-202110 | Install power flow control devices along the Imperial Park – Melksham 400kV circuit | 11/09/2028
Langage 400 | PRO-002192 | CS-08046 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 19/12/2036
|  | CS-08055 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101501-202958 | Reconductor the Hinkley point - Sandford CSE circuit 2 (only ZG section) in order to achieve a summer post fault rating of 2850MVA. | 19/12/2036
|  | CS-08043 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 100480-201051 | Uprate the cable section of the Seabank -Whitson section of the three-ended Seabank -Whitson - Cilfynydd circuit to a pre-fault rating of 1800MVA | 19/12/2036
|  | CS-08054 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101500-202955 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 1 in order to achieve a summer post fault rating of 2850MVA | 19/12/2036
|  | CS-08051 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 19/12/2036
|  | CS-08056 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101501-202957 | Reconductor the Hinkley point - Sandford CSE circuit 1 (only ZG section) in order to achieve a summer post fault rating of 2850MVA | 19/12/2036
|  | CS-08049 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 131499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer pre fault of 2550MVA and a post fault of 2900MVA | 19/12/2036
|  | CS-08047 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 19/12/2036
|  | CS-08057 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101833-203761 | Uprate the Chickerel - Mannington double circuit (NASP Code: A851 and A830) to summer pre fault rating of 2200MVA. | 19/12/2036
|  | CS-08052 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 19/12/2036
|  | CS-08048 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101498-202953 | Uprate the double circuit between the Exeter - Axminster – Chickerell substations, to achieve at least a post fault summer rating of 2420MVA | 19/12/2036
|  | CS-08045 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 19/12/2036
|  | CS-08058 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101497-202952 | Reconductor the single circuit between Melksham - Seabank (route 4YX and 2VL) in order to achieve a pre fault summer rating of 2500MVA and post fault summer rating of 3210MVA. | 19/12/2036
|  | CS-08042 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 102066-204240 | At Langage 400kV Substation: 1. Extension of substation building. 2. Extension of GIS substation to accommodate the installation of one generator bay by the User. 3. Local works to integrate the User into South West Operational Tripping Scheme. | 19/12/2036
|  | CS-08044 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 19/12/2036
|  | CS-08053 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101500-202956 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 2 in order to achieve a summer post fault rating of 2850MVA | 19/12/2036
|  | CS-08050 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 101620-203254 | Reconductoring of the Landulph – Indian Queens 2 circuit to achieve a post-fault Summer rating of 2300MVA. | 19/12/2036
Langbank Solar and BESS | PRO-003569 | CS-09516 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-2268 | BZ Route No.2 Uprating - Generation connections into the Devol Moor – Erskine 132kV circuit have identified the need to uprate the No.2 side of BZ Route between Erskine and Braehead Park. It has been noted through system studies that an outage on the Erskine to Braehead circuit (BZ No.1) could result in overloads on the No.2 side. In order to alleviate these overloads, it is required to uprate the OHL and cable sections of the circuit. It is proposed to install 1x 280mm2 AAAC “Sycamore” conductor on the OHL sections operating at 75℃ with similarly rated cable sections | 29/10/2027
|  | CS-09518 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-2311 | G Route Modernisation - The existing G Route 132kV Devol Moor to Erskine overhead line (OHL) is predominantly situated close to the coastline and is approximately 16km in length supported on 50 lattice towers (PL-1 design) built in 1929 as a single circuit. The majority of the conductors (175mm2 Lynx ACSR) and earthwire (70mm2 Horse ASCR) were replaced in 1960. The route has been identified as at end of life and a result its replacement with a new 132kV OHL circuit is proposed. The replacement scheme would entail the construction of a new 132kV single circuit wood pole overhead line being Devol Moor substation and Erskine substation. The approximate length of the circuit would be 17km and shall comprise of 250mm2 Sycamore AAAC and OPPC Sycamore equivalent phase wire (middle phase) incorporating a fibre optic cable for communications and protection purposes. They will have the overall effect on reducing the visual impact along the route and overcome environmental and landowner issues that currently prevail on the existing G Route | 29/10/2027
|  | CS-09517 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-3285 | Devol Moor-Erskine-Braehead Park 132kV LMS – BZ Route Monitoring Upgrade –An extension to the existing Devol Moor-Erskine-Braehead Park Load Management Scheme (LMS) is required to manage connections to prevent thermal overloads on the Erskine-Braehead Park Circuit. A new monitoring outstation will be installed at Braehead Park to monitor the loading on the ErskineBraehead Park 132kV circuit. The measurements will be communicated to Devol Moor 132kV where the IED associated with the existing Devol Moor-Erskine LMS scheme (established under TORI243) will relay trip signals to relevant non-firm connections as appropriate. | 29/10/2027
|  | CS-09515 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-243 - Devol Moor-Erskine-Braehead Park Circuit LMS | A Load Management Scheme (LMS) is required to manage connections in the Neilston – Devol Moor 132 kV group to prevent overloads on the Devol Moor-Erskine-Braehead Park Circuit. The overload will be removed by the LMS tripping the appropriate non-firm connections. | 29/10/2027
|  | CS-09519 | UK RENFREWSHIRE 1 LTD | Devol Moor 132kV Substation | SPT-RI-3263 | Erskine 132kV Bus Section Circuit Breaker | 29/10/2027
Langlands Business Park | PRO-003476 | CS-09537 | SP Distribution plc | East Kilbride South GSP | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 30/10/2027
|  | CS-09536 | SP Distribution plc | East Kilbride South GSP | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 30/10/2027
|  | CS-09535 | SP Distribution plc | East Kilbride South GSP | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 30/10/2027
Lapwing Fen II | PRO-001995 | CS-07458 | Eclipse Power Networks Limited | Walpole 132kV Substation | 100075 - 200225 | 1. Extension of the Gas Insulated Switchgear (GIS) busbars at Walpole 132kV substation. 2. Provision for sufficient space within the GIS hall to allow the User to install a feeder bay at Walpole 132kV substation 3.Substation Control System database changes and the Relevant Transmission Licensee’s operations commissioning resource. | 30/06/2025
Larbrax Wind Farm | PRO-000781 | CS-09749 | SP Distribution plc | Glenluce GSP | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 02/11/2029
|  | CS-09745 | SP Distribution plc | Glenluce GSP | SPT-RI-2885 | BT Route 132kV Uprating | 02/11/2029
|  | CS-09747 | SP Distribution plc | Glenluce GSP | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 02/11/2029
|  | CS-09744 | SP Distribution plc | Glenluce GSP | SPT-RI-3223 | BT Route No.2 Circuit 132kV Uprating | 02/11/2029
|  | CS-09751 | SP Distribution plc | Glenluce GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 02/11/2029
|  | CS-09746 | SP Distribution plc | Glenluce GSP | SPT-RI-3303 | Tee into Newton Stewart-Glenluce 1(2) 132kV Circuits | 02/11/2029
|  | CS-09748 | SP Distribution plc | Glenluce GSP | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 02/11/2029
|  | CS-09750 | SP Distribution plc | Glenluce GSP | SPT-RI-223 | Reconductor the existing circuits between Glenlee and Newton Stewart with High Temperature Low Sag conductors. | 02/11/2029
Learielaw Energy Storage | PRO-002531 | CS-08587 | Learielaw Energy Storage Ltd | Broxburn GSP | SPT-RI-2711 | AP Route 132kV Uprating - The connected and contracted generation at Broxburn GSP has reached a level that will exceed the intact capacity of the existing 132kV OHL AP Route (BROXCURR) on the No.1 Circuit. It is proposed to reconductor the No.1 Circuit on the AP Route with LARK conductor which will operate at 190°C. The increased rating will provide 191MVA to provide a higher rating to remove the overload under an intact system. Furthermore, the No.1 Circuit of the 132kV cable section entry into Currie 132kV substation will also need replaced to achieve 191MVA loading on this circuit. It is proposed to replace the No.1 Circuit with a single 1600mm AL cable. Additionally, the cost of replacing the existing cable section (130MVA rated) before the end of life will be recovered through TNUoS. | 31/10/2028
Legacy 400 | PRO-002193 | CS-08030 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101908-203900 | Uprate the Feckenham-Hams Hall 400 kV circuit to achieve a pre-fault summer rating more than 1800 MVA | 30/10/2033
|  | CS-08029 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 100425-200971 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2033
|  | CS-08035 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101909-203901 | Reconductor the Ironbridge-Rugeley 400kV circuit with 2x620mm2 conductor to achieve a pre-fault summer rating of 2490 MVA. | 30/10/2033
|  | CS-08037 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 100478-201049 | Reconductor the Drakelow-Willington East 400kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA | 30/10/2033
|  | CS-08036 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101978-204103 | Reconductor the Drakelow-Ratcliffe On Soar 400kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA | 30/10/2033
|  | CS-08024 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101329-202649 | Hotwire Enderby – Ratcliffe 400kV circuits 1 and 2 to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 30/10/2033
|  | CS-08027 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2033
|  | CS-08039 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 100975-201954 | Establish the Pentir - Trawsfynydd 400kV circuit 2 (including conversion of the existing 132kV circuit) | 30/10/2033
|  | CS-08025 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 30/10/2033
|  | CS-08028 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101910-203902 | Uprating of the Feckenham - Walham 400kV circuit to achieve minimum summer pre-fault rating of 2550MVA | 30/10/2033
|  | CS-08022 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 102069-204245 | Install power control devices with push and pull capability (up to 8 ohm) at the Connahs Quay-Rugeley circuit 1 & 2 | 30/10/2033
|  | CS-08023 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101292-201374 | Modification of the double tee circuit arrangement at Bodelwyddan (including the required busbar extension) to a double turn in arrangement. Creating Pentir - Bodelwyddan circuits 1&2, and Bodelwyddan - Connahs Quay circuits 1&2. Ensuring the turn-in arrangements match the rating of the circuits to Bodelwyddan and Connahs Quay | 30/10/2033
|  | CS-08032 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101939-203974 | Reconductor the Drakelow-Rugeley 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA | 30/10/2033
|  | CS-08038 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101987-204116 | Reconductor of the Bodelwyddan - Connahs Quay circuits 1&2 and Pentir-Bodelwyddan 1&2 with 3x700@75 degrees to achieve a Summer pre-Fault rating of 2790 MVA | 30/10/2033
|  | CS-08031 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101907-203905 | Reconductor the Drakelow – Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault summer rating of 2490 MVA | 30/10/2033
|  | CS-08033 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101977-204102 | Cable section uprate of the Bishops Wood-Penn 275kV circuit to match the overhead line summer prefault rating of 925MVA | 30/10/2033
|  | CS-08040 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 30/10/2033
|  | CS-08021 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 102068-204244 | Extend Legacy 400kV substation and make provision for the connection of the user bay. | 30/10/2033
|  | CS-08034 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2033
|  | CS-08041 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101267-202510 | Establish a CUSC Category 2 system to generator intertrip scheme to monitor both of the Wylfa – Pentir 400kV double circuits, and the 400kV circuits between Pentir, Connahs Quay, Trawsfynydd and Legacy | 30/10/2033
|  | CS-08026 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation | 101905-203903 | Install power control devices with push and pull capability (up to 8 ohm) at the Rugeley-Drakelow circuit | 30/10/2033
Legacy Green Energy Centre | PRO-001662 | CS-04487 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101327-202647 | Works to allow User to connect their generator bay at Legacy 400kV substation. Works to allow User to connect their generator bay at Legacy 400kV substation. | 30/10/2026
|  | CS-06846 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor triggered by R4 connection | 30/10/2026
|  | CS-06847 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the Circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits and the Cellarhead – Macclesfield and Cellarhead – Daines circuits | 30/10/2026
|  | CS-06848 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor. | 30/10/2026
|  | CS-06849 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 30/10/2026
|  | CS-06850 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101277-202523 | Installation of power electronics-based power flow control devices in the Pentir – Trawsfynydd 1 and 2 circuits 400kV circuits. | 30/10/2026
|  | CS-06844 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 101006-202010 | 1. Uprating of the Bodelwyddan – Connahs Quay 1 and 2 400kV circuits | 30/10/2026
|  | CS-06845 | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/10/2026
Legacy Tertiary Connection | PRO-001171 | CS-06851 | HD639LEG LIMITED | Legacy 400kV Substation | 100646-201324 | 1. Install a tertiary cable box or bushings on SGT4 2. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer at the 13kV side. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 31/08/2024
Leithenwater Wind Farm | PRO-001914 | CS-07649 | LEITHENWATER WIND ENERGY HUB LIMITED | Galashiels GSP | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 29/10/2027
|  | CS-07650 | LEITHENWATER WIND ENERGY HUB LIMITED | Galashiels GSP | SPT-RI-2080 | Dunlaw Extension to Galashiels Reinforcements – The works in this reinforcement entails the construction of a new 132kV overhead line (OHL) between Dunlaw Extension 132kV substation and Galashiels 132kV substation. The new OHL will be built on L7 steel lattice towers and strung with twin UPAS conductor. The new OHL will be tee-ed to the proposed Galashiels North 400kV substation. At Galashiels North 400kV two 400/132kV 360MVA transformer will be installed to establish connectivity to the new OHL. Two 400kV bay will be added to the 400kV substation to connect the transformers and two 132kV circuit breakers will be installed to connect the transformers to the new OHL. | 29/10/2027
Lethans Wind Farm | PRO-001367 | CS-05876 | BANKS RENEWABLES (LETHANS WIND FARM) LIMITED | Lethans 132kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/06/2027
|  | CS-05877 | BANKS RENEWABLES (LETHANS WIND FARM) LIMITED | Lethans 132kV Substation | Lethans WF Enabling Works | 1) Lethans 132kV substation install 132kV line isolator 2) Install c. 3km of cable from Lethans to Glenmucklock Substation 3) at Glenmuckloch substation install 132kV feeder bay 4) Kilmarnock South 400kV and 275kV uprating 5) New Cumnock 275kV Transformers Uprating 6) Glenglass Extension and Glenmuckloch Collector 7) Generation Export Management Scheme (GEMS) 8) Glenglass 132kV Substation | 30/06/2027
|  | CS-05878 | BANKS RENEWABLES (LETHANS WIND FARM) LIMITED | Lethans 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/06/2027
|  | CS-05879 | BANKS RENEWABLES (LETHANS WIND FARM) LIMITED | Lethans 132kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 30/06/2027
|  | CS-05880 | BANKS RENEWABLES (LETHANS WIND FARM) LIMITED | Lethans 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/06/2027
|  | CS-06455 | BANKS RENEWABLES (LETHANS WIND FARM) LIMITED | Lethans 132kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 30/06/2027
Lethans Wind Farm Extension | PRO-003553 | CS-08520 | Banks Renewables (Lethans East Wind Farm) Limited | Lethans 132kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 30/10/2027
|  | CS-08521 | Banks Renewables (Lethans East Wind Farm) Limited | Lethans 132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 30/10/2027
|  | CS-08523 | Banks Renewables (Lethans East Wind Farm) Limited | Lethans 132kV Substation | Lethans Extension Wind Farm - enabling works | At Lethans Collector substation install a 132kV line disconnector. | 30/10/2027
|  | CS-08522 | Banks Renewables (Lethans East Wind Farm) Limited | Lethans 132kV Substation | SPT-RI-2792 | Glenmuckloch to Lethans Collector 132kV Circuit | 30/10/2027
Lethen Wind Farm | PRO-002307 | CS-08107 | FRED. OLSEN RENEWABLES LIMITED | Lethen Wind Farm 132/33kV Substation | SHET-RI-177 | 3. Tomatin Additional SGTs - Install a new 275kV indoor GIS double busbar and two additional 275/132kV Super Grid Transformers at the Tomatin 275/132kV Substation | 31/10/2029
|  | CS-08109 | FRED. OLSEN RENEWABLES LIMITED | Lethen Wind Farm 132/33kV Substation | Lethen Wind Farm-132kV AIS Switch BayA1 | 0 | 31/10/2029
|  | CS-08108 | FRED. OLSEN RENEWABLES LIMITED | Lethen Wind Farm 132/33kV Substation | Lethen Wind Farm-132kV GIS Switch BayH1 | 0 | 31/10/2029
LGB300 | PRO-003907 | CS-09837 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/07/2031
|  | CS-09846 | Lovat Estates Ltd | LGB300 400KV Substation |  | FALSE | 31/07/2031
|  | CS-09835 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/07/2031
|  | CS-09845 | Lovat Estates Ltd | LGB300 400KV Substation | SPT-RI-2095 | Kincardine North 400kV Substation - The scope of works at Kincardine North 400kV Substation (ref. NOA Code LWUP) is summarised as follows. The new Kincardine North 400kV GIS Substation will initially connect the following circuits: SHE Transmission Alyth No.1 400kV, SHE Transmission Alyth No.2 400kV, Denny North No.1 400kV, Denny North No.2 400kV, Kincardine No.1 400kV, and Kincardine No.2 400kV. The substation will be equipped with two bus section circuit breakers and two bus coupler circuit breakers | 31/07/2031
|  | CS-09838 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI-025d | North East Reinforcement | 31/07/2031
|  | CS-09840 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/07/2031
|  | CS-09842 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI-180 | Second Peterhead 400kV Busbar - Construct a second 400kV Substation at Peterhead | 31/07/2031
|  | CS-09833 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI-007a | Beauly - Blackhillock 400kV OHL - Establish a new double circuit 400kV overhead line approximately 130km from Beauly to Blackhillock. The new OHL is connected to the Beauly 400kV AIS busbar and the Blackhillock 400kV GIS busbar. | 31/07/2031
|  | CS-09839 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI 033 | 7. Second East Coast 2GW HVDC Link Peterhead – England - Install an indoor 2GW HVDC converter station with associated equipment. HVDC cables to be routed into the sea and then south towards England (landing point to be confirmed). | 31/07/2031
|  | CS-09836 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/07/2031
|  | CS-09841 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI-134 and SPT-RI-1560 | 9. Beauly – Denny Second Circuit Upgrade from 275kV to 400kV -Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 31/07/2031
|  | CS-09834 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 31/07/2031
|  | CS-09844 | Lovat Estates Ltd | LGB300 400KV Substation | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 31/07/2031
|  | CS-09843 | Lovat Estates Ltd | LGB300 400KV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/07/2031
Lightsource Mount Annan BESS | PRO-003034 | CS-09286 | LIGHTSOURCE RENEWABLE UK DEVELOPMENT LIMITED | Chapelcross 132/33kV Substation | SPT-RI-231 | 0 | 31/10/2031
|  | CS-09287 | LIGHTSOURCE RENEWABLE UK DEVELOPMENT LIMITED | Chapelcross 132/33kV Substation | SPT-RI-2320 | 0 | 31/10/2031
|  | CS-09289 | LIGHTSOURCE RENEWABLE UK DEVELOPMENT LIMITED | Chapelcross 132/33kV Substation | Mount Annan - Substation Works | Installation of one 400/132kV 240MVA SGT and one 132kV disconnector | 31/10/2031
|  | CS-09288 | LIGHTSOURCE RENEWABLE UK DEVELOPMENT LIMITED | Chapelcross 132/33kV Substation | 400kV DBB Bay - Mount Annan | Installation of 400kV DBB bay at Wyseby Hill substation, extension to the original compound design may be required | 31/10/2031
|  | CS-09290 | LIGHTSOURCE RENEWABLE UK DEVELOPMENT LIMITED | Chapelcross 132/33kV Substation | Mount Annan - 132kV Disconnector | At Lightsource Mount Annan BESS substation, installation of one 132kV disconnector | 31/10/2031
Limekiln | PRO-000515 | CS-05887 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 30/04/2024
|  | CS-05888 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-006 | Install two x 240MVA 220kV 3.6km underground cable circuits from a transition joint near Ardneil bay to Hunterston. Develop a new transformer compound at Hunterston comprising 2 x 400/220kV 240MVA transformers, each equipped with tertiary connected 60MVAr shunt reactors. Install two new feeder bays of 400kV GIS double busbar switchgear at Hunterston East 400kV Substation and establish 400kV connections to the new transformer compound. Complete Associated civil works and other miscellaneous works including installation/modification of associated protection, control, telecommunications and metering equipment. | 30/04/2024
|  | CS-05889 | Limekiln Extension Limited | Limekilns 132/33kV substation | Limekilns Item 1 | Construction of a 6km single 132kV circuit from Dounreay 275/132kV substation, comprising 1km 132kV underground cable and 5km of 132kV trident wood pole overhead line (OHL), terminating on an indoor 132kV disconnector (613) installed within the Relevant Transmission Licensee building at Limekiln 132/33kV substation. | 30/04/2024
|  | CS-05890 | Limekiln Extension Limited | Limekilns 132/33kV substation | Limekilns Item 2 | The 132kV circuit will be connected to Dounreay 275/132kV substation via a spare 132kV feeder bay, comprising 132kV line disconnector (603), 132kV feeder circuit breaker (605) and 132kV double busbar selector disconnectors (604 and 606). | 30/04/2024
|  | CS-05891 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 30/04/2024
|  | CS-05892 | Limekiln Extension Limited | Limekilns 132/33kV substation | Limekilns Item 3 | The existing protection and telecommunication equipment at Dounreay 275/132 kV substation will be modified for the new connection. | 30/04/2024
|  | CS-03701 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-005 | Extend both the 275kV and 132kV busbars and install a second 275/132kV interbus auto-transformer at Dounreay substation. Upgrade the existing 150MVA interbus auto-transformer at Dounreay to 240MVA. | 30/04/2024
|  | CS-05881 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-037 | Fyrish 275/132kV Substation – Establish a new 275kV/132kV Fyrish substation close to the existing Alness 132kV OHL Teed location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. Two new 132kV underground cables will be installed to link the new 275kV/132kV Fyrish substation with the existing Alness GSP. (SHET-RI-037) | 30/04/2024
|  | CS-05882 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/04/2024
|  | CS-05883 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 30/04/2024
|  | CS-05884 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 30/04/2024
|  | CS-05885 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 30/04/2024
|  | CS-05886 | Limekiln Extension Limited | Limekilns 132/33kV substation | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 30/04/2024
Lincomb Farm 120MW BESS Scheme | PRO-002442 | CS-08488 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 101891-203873 | Uprate the circuit Drakelow 400kV Willington East 400kV to achieve a summer pre-fault rating of 1820MVA | 30/06/2033
|  | CS-08487 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/06/2033
|  | CS-08485 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 102411-204935 | Replace SGT4 existing 275/132kV 240MVA Supergrid Transformers with 275/132kV 360MVA Supergrid Transformer and associated circuit breaker with 40kA rms breaker rating | 30/06/2033
|  | CS-08491 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 101880-203857 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4-WILE4-2) to summer pre-fault rating 2490MVA | 30/06/2033
|  | CS-08495 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 101889-203868 | Reconductor the East Claydon legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 1820MVA | 30/06/2033
|  | CS-08483 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 102411-204933 | Replace SGT2 existing 275/132kV 240MVA Supergrid Transformers with 275/132kV 360MVA Supergrid Transformers and associated circuit breaker with 40kA rms breaker rating | 30/06/2033
|  | CS-08494 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 101978-204103 | Reconductor the Drakelow-Ratcliffe On Soar 400kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA | 30/06/2033
|  | CS-08493 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 101977-204102 | Cable section uprate of the Bishops Wood-Penn 275kV circuit to match the overhead line summer prefault rating of 925MVA | 30/06/2033
|  | CS-08489 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/06/2033
|  | CS-08490 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 101879-203856 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #1 (RATS4-WILE4-1) to summer pre-fault rating 2490 MVA | 30/06/2033
|  | CS-08486 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 102411-204936 | Replacement of CB 250 to have 40kA from existing 20kA | 30/06/2033
|  | CS-08492 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 100425-200971 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/06/2033
|  | CS-08482 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 102411-204932 | Replace SGT1 existing 275/132kV 240MVA Supergrid Transformers with 275/132kV 360MVA Supergrid Transformers and associated circuit breaker with 40kA rms breaker rating. | 30/06/2033
|  | CS-08484 | FPC Electric Land Limited | Bishops Wood 275kV Substation | 102411-204934 | Replace SGT3 existing 275/132kV 240MVA Supergrid Transformers with 275/132kV 360MVA Supergrid Transformer and associated circuit breaker with 40kA rms breaker rating. | 30/06/2033
Lisa's Battery Storage | PRO-003280 | CS-08294 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2030
|  | CS-08291 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2030
|  | CS-08293 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 31/10/2030
|  | CS-08295 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2030
|  | CS-08292 | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 31/10/2030
Lister Battery (formerly Lister Drive) | PRO-001088 | CS-05893 | LISTER BATTERY LTD | Lister Drive 275kV Substation | 100787-201590 | Attributable | 31/10/2023
|  | CS-05894 | LISTER BATTERY LTD | Lister Drive 275kV Substation | 100787-201589 | Attributable | 31/10/2023
Lister Drive 275kV | PRO-001248 | CS-07322 | LISTER DRIVE SOLUTIONS LIMITED | Lister Drive 275kV Substation | 100980-202032 | 0 | 23/06/2022
Little Gala Wind Farm | PRO-001478 | CS-06746 | SP Distribution plc | Lesmahagow GSP | SPT-RI-263 | Coalburn SGT4 - At Coalburn 400/132kV substation, works will be required to extend the compound to facilitate the extension of the 400kV and 132kV double busbars, installation of a fourth supergrid transformer (SGT4), along with the associated switchbays. | 31/10/2027
|  | CS-06747 | SP Distribution plc | Lesmahagow GSP | SPT-TOCO-551 | Lesmahagow GSP - The connection will be provided by installing two new 132kV double busbar feeder bays at Coalburn 132kV. From here two 132kV cable circuits of approximately 4km will be installed to the new Lesmahagow GSP site. At Lesmahagow GSP two new 132kV line disconnectors will be installed along with two 132/33kV 60MVA transformers. The Relevant Transmission Licensee shall install two new 33kV circuit breakers which will form the Point of Connection between the Relevant Transmission Licensee and the User | 31/10/2027
Little Hill | PRO-001556 | CS-06852 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 31/10/2026
|  | CS-06853 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 31/10/2026
|  | CS-06854 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 033769-033769 | Reconductor the Exeter – Hinkley Point – Taunton 400kV circuits to achieve a 2787MVA pre-fault summer rating. | 31/10/2026
|  | CS-06855 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 101052-202110 | Install power flow control devices along the Imperial Park – Melksham 400kV circuit | 31/10/2026
|  | CS-06856 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 100424-200970 | Reconductor the Bramley – Melksham 400kV circuits 1 and 2 to achieve a pre-fault summer rating of 1581MVA. | 31/10/2026
|  | CS-04726 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 31/10/2026
|  | CS-04727 | BRYN GILWERN ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 31/10/2026
Little Horsted | PRO-002214 | CS-08937 | CSE34 LIMITED | Little Horsted GSP | 033800-033800 | 1. Installation of new towers, and associated OHL works, for the single circuit turn0in of the Bolney – Ninfield, replacing tower 4VM069 2. The construction of new single-swtich mesh 400kV Little Horsted Substation with one section circuit breaker and associated disconnectors 3. The construction of two new feeder circuit bays including associated circuit breakers and disconnectors 4. Construction of two SGT HV circuit breakers and disconnectors 5. Works required to establish Little Horsted 400/132kV Substation, including the installation of the substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure | 31/10/2031
|  | CS-08938 | CSE34 LIMITED | Little Horsted GSP | 033800-200658 | 1. The installation of two 240MVA 400/132kV Super Grid Transformers (SGTs) including associated HV/LV surge arresters and earth switches 2. The installation of 132kV Switchgear on the LV side of the SGTs. This equipment will include the LV side SGT bay disconnector, circuit breaker and line side / cable side disconnectors 3. The installation of HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practive 1 | 31/10/2031
|  | CS-08939 | CSE34 LIMITED | Little Horsted GSP | 033800-204124 | 1. Works required to allow for the onversion of Little Horsted GSP Substation into a double busbar substion with a double circuit turn of the Bolney – Ninfield 400kV transmission circuit | 31/10/2031
|  | CS-08936 | CSE34 LIMITED | Little Horsted GSP | 101993-204127 | 1. Install a tertiary cable box or bushing on the SGT2 2. Install 13kV Cable (if required) from tertiary cable box or bushing to earthing transforer 3. Install an earthing transformer 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets | 31/10/2031
Little Raith BES | PRO-000887 | CS-06638 | DAISY NO 2 LIMITED | Glenniston GSP | SPT-RI-234 | Glenniston 132kV Substation Reinforcement and Associated Works to increase the thermal rating of the equipment: a. Glenniston 132kV T1 LVDOC Relay. b. Glenniston 132kV T2 LVDOC Relay. In addition, replacement of the 132kV disconnectors 124 and 128 and bus section circuit breaker 120 to achieve a minimum rating of 185MVA. | 15/08/2023
Littlewoods Wind Farm | PRO-001825 | CS-08473 | EDF ENERGY RENEWABLES LIMITED | Littlewoods Wind Farm 132/33kV | SHET-RI-079 | Additional 275/132kV SGT’s at Blackhillock - Reinforce the transmission network at Blackhillock substation by installing two additional new 275/132kV Supergrid Transformers. The transformers are to be rated at 360MVA. (SHETL- RI-079) | 31/08/2028
|  | CS-08474 | EDF ENERGY RENEWABLES LIMITED | Littlewoods Wind Farm 132/33kV | SHET-RI-176 | Pauls Hill/Glenfarclas Circuit Turn In - Move the existing open point from Keith 132kV Substation to Pauls Hill Substation and then turn in the Pauls Hill/Glenfarclas circuit to Blackhillock 132kV Substation. | 31/08/2028
Llanwern Phase 1 | PRO-001124 | CS-06857 | GREENFIELDS (T) LIMITED | Whitson 275kV Substation | 100304-200731 | 1. Extension of 33kV busbar and installation of a disconnector to accommodate 33kV generator bay. | 01/10/2028
|  | CS-06858 | GREENFIELDS (T) LIMITED | Whitson 275kV Substation | 100304-201748 | Replace the Quad Boosters 1 and 2 at Whitson for larger units | 01/10/2028
|  | CS-06859 | GREENFIELDS (T) LIMITED | Whitson 275kV Substation | 100304-201749 | Replacement of Whitson SGT5 for a larger rated unit | 01/10/2028
Llanwern Phase 2 | PRO-001125 | CS-07021 | FUTURE ENERGY LLANWERN LIMITED | Whitson 275kV Substation | 100414-200951 | Extension of 33 kV busbars on SGTs 3 and 4 and installation of disconnectors to accommodate 33 kV generator bays. | 01/10/2028
|  | CS-07022 | FUTURE ENERGY LLANWERN LIMITED | Whitson 275kV Substation | 100414-200957 | Extension of existing 33 kV cable sealing end compounds. | 01/10/2028
Llwynygog | PRO-001583 | CS-04715 | ESGAIR GALED ENERGY PARK LIMITED | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 04/02/2027
|  | CS-04716 | ESGAIR GALED ENERGY PARK LIMITED | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 04/02/2027
|  | CS-04717 | ESGAIR GALED ENERGY PARK LIMITED | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 04/02/2027
|  | CS-04718 | ESGAIR GALED ENERGY PARK LIMITED | Chirk GSP | 131323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 04/02/2027
|  | CS-04719 | ESGAIR GALED ENERGY PARK LIMITED | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 04/02/2027
Lochaber Smelter | PRO-001274 | CS-05895 | SIMEC LOCHABER HYDROPOWER 2 LIMITED | Fort William GSP | SHET-RI-045b | 1. Fort Augustus–Fort William 132kV OHL Upgrade Phase 2 - Reconductor one side of the 132kV double circuit OHL between Fort Augustus and Fort William (FFE). The 132kV circuit OHL (FFE) is to be reconductored with a higher capacity conductor. This will have a minimum summer pre-fault rating of 208MVA per circuit. Replace the existing 132kV cables on FFE & FFW into Fort Augustus with new 132kV cables rated suitably for the increased capacity of the new OHL conductor. Reinstate the permanent connection of the 132kV Kinlochleven circuit (FV1) to FFE following the completion of FFE reconductoring work. (SHET-RI-045b) | 31/10/2019
|  | CS-05896 | SIMEC LOCHABER HYDROPOWER 2 LIMITED | Fort William GSP | SHET-RI-045a | 3. Fort Augustus–Fort William 132kV OHL Upgrade Phase 1 - Reconductor the 132kV double circuit OHL between Fort Augustus and Fort William (FFW). The 132kV double circuit OHL (FFW) is to be reconductored with a higher capacity conductor. This will have a minimum summer pre-fault rating of 208MVA per circuit. Transfer the connection of Invergarry power station from FFE circuit of the OHL between Fort Augustus and Fort William to the FFW circuit. Temporarily transfer the connection of the Kinlochleven (FV1) 132kV circuit to FFW for the duration of the FFE reconductoring work. (SHET-RI-045a) | 31/10/2019
Locharber | PRO-004283 | CS-09795 | Renewable Connections Developments Limited | Arbroath GSP | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 31/10/2032
|  | CS-09796 | Renewable Connections Developments Limited | Arbroath GSP | SHET-RI-234 | Tealing Solar Tee – Tealing 132kV Upgrade – Upgrade the 5.8km of single circuit overhead line between the Tealing Solar tee-point and Tealing 132kV substation. The circuit requires a minimum continuous summer rating of 170MVA | 31/10/2032
|  | CS-09797 | Renewable Connections Developments Limited | Arbroath GSP | Transformers - Arbroath GSP | Installation of 2 x 120MVA transformers within the existing substation | 31/10/2032
|  | CS-09798 | Renewable Connections Developments Limited | Arbroath GSP | Arbroath Extension | The TCA asset installation will require an extension of the existing Arbroath GSP substation, and the new equipment will be installed to meet current Fire Separation Standards | 31/10/2032
|  | CS-09794 | Renewable Connections Developments Limited | Arbroath GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 31/10/2032
Locharmoss Solar & Battery | PRO-003477 | CS-09383 | SP Distribution plc | Dumfries GSP | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 30/10/2036
|  | CS-09385 | SP Distribution plc | Dumfries GSP | SPT-RI-298 | Chapelcross to Gretna OHL Reinforcement | 30/10/2036
|  | CS-09384 | SP Distribution plc | Dumfries GSP | SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 30/10/2036
Loch Fearna Pumped Storage | PRO-002569 | CS-07736 | GILKES ENERGY LIMITED | Loch Fearna Pumped Storage 132/18kV | Loch Fearna Item 1 | The installation of a 132kV feeder bay that would be required at the new Loch Lundie 132kV Substation (Part of TORI, SHET-RI-068) to connect the new banked double circuit from the Loch Fearna Pumped Storage 132/18kV Substation. The Loch Fearna Pumped Storage 132/18kV Substation will be connected to the new Loch Lundie 400/132kV Substation by approximately 25km of 132kV banked double circuit. The 25km circuit will consist of 24.5km OHL with the remaining 0.5km section into Loch Lundie 132kV Substation being underground cable. (At this early stage of the process we acknowledge that there may be challenges in obtaining planning consent for the construction of the 24.5km OHL but we will not be in a position to understand any specific planning requirements in advance of your acceptance of this offer. As per the terms of the offer, any changes to the design that are required in order to comply with any planning requirements, and any associated changes in costs, will be dealt with by way of amendments to the terms of the connection agreement.) | 31/10/2029
|  | CS-07737 | GILKES ENERGY LIMITED | Loch Fearna Pumped Storage 132/18kV | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 31/10/2029
|  | CS-07738 | GILKES ENERGY LIMITED | Loch Fearna Pumped Storage 132/18kV | SHET-RI-068 | Upgrade the existing 132kV double circuit OHL between Fort Augustus and Invergarry substation by a new 400kV OHL. The existing 132kV OHL forms part of the Fort Augustus to Fort William FFE/FFW circuits. Part of the upgrade is to establish a 400/132kV substation at Invergarry to connect the existing 132kV OHL from Fort William and Invergarry Generation. The new 400kV OHL will terminate into the 400kV busbar at For Augustus. | 31/10/2029
|  | CS-07739 | GILKES ENERGY LIMITED | Loch Fearna Pumped Storage 132/18kV | SHET-RI-069 | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | 31/10/2029
|  | CS-07741 | GILKES ENERGY LIMITED | Loch Fearna Pumped Storage 132/18kV | SPT-RI-1560 | It is proposed to uprate the existing Denny-Braco West 275kV circuit to 400kV operation by transferring the circuit from its current bay in Denny 275kV substation to a new bay in Denny 400kV substation. | 31/10/2029
|  | CS-07740 | GILKES ENERGY LIMITED | Loch Fearna Pumped Storage 132/18kV | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 31/10/2029
Loch Fergus Solar | PRO-003808 | CS-09404 | Lochfergus Solar LTD | Lochfergus Solar Substation 33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/04/2026
Loch Kemp PSH Phase 2 | PRO-002285 | CS-08475 | STATERA ENERGY LIMITED | Loch Kemp 275kV substation | SHET-RI-007a | Beauly - Blackhillock 400kV OHL - Establish a new double circuit 400kV overhead line approximately 130km from Beauly to Blackhillock. The new OHL is connected to the Beauly 400kV AIS busbar and the Blackhillock 400kV GIS busbar. | 31/10/2030
|  | CS-08476 | STATERA ENERGY LIMITED | Loch Kemp 275kV substation | SHET-RI-201 | Foyers Substation Extension and Connection to Loch Kemp - Extend the existing Foyers 275kV busbar to include a new 275kV bay to connect the new circuit from the Loch Kemp Pumped Storage 275/18kV Substation. Construct a 275kV busbar with three bays at the Loch Kemp 275kV/18kV Substation. The Loch Kemp Pumped Storage 275/18kV Substation will be connected to the existing Foyers 275kV Substation by approximately 10.5km of single circuit 275kV underground cable. | 31/10/2030
Loch Kemp Pumped Storage | PRO-001559 | CS-04281 | LOCH KEMP STORAGE LIMITED | Loch Kemp 275kV substation | Loch Kemp H1 Works | Extension of the existing Foyers 275kV busbar to include a new 275kV bay to connect the new circuit from the Loch Kemp Pumped Storage 275/18kV Substation. The Loch Kemp Pumped Storage 275/18kV Substation will be connected to the existing Foyers 275kV Substation by approximately 10.5km of single circuit 275kV underground cable. The User has requested an underground cable option instead of an overhead line connection. The additional cost of the 6.5km of the underground cable compared to the original overhead line solution would be payable by the User as a One-Off Works cost. The remaining 4km of underground cable has not been determined as customer choice to connect Loch Kemp Pumped Storage due to consenting issues of an overhead line solution for this length. | 31/10/2027
|  | CS-04282 | LOCH KEMP STORAGE LIMITED | Loch Kemp 275kV substation | SHET-RI-132 | Beauly - Blackhillock High Temperature Reconductoring | 31/10/2027
Loch Liath Wind Farm | PRO-001671 | CS-09459 | LOCH LIATH WIND FARM LIMITED | Loch Liath 132/33kV Substation | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 31/10/2035
|  | CS-09458 | LOCH LIATH WIND FARM LIMITED | Loch Liath 132/33kV Substation | Loch Liath Wind Farm H1 | 1. Install a new 132kV double busbar feeder bay with associated 132kV Switchgear at the new Fasnakyle 132kV Substation (Part of TORI, SHET-RI 134b). 2. Construct approximately 10.4km of single circuit 132kV overhead line from the Loch Liath Wind Farm 132kV Substation to Fasnakyle 132kV Substation. This 132kV OHL will connect to a new bay on the Fasnakyle 132kV busbars, via the required 132kV switchgear. 3. Installation of a new 132kV disconnector at the Loch Liath Wind Farm 132kV Substation. | 31/10/2035
|  | CS-09460 | LOCH LIATH WIND FARM LIMITED | Loch Liath 132/33kV Substation | SHET-RI-134b | Fasnakyle Substation 132kV Reinforcement – The existing Fasnakyle Substation is due to be upgraded from 275kV circuit to 400kV, as part of the Beauly-Denny Second Circuit Upgrade (SHET-RI-134). This document provides additional information on the specific changes required at Fasnakyle Substation, as part of this reinforcement. (SHET-RI-134b). | 31/10/2035
|  | CS-09461 | LOCH LIATH WIND FARM LIMITED | Loch Liath 132/33kV Substation | SHET-RI-212 | Construct a new 400kV overhead line to run from Beauly, via the Fort Augustus 2 400kV substation, to run across the B4 boundary. | 31/10/2035
Lochluichart Battery Storage | PRO-002288 | CS-08205 | SSE GENERATION LIMITED | Grudie Bridge GSP | SHET-RI-065a | Beauly 132 kV Substation Redevelopment- Establish a new 132kV double busbar arrangement at Beauly substation, and transfer the circuits from the existing 132kV busbar to the new busbar. Connect the new 132kV double busbar to the existing 275kV busbar via two new 360MVA 275/132kV transformers. Third new 360MVA 275/132kV transformer will be undertaken under SHET-RI 065b. (SHET-RI-065a) | 31/10/2025
|  | CS-08206 | SSE GENERATION LIMITED | Grudie Bridge GSP | SHET-RI-065b | Beauly 3rd SGT Replacement- Replacement of third existing 275/132kV 120MVA SGT with a new 360MVA 275/132kV transformer. (SHET-RI-065b) | 31/10/2025
Loch Luichart Extension II | PRO-000487 | CS-03702 | BLUEBELL WIND FARM LIMITED | Loch Luichart Extension II Substation | SHET-RI-065 | Beauly 132kV Reinforcement – Establish a new 132kV GIS double busbar arrangement at Beauly substation, and connect to the existing 275kV busbar via two 480MVA 275/132kV transformers. The Deanie/Aigas (BDN/BDS) 132kV circuits and the Corriemoillie (BM1/BM2) 132kV double circuit will be removed from the existing 132kV busbar at Beauly, and connected to the new 132kV GIS busbar. The existing 132kV busbar will in part be retained, with connectivity to the 275kV busbar maintained via two of the existing 120MVA 275/132kV transformers. The existing 132kV circuits to Elgin/Keith (BIN/BIS) and Boat of Garten (BR1/BR2) and the 132/33kV GTs will remain connected to this busbar. The third 120MVA SGT will be removed. (SHET-RI-065) | 31/10/2024
|  | CS-03703 | BLUEBELL WIND FARM LIMITED | Loch Luichart Extension II Substation | SHET-RI-119 | 2. Corriemoillie Transformer Protection Modification - At the existing Corriemoillie substation, install a 3 ended grid transformer differential protection scheme on GT2 to enable the connection of a second generator at Corriemoillie. | 31/10/2024
Loch nan Eun PSH | PRO-002063 | CS-07456 | LOCH NAN EUN STORAGE LIMITED | Loch Nan Eun 275/18kV | SPT-RI-1560 | It is proposed to uprate the existing Denny-Braco West 275kV circuit to 400kV operation by transferring the circuit from its current bay in Denny 275kV substation to a new bay in Denny 400kV substation. | 31/10/2029
|  | CS-07457 | LOCH NAN EUN STORAGE LIMITED | Loch Nan Eun 275/18kV | SPT-RI-246 | Denny North SGT2 – At Denny North substation, a new 1000MVA 400/275kV supergrid transformer and associated circuit breakers will be installed. This will increase the thermal capacity of Denny North 400kV substation, and across the B4 Boundary, to facilitate the connection of generation in the SHE Transmission area. | 31/10/2029
|  | CS-04635 | LOCH NAN EUN STORAGE LIMITED | Loch Nan Eun 275/18kV | Loch Tarff H1 Works | The installation of a 400kV feeder bay and a step down 480MVA 400/132kV Super Grid Transformer would be required at the new Fort Augustus 400kV Substation Extension to connect the new circuit from the Loch Tarff Pumped Storage 132/18kV Substation. | 31/10/2029
|  | CS-04636 | LOCH NAN EUN STORAGE LIMITED | Loch Nan Eun 275/18kV | Loch Tarff H1 Works 2 | The Loch Tarff Pumped Storage 132/18kV Substation will be connected to the new Fort Augustus 400/132kV Substation by approximately 7km of single circuit 132kV underground cable. The User has requested an underground cable option instead of an overhead line connection. The additional cost of 3.65KM of the underground cable compared to the original overhead line solution would be payable by the User as a One-Off Works cost. The remaining 3.35KM of underground cable has not been determined as customer choice to connect Loch Tarff Pumped Storage. | 31/10/2029
|  | CS-04637 | LOCH NAN EUN STORAGE LIMITED | Loch Nan Eun 275/18kV | SHET-RI-069 | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | 31/10/2029
|  | CS-04638 | LOCH NAN EUN STORAGE LIMITED | Loch Nan Eun 275/18kV | SHET-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 31/10/2029
|  | CS-04639 | LOCH NAN EUN STORAGE LIMITED | Loch Nan Eun 275/18kV | SHET-RI-068 | Upgrade the existing 132kV double circuit OHL between Fort Augustus and Invergarry substation by a new 400kV OHL. The existing 132kV OHL forms part of the Fort Augustus to Fort William FFE/FFW circuits. Part of the upgrade is to establish a 400/132kV substation at Invergarry to connect the existing 132kV OHL from Fort William and Invergarry Generation. The new 400kV OHL will terminate into the 400kV busbar at For Augustus. | 31/10/2029
|  | CS-04640 | LOCH NAN EUN STORAGE LIMITED | Loch Nan Eun 275/18kV | SHET-RI-134 | Upgrade the existing Beauly / Fasnakyle/ Fort Augustus / Tummel-Kinardochy / Braco West / Bonny Bridge 275kV circuit to 400kV; mirroring the ratings of the existing 400kV circuit, along the route. | 31/10/2029
|  | CS-04641 | LOCH NAN EUN STORAGE LIMITED | Loch Nan Eun 275/18kV | SPT-RI-1560 | It is proposed to uprate the existing Denny-Braco West 275kV circuit to 400kV operation by transferring the circuit from its current bay in Denny 275kV substation to a new bay in Denny 400kV substation. | 31/10/2029
|  | CS-04642 | LOCH NAN EUN STORAGE LIMITED | Loch Nan Eun 275/18kV | SHET-RI-169 | Fort Augustus 400kV Busbar Extension - The Fort Augustus 400kV Busbar Extension includes the establishment of a 400kV double busbar complete with two bus couplers, one bus section, four feeder bays to connect to the line feeder bays (Cable) and two feeder bays to connect to the Super Grid Transformers (SGT). | 31/10/2029
Lochore BESS | PRO-003483 | CS-09507 | LOCHORE BESS LTD | Westfield GSP | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 31/10/2031
|  | CS-09508 | LOCHORE BESS LTD | Westfield GSP | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 31/10/2031
|  | CS-09509 | LOCHORE BESS LTD | Westfield GSP | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 31/10/2031
|  | CS-09510 | LOCHORE BESS LTD | Westfield GSP | SHET-RI-185 | Kintore - Tealing 400kV circuit – Establish a new 400 kV double circuit overhead line between Kintore 400 kV substation and Tealing 400 kV substation. | 31/10/2031
Loganhead Windfarm | PRO-000306 | CS-05897 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-294 | Ewe Hill to Hopsrig collector substations 132kV circuit | 31/10/2026
|  | CS-05898 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-191 | The thermal capacity of the 132kV circuit between Gretna 132kV substation and Ewe Hill Wind Farm 132kV Collector Substation (works detailed in SPT-RI-017), will be increased by re-conductoring the 132kV overhead line utilising “Lark” High Temperature Low Sag (HTLS) conductor (~16km), and installing an additional 800mm2 Al XLPE 132kV underground cable in parallel with the existing cable(~0.3km), to give a minimum summer continuous rating of 224MVA. This is to accommodate additional generation connecting at the Ewe Hill Wind Farm 132kV Collector Substation. | 31/10/2026
|  | CS-05899 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | 100442-200991 | Chapelcross – Harker 132kV circuit uprating | 31/10/2026
|  | CS-05900 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-232 | Ewe Hill Substation Transformer 132/33kV - Installation of a new 132/33kV 90MVA transformer at Ewe Hill Wind Farm Substation. This will create a new 33kV busbar to allow new generation to connect. (SPT-RI-232). | 31/10/2026
|  | CS-05901 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 31/10/2026
|  | CS-05902 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 31/10/2026
|  | CS-05903 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | SPT-RI-232 | Ewe Hill Substation Transformer 132/33kV - Installation of a new 132/33kV 90MVA transformer at Ewe Hill Wind Farm Substation. This will create a new 33kV busbar to allow new generation to connect. (SPT-RI-232). | 31/10/2026
|  | CS-05904 | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation | 100406-200937 | Reconductor Harker – Gretna – Hawick circuit. Uprate the V route 132kV overload line circuit (between Tower V075 and Harker 132kV substation) to provide a minimum summer pre-fault continuous rating of 170MVA. | 31/10/2026
Longfield Solar | PRO-001053 | CS-06925 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | NGET - 100504-201083 | Construction of a new 6 bay 400kV substation at Porters Wood, including 4x feeder bays, lx coupler bay and provision for lx Generator Bay (User Works) | 01/04/2025
|  | CS-06926 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | NGET - 100504-201137 (Opex) | Temporary diversion of the Bramford-Braintree-Bulls Lodge 400kV circuit to facilitate the permanent ORL works | 01/04/2025
|  | CS-06927 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | NGET —10027- 200606 | OHL reconductoring to uprate the new Porters Wood — Rayleigh Main 400 kV circuit. | 01/04/2025
|  | CS-06928 | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 033458-033458 | OHL reconductoring to uprate the new Porters Wood - Bulls Lodge -Rayleigh Main 400 kV circuit | 01/04/2025
Longmorn Energy Park | PRO-002727 | CS-09243 | ELGIN ENERGY ES CO LIMITED | Blackhillock 275kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 15/08/2031
|  | CS-09242 | ELGIN ENERGY ES CO LIMITED | Blackhillock 275kV Substation | Longmorn 275kV Line Isolator H1 | Longmorn 275kV Line Isolator H1 | 15/08/2031
|  | CS-09244 | ELGIN ENERGY ES CO LIMITED | Blackhillock 275kV Substation | SHET-RI-222 | SHET-RI-222 - Longmorn energypark Substation and OHL works | 15/08/2031
|  | CS-09241 | ELGIN ENERGY ES CO LIMITED | Blackhillock 275kV Substation | Longmorn 275kV AIS switch bay - A1 | 0 | 15/08/2031
Long Stratton PV & BESS Station | PRO-002297 | CS-08835 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 30/10/2031
|  | CS-08828 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 102188-204406 | Installation of a new AIS double busbar 400kV substation between between Bramford 400kV and Norwich Main 400 kV with associated 4 feeder bays, 1 Coupler Bay, 1 section bay. Provide a Double turn in connection of the new substation to the existing 400 kV OHL circuits between Bramford and Norwich Main Substations. Installation of all Circuit Breakers with a higher nominal rating, X/R derating and Initial peak CB rating breakers. | 30/10/2031
|  | CS-08834 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 100381-200905 | Extension of the existing East Anglia operational intertripping scheme to include the connection. | 30/10/2031
|  | CS-08829 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 102188-204407 | Extension of 400kV main and reserve busbar of newly built Long Stratton 400kV substation to accommodate the User’s Bay. | 30/10/2031
|  | CS-08836 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 100952-201899 | Reconductor EAST CLAYDON-LEIGHTON BUZZARD (ECLA4- LEIB4B-1) 400kV circuit to achieve a minimum rating of 2450MVA summer pre-fault rating | 30/10/2031
|  | CS-08837 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 101247-202487 | The circuits running from Leighton Buzzard to Sundon 1&2 (LEIB4A-SUND4- 1) and LEIB4B-SUND4-2 will also be reconductored with 4 x 400mm2 conductor rating 2870MVA, 75˚C for winter intact condition. | 30/10/2031
|  | CS-08838 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 021742-021742 | 1) The existing double circuits running from Pelham to Rye House (PELH4- RYEH4B-1) and from Rye House to Rye House (RYEG4 – RYEH4B-1) will also be reconductored with Triple Araucaria 3 x 700mm2 conductor rating 3160MVA, 90˚C for pre fault summer rating. 2) The circuit running from Rye House to Waltham Cross (RYEH4- WALX4A-1) will also be reconductored with 2 x 700mm2 conductor rating 2800MVA, 160˚C for pre fault summer rating. 3) The circuit running from (Brimsdown to Hackney (BRIM4C - HACK4-1) and Brimsdown to Waltham Cross (BRIM4D -WALX4-2) will also be reconductored with 2 x 700mm2 conductor rating 1860MVA, 75˚C for pre fault summer rating. | 30/10/2031
|  | CS-08843 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 30/10/2031
|  | CS-08847 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 101975-204100 | 1. At Kings Lynn 400kV: Ensure circuit break X130 to be rated to 63kA with tested X/R ration of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2031
|  | CS-08856 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 102122-204324 | Extend Wymondley 400kV substation main and reserve 2 busbars for the provision of one User bay | 30/10/2031
|  | CS-08857 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 101248-204325 | Add a new bus coupler and three new bays at Wymondley 400kV substation to facilitate the turn in of the existing Pelham to Sundon 400kV circuit at Wymondley 400kV substation. | 30/10/2031
|  | CS-08850 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 30/10/2031
|  | CS-08858 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 30/10/2031
|  | CS-08844 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 101729-203439 | At Necton 400kV Replace circuit breakers X230, X130, X330, X160, X170, X120, X370, X305 with higher ratings fault capability at Necton 400kV substation. | 30/10/2031
|  | CS-08852 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 30/10/2031
|  | CS-08855 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 30/10/2031
|  | CS-08848 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 30/10/2031
|  | CS-08849 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 021071-021073 | Loop into the new Kings Lynn B 400kV substation with the near side Norwich-Walpole 400kV circuit to form a Walpole- Kings Lynn B and Kings Lynn - Necton - Norwich Main circuit connection. Construction of a new 2.7km double circuit | 30/10/2031
|  | CS-08840 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 30/10/2031
|  | CS-08851 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 100944-201883 | Build a new 400 kV double circuit between Mablethorpe and Weston Marsh Substations | 30/10/2031
|  | CS-08839 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 101248-202488 | 1. The circuit running from Pelham to Wymondley (PELH4-WYMO4-1) will also be reconductored with 3 x 700mm2 conductor rating 2790MVA, 75˚C for pre fault summer rating. 2. The circuit running from Pelham to Wymondley (PELH4-WYMO4-1_a) will also be reconductored with 3 x 700mm2 conductor rating 3160MVA, 90˚C for pre fault summer rating. 3. The circuit running from Sundon to Wymondley (SUND4-WYMO4-1) will also be reconductored with 3 x 700mm2 conductor rating 3160MVA, 90˚C for pre fault summer rating. | 30/10/2031
|  | CS-08854 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3820 MVA | 30/10/2031
|  | CS-08846 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ration of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2031
|  | CS-08841 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 100468-201037 | The circuits running from Cowley to East Claydon (COWL4-ECLA4-1) and Cowley to Leighton Buzzard (COWL4-LEIB4A-1) will also be reconductored with 4 x 400mm2 conductor rating 2870 MVA, 75˚C for winter intact condition | 30/10/2031
|  | CS-08853 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 30/10/2031
|  | CS-08845 | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2031
Lorg Extension Wind Farm | PRO-002430 | CS-08309 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 13/08/2029
|  | CS-08307 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 13/08/2029
|  | CS-08310 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 13/08/2029
|  | CS-08308 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 13/08/2029
Lorg Wind Farm | PRO-000153 | CS-06402 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-007 | New Cumnock 275/132kV Substation | 30/04/2027
|  | CS-06403 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | Lorg Wind Farm Part 1 | Installation of one disconnector at Lorg Wind Farm. | 30/04/2027
|  | CS-06404 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-111 | The Kendoon to Maybole T 132kV single circuit will be reconfigured to form two new circuits, a circuit from Kendoon to New Cumnock, and a circuit from New Cumnock to Margree windfarm substation. | 30/04/2027
|  | CS-06405 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/04/2027
|  | CS-06406 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/04/2027
|  | CS-06407 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-292 | Lorg to Shepherds Rig Tee - Install ~10km of 132kV wood pole overhead line with UPAS conductor (75°C, minimum summer pre-fault rating 176MVA) between Lorg 132kV substation and the proposed Shepherds Rig tee connection. The will form part of the Lorg to Holmhill 132kV overhead line. | 30/04/2027
|  | CS-05905 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-211 | Construct a new 132kV switching station, named Holm Hill, and install a 132kV OHL circuit between the new site and the tee off points to Shepherds Rig and Lorg wind farms. At an appropriate tee-off point on the New Cumnock to Kendoon 132kV circuit, install the new Holm Hill 132kV Switching Station containing one 132kV circuit breaker with two associated disconnectors. Install ~8km of 132kV wood pole overhead line with High Temperature Low Sag (HTLS) EAGLE conductor (190°C, minimum summer pre-fault rating 295MVA) to the tee point between Shepherd’s Rig and Lorg wind farms. | 30/04/2027
|  | CS-05906 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 30/04/2027
|  | CS-05907 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/04/2027
|  | CS-06408 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV | SPT-RI-1507 | Holm Hill 132kV substation - At an appropriate point next to the DE route establish a 132kV substation (Holmhill 132kV substation) by teeing into the proposed future New Cumnock to Glenlee 132kV circuit. The substation will consist of a 132kV busbar to which wind farm circuits will connect to. | 30/04/2027
Lovedean (Tertiary) | PRO-000484 | CS-07122 | LOVEDEAN GREEN LIMITED | Lovedean 400kV Substation | 100574-201198 | 1. Site extension to facilitate the transmission works 2. Install a tertiary cable box or bushings on the SGT 2A. 3. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer. 4. Install an earthing transformer. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 6. Local works to facilitate the Category 2 with Sellindge Operational Tripping Scheme (OTS) as described in Appendix F3 to the Bilateral Connection Agreement. 7. Local works required to connect the User to the South West Operational Tripping Scheme (OTS), as described in Appendix F3 to the Bilateral Connection Agreement. | 30/07/2024
|  | CS-07123 | LOVEDEAN GREEN LIMITED | Lovedean 400kV Substation | 100298-200724 | 1. Re-conductor Fleet-Lovedean 400kV double circuits. | 30/07/2024
|  | CS-07124 | LOVEDEAN GREEN LIMITED | Lovedean 400kV Substation | 033773-033773 | Thermal upgrade of Bramley – Fleet 400kV double circuits. | 30/07/2024
|  | CS-07125 | LOVEDEAN GREEN LIMITED | Lovedean 400kV Substation | 31867 | 1. Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent | 30/07/2024
Lovedean Greener Grid Park | PRO-001855 | CS-09300 | STATKRAFT UK LTD | Lovedean 400kV Substation | 101655-203302 | At Lovedean 400kV site, Bus extension to facilitate the transmission works | 01/06/2028
|  | CS-09301 | STATKRAFT UK LTD | Lovedean 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to achieve 1990MVA pre-fault summer rating | 01/06/2028
|  | CS-09302 | STATKRAFT UK LTD | Lovedean 400kV Substation | 033773-033773 | Hotwire the Bramley – Fleet circuits (A846/A847). The existing conductor is 4×400mm2 ACSR 50oC, hotwiring the route to 65oC or higher would meet the required rating. The post-fault winter peak rating of 4×400mm2 ACSR 65oC is 3180MVA | 01/06/2028
Lunanhead Battery | PRO-000883 | CS-06681 | GIGABOX NO 4 LIMITED | Lunanhead GSP | Lunanhead TCA Works | Intertrip required for the loss of one of the grid transformers at Lunanhead 132/33kV GSP | 31/08/2022
Lunanhead Solar Park | PRO-001623 | CS-04475 | RELAY SUTTIESIDE LIMITED | Lunanhead GSP | Lunanhead Solar Park H1 works item 1 | 1. The installation of four new protection bays, two at each of the remote ends between Tealing and Lunanhead. There is also a Requirement to install two new VTs on both circuits at Lunanhead. | 31/10/2025
|  | CS-04476 | RELAY SUTTIESIDE LIMITED | Lunanhead GSP | Lunanhead Solar Park H1 Works item 2 | 2. Replacement or modification of the Battery Systems, LVAC Board and Standby Generator at Lunanhead 132/33kV GSP, along with the upgrade of communication links between Lunanhead 132/33kV GSP substation and Tealing 132kV substation. | 31/10/2025
|  | CS-04477 | RELAY SUTTIESIDE LIMITED | Lunanhead GSP | Lunanhead Solar Park H1 works item 3 | 3. An intertrip is required for the loss of one of the Grid Transformers at Lunanhead 132/33kV GSP. a. These signals shall be provided by the Host Distribution Network Operator via a separate relay panel within the 33kV Switchroom from the signals described below. b. Provision of status signals are required for the following: i. 1TO and 2TO 33kV circuit breakers at Lunanhead GSP. ii. 1T7 and 2T7 33kV disconnectors at Lunanhead GSP. iii. 115 and 215 132kV circuit breakers at Lunanhead GSP | 31/10/2025
Lurg Hill | PRO-001264 | CS-05911 | EDP RENEWABLES UK LIMITED | Keith GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 01/05/2024
|  | CS-05912 | EDP RENEWABLES UK LIMITED | Keith GSP | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 01/05/2024
M74 West Wind Farm | PRO-002398 | CS-08142 | RENEWCO POWER LIMITED | M74 West Wind Farm 132kV | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 27/10/2028
|  | CS-08143 | RENEWCO POWER LIMITED | M74 West Wind Farm 132kV | M74 West Wind Farm Enabling Works | 1. Redshaw 400kV Substation - It is proposed to build a new 400kV GIS substation, building to be sized to accommodate 15 bays. The initial GIS installed to include the following: • 6x 400kV feeder bays: 2x ELVA, 1x STHA, 1x COAL, 2x Glenmuckloch • 1x 400kV bus coupler • 1x 400kV bus section • 2x 400kV SGT bays (SGT2 not proposed but 400kV GIS bay to be installed as part of the initial build) • Space to be included within the building to accommodate a future bus section, future SGT3 and SGT4 400kV GIS bays and 2x future 400kV GIS feeder bays • Installation of a single 400/132kV 360MVA (SGT1) unit at this time | 27/10/2028
Mablethorpe Storage | PRO-001979 | CS-07639 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 100944-201880 | Modifications to Grimsby West substation for the new Lincolnshire Green 400kV OHL | 30/11/2031
|  | CS-07645 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 101875-203853 | At Keadby 400kV substation: Installation of a 2750MVA power electronics bases Power flow control device with the capacity of pushing mode capable of injecting up to +8 ohm in the Creyke Beck-Killingholme-Keadby 400kV circuit | 30/11/2031
|  | CS-07626 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 101815-203742 | Mablethorpe Storage SEL infrastructure comprising of a substation extension to new Maplethorpe substation including three generator bays, a bus coupler, a feeder bay and section breakers | 30/11/2031
|  | CS-07632 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 100944-201881 | Build a new 400kV double circuit between Grimsby West and Maplethorpe 400kV substation | 30/11/2031
|  | CS-07633 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 100944-201882 | Build a new 400kV Mablethorpe Substation with 6 Bays - 4 Feeder bays, 1 Coupler Bay, 2 Section Breakers Main & Reserve | 30/11/2031
|  | CS-07634 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Mablethorpe and Weston Marsh Substations | 30/11/2031
|  | CS-07644 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 100455-201020 | At Keadby 400kV substation: Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby –Thorpe Marsh 400kV circuit | 30/11/2031
|  | CS-07635 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main & Reserve | 30/11/2031
|  | CS-07636 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 30/11/2031
|  | CS-07646 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 101892-203877 | Reconductoring of the Drax - Keadby - Thorpe Marsh circuit (Drax leg only) to achieve 2750MVA Pre-summer ratings. | 30/11/2031
|  | CS-07648 | STATERA ENERGY LIMITED | Mablethorpe 400kV Substation | 101746-203470 | LRNC - South Lincolnshire to Rutland new OHL reinforcement works | 30/11/2031
Macduff Battery Storage | PRO-002250 | CS-07701 | Macduff Battery Storage Ltd | Macduff GSP | Macduff Battery Storage Intertrip | Intertrip for the loss of one of the Grid Transformers at MacDuff 132/33kV GSP. These signals will be provided to the Host Distribution Network Operator via a separate relay panel within the 33kV Switchroom | 30/04/2024
|  | CS-07703 | Macduff Battery Storage Ltd | Macduff GSP | Macduff Battery Storage - LoM | A loss of mains scheme will also be configured at Macduff GSP as requested by the Host DNO | 30/04/2024
|  | CS-07702 | Macduff Battery Storage Ltd | Macduff GSP | Macduff Battery Storage - Protection Schemes | Modification to the existing LV Directional Overcurrent (DOC) protection settings at MacDuff 132/33kV substation will also be required. | 30/04/2024
Maesnant Energy Park | PRO-001919 | CS-08980 | Maesnant Energy Park Limited | Chirk GSP | 101323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 01/11/2033
|  | CS-08982 | Maesnant Energy Park Limited | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 01/11/2033
|  | CS-08984 | Maesnant Energy Park Limited | Chirk GSP | 01381-202705 | Establish a new 400kV double circuit from Connahs Quay 400kV substation to the Rugeley 400 kV substation. (This includes circa 90km of L6 tower with 4x400mm2 conductor for each circuit plus 2 feeder bays at each Connahs Quay and Rugeley substations) | 01/11/2033
|  | CS-08985 | Maesnant Energy Park Limited | Chirk GSP | 101905-203903 | nstall power control devices with push and pull capability (up to 8 ohm) at the Rugeley-Drakelow circuit | 01/11/2033
|  | CS-08981 | Maesnant Energy Park Limited | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 01/11/2033
|  | CS-08978 | Maesnant Energy Park Limited | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 01/11/2033
|  | CS-08983 | Maesnant Energy Park Limited | Chirk GSP | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 01/11/2033
|  | CS-08979 | Maesnant Energy Park Limited | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 01/11/2033
Magwind | PRO-001766 | CS-05384 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | Magwind Item 1 | At New Dounreay 400kV Substation, install two 400 kV feeder bays, with each bay comprising 2 x 400 kV busbar selection switches, 1 x 400 kV circuit breaker, 1 x 400 kV line disconnector and associated protection equipment. The ownership boundary between the Onshore Transmission Licensee’s assets and User owned equipment will be the 400kV clamps on the User’s side of the 400kV line disconnectors at the New Dounreay 400kV Substation. | 31/10/2033
|  | CS-05385 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-05386 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-05387 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-05388 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-05389 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-05390 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-05391 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2033
|  | CS-05392 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-05393 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 31/10/2033
|  | CS-05394 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-05395 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-05396 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-05397 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 31/10/2033
|  | CS-05398 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-05399 | MAGNORA OFFSHORE WIND AS | REVIEW - New Dounreay | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
Mannington | PRO-001091 | CS-05913 | PIVOTED POWER LLP | Mannington 400kV Substation | NGET-RI-30752 | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. | 31/10/2024
|  | CS-05914 | PIVOTED POWER LLP | Mannington 400kV Substation | NGET-RI-31671-1 | Re-conductor the Bramley - Fleet OHL circuits to increase capacity. | 31/10/2024
|  | CS-05915 | PIVOTED POWER LLP | Mannington 400kV Substation | NGET-RI-31671-2 | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. | 31/10/2024
|  | CS-05916 | PIVOTED POWER LLP | Mannington 400kV Substation | NGET-RI-33539 | Hot wiring of the Hinckley Point - Melksham 1 and 2 circuits to increase their thermal rating. | 31/10/2024
| PRO-001092 | CS-07114 | BAYWA R.E. UK LIMITED | Mannington 400kV Substation | 100298-200724 | 1. Re-conductor Fleet-Lovedean 400kV double circuits. | 20/05/2025
|  | CS-07115 | BAYWA R.E. UK LIMITED | Mannington 400kV Substation | 033773-033773 | Thermal upgrade of Bramley – Fleet 400kV double circuits. | 20/05/2025
|  | CS-07112 | BAYWA R.E. UK LIMITED | Mannington 400kV Substation | 100978-201961 | 1. Install a tertiary cable box or bushings on the SGT 4*. 2. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 5. Local works required to connect the User to the Melksham Operational Tripping Scheme as described in Appendix F3 of the Bilateral Connection Agreement. * Note: Alternative running arrangements to be discussed and arranged as per Appendix N | 20/05/2025
|  | CS-07113 | BAYWA R.E. UK LIMITED | Mannington 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 20/05/2025
Mannington Tertiary | PRO-000464 | CS-05918 | MANNINGTON ENERGY CENTRE LIMITED | Mannington 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 30/10/2025
|  | CS-08086 | MANNINGTON ENERGY CENTRE LIMITED | Mannington 400kV Substation | 100298-200724 | Re-conductor Fleet - Lovedean OHL circuits to increase capacity. | 30/10/2025
|  | CS-08087 | MANNINGTON ENERGY CENTRE LIMITED | Mannington 400kV Substation | 033773-033773 | Thermal uprating of Bramley - Fleet OHL circuits to increase capacity. | 30/10/2025
|  | CS-05917 | MANNINGTON ENERGY CENTRE LIMITED | Mannington 400kV Substation | 102051-204221 | 1. Installation of a new 150MVA-rated 400/33kV SGT including HV and LV bays 2. Establish a new single busbar 33kV substation at Mannington to be connected via the new 400/33kV SGT. 3. Installation of an earthing transformer connecting onto the 33kV busbar 4. Local works required to connect the User to the Melksham Operational Tripping Scheme as described in Appendix F3 of the Bilateral Connection Agreement | 30/10/2025
Manor Farm Solar Park | PRO-002337 | CS-08903 | CSE42 LIMITED | Fawley GSP | 102141-204346 | Installation of a 4th 240MVA 400/132kV SGT at Fawley 400kV. | 24/10/2036
MARCHWOOD ENERGY STORAGE | PRO-002190 | CS-07890 | Penso Power Limited | Marchwood 400kV Substation | 033773-033773 | Upgrade the Bramley - Fleet 1 &amp; 2 Circuits to achieve a post-fault winter rating of 3180 MVA | 14/11/2031
|  | CS-07893 | Penso Power Limited | Marchwood 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 14/11/2031
|  | CS-07897 | Penso Power Limited | Marchwood 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 14/11/2031
|  | CS-07889 | Penso Power Limited | Marchwood 400kV Substation | 101996-204131 | 1. Extend the main and reserve busbars at Marchwood 400kV Substation to accommodate the new User bay | 14/11/2031
|  | CS-07895 | Penso Power Limited | Marchwood 400kV Substation | 101033-202065 | Installation of stability OTS for the South West, driven by multiple generation customers | 14/11/2031
|  | CS-07892 | Penso Power Limited | Marchwood 400kV Substation | 101387-202718 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 14/11/2031
|  | CS-07894 | Penso Power Limited | Marchwood 400kV Substation | 101562-203112 | Reconductor Taunton - Exeter 1 & 2 400kV circuits (2 x 500mm2 Rubus at 75oC) with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MV | 14/11/2031
|  | CS-07896 | Penso Power Limited | Marchwood 400kV Substation | 100298-200724 | Uprate Fleet - Lovedean 1 &amp; 2 Circuits to provide a post fault winter rating of 3140MVA. | 14/11/2031
|  | CS-07891 | Penso Power Limited | Marchwood 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 1990MVA | 14/11/2031
MARES | PRO-000978 | CS-05924 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32030 | Uprate the two Quad Boosters at Legacy to 2750MVA. | 30/11/2028
|  | CS-05925 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32029 | Reconductor the Legacy legs of the Deeside - Trawsfynydd - Legacy circuits with GAP conductor. Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor. | 30/11/2028
|  | CS-05926 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32028 | Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor. | 30/11/2028
|  | CS-05927 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-11076 | Reconductor Ironbridge - Rugely circuit with 2 x 570 AAAC conductors. | 30/11/2028
|  | CS-05928 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32014S2 | Install two MSCDN's at Connah's Quay. | 30/11/2028
|  | CS-05929 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32281 | Establish one unpopulated skeletal generator bay in the Pentir 400kV GIS substation. | 30/11/2028
|  | CS-05930 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32372LI | Increase thermal rating of Carrington - South Manchester circuit. | 30/11/2028
|  | CS-05931 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32373LI | Reconductor Connah's Quay - Daines circuit with London. | 30/11/2028
|  | CS-05932 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32374LI | Increase thermal rating of Cellarhead - Daines cable. | 30/11/2028
|  | CS-05919 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-30915 | Design, construct and commission a 2.5GW capacity VSC HVDC link from Wylfa to Pembroke comprising of a 2.5GW VSC based HVDC converter station local to the company's owned Wylfa 400kV substation in North Wales, a 2.5GW VSC based HVDC converter station local to the company's owned Pembroke 400kV substation in South Wales and a 2.5GW capacity HVDC linking the converter stations at Wylfa and Pembroke. | 30/11/2028
|  | CS-05920 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32014S1 | Install two new MSCDN's at Ironbridge 400kV substation. | 30/11/2028
|  | CS-05921 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32014S3 | Install two MSCDN's at Legacy 400kV. | 30/11/2028
|  | CS-05922 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32021 | Reconductor the Cellarhead - Drakelow 400kV circuit with 2 x 620mm² GZTACSR. | 30/11/2028
|  | CS-05923 | MARESCONNECT LIMITED | Bodelwyddan 400kV Substation | NGET-RI-32022 | Increase the thermal capability of the existing South Manchester - Bredbury 275kV circuit. | 30/11/2028
Margree Wind Farm | PRO-001789 | CS-04779 | ENERGYFARM UK MARGREE LLP | Quantans Hill 132kV | SPT-RI-2243 | Glenshimmeroch 132/33kV substation transformer | 31/10/2027
|  | CS-04781 | ENERGYFARM UK MARGREE LLP | Quantans Hill 132kV | SPT- RI- 213 | New Cumnock 275/132kV transformer SGT2B | 31/10/2027
|  | CS-04782 | ENERGYFARM UK MARGREE LLP | Quantans Hill 132kV | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 31/10/2027
|  | CS-04783 | ENERGYFARM UK MARGREE LLP | Quantans Hill 132kV | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 31/10/2027
|  | CS-04784 | ENERGYFARM UK MARGREE LLP | Quantans Hill 132kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 31/10/2027
|  | CS-04785 | ENERGYFARM UK MARGREE LLP | Quantans Hill 132kV | SPT-RI-274 | Glenshimmeroch Collector Substation - On the New Cumnock / Blackcraig 132kV circuit, installation of a 132kV circuit breaker and associated disconnectors at Glenshimmeroch Collector Substation in South West Scotland. | 31/10/2027
|  | CS-04786 | ENERGYFARM UK MARGREE LLP | Quantans Hill 132kV | SPT-RI-296 | Glenshimmeroch collector substation 132kV overhead line uprating - Due to an increase in the generation contracted in the area, it is proposed to uprate a section of the overhead line between the proposed Glenshimmeroch collector substation to the cable end on the New Cumnock 132kV circuit. This is approximately 11km. This will be achieved by replacing the existing UPAS conductor with LARK conductor on the existing wood pole system. | 31/10/2027
McQuittiston Farm | PRO-004049 | CS-09265 | SP Distribution plc | Coylton GSP | SPT-RI-224 | At Coylton substation, the existing SGT1 and SGT2 275/132kV 120MVA transformers will be replaced (on line) with 240MVA units. | 29/05/2026
|  | CS-09266 | SP Distribution plc | Coylton GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 29/05/2026
Meadaple Wind Farm | PRO-000677 | CS-05933 | Scottish Hydro Electric Power Distribution Plc | Rothienorman GSP | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 01/06/2021
Medway 3 Power Station | PRO-002578 | CS-08556 | MEDWAY POWER LIMITED | Grain 400kV Substation | 102481-205063 | 1. Facilitate the connection of the generator bay at Kingsnorth 400kV AIS substation. 2. Modification / upgrade to substation control system (SCS) and protection and control systems at the Kingsnorth 400kV substation. | 31/12/2030
Meetlaw BESS | PRO-001966 | CS-07371 | CARRAVINDOON LIMITED | Fiddes GSP | Fiddes SS | 0 | 31/10/2028
|  | CS-07372 | CARRAVINDOON LIMITED | Fiddes GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 31/10/2028
|  | CS-07373 | CARRAVINDOON LIMITED | Fiddes GSP | Fiddes circuit breakers | 0 | 31/10/2028
Meiklelaught Farm BESS | PRO-003631 | CS-09657 | GPC 1127 LTD | Saltcoats 132kV Substation | SPT-RI-3185 - KILW-HUNF-HUNE No.2 Cable Replacement | KILW-HUNF-HUNE No.2 Cable Replacement | 21/08/2028
|  | CS-09658 | GPC 1127 LTD | Saltcoats 132kV Substation | SPT-RI-2710 | BU Route OHL Reconductor - As part of RIIO-T2 asset modernisation a number of assets across the transmission network have been identified for replacement. This TORI captures the asset modernisation work that is scheduled to be carried out on the 132kV OHL BU Route which runs between KILW-HUNF-HUNE at ~13km. The OHL circuit will be reconductored to achieve a minimum of 220MVA per circuit (Reconductor with 425mm2 ‘Totara’ AAAC @ 75°C) | 21/08/2028
|  | CS-09656 | GPC 1127 LTD | Saltcoats 132kV Substation | SPT-RI-3052 - CE Route No.2 Circuit Reconductoring and HUNE?SACO-KILW Cable Rep. | CE Route No.2 Circuit Reconductoring and HUNESACO-KILW Cable Replacement | 21/08/2028
Melksham | PRO-001605 | CS-06864 | IGP SOLAR 15 LIMITED | Melksham 400kV Substation | 033769-033769 | Reconductor the Exeter – Hinkley Point – Taunton 400kV circuits to achieve a pre-fault summer rating of 3100MVA. | 31/07/2029
|  | CS-06860 | IGP SOLAR 15 LIMITED | Melksham 400kV Substation | 101463-202903 | Double busbar extension at Melksham 400kV Substation to provide space for The User’s Generator Bay. | 31/07/2029
|  | CS-06861 | IGP SOLAR 15 LIMITED | Melksham 400kV Substation | 101033-202065 | Extension of the existing Melksham Operational Tripping Scheme | 31/07/2029
|  | CS-06862 | IGP SOLAR 15 LIMITED | Melksham 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 1990MVA | 31/07/2029
|  | CS-06863 | IGP SOLAR 15 LIMITED | Melksham 400kV Substation | 020903-020903 | Uprating of the Cowley - Minety 400kV cable to achieve a pre-fault summer rating of at least 1233MVA. | 31/07/2029
Melksham (Tertiary) | PRO-000463 | CS-05939 | MELKSHAM CALNE GREEN LIMITED | Melksham 400kV Substation | 100651-201330 | Install an earthing transformer on the 13kV tertiary connection Install a 13kV cable connecting earthing transformer to Disconnecting Circuit Breaker (DCB) Install a 72.5kV, 40kA rated Disconnecting Circuit Breaker (DCB) to connection assets for the User’s connection | 30/10/2022
|  | CS-06865 | MELKSHAM CALNE GREEN LIMITED | Melksham 400kV Substation | 030752-030752 | Creation of a new Melksham Operational Tripping Scheme | 30/10/2022
Melksham BESS & PV | PRO-002441 | CS-08900 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 15/10/2037
|  | CS-08897 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 101065-202138 | Uprate A83A & A873 Melksham – Minety 1 & 2 400kV circuits 28km, 2x500mm2 Rubus at 85oC on L2 towers with summer pre-fault rating of 1568MVA by reconductoring with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 15/10/2037
|  | CS-08898 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 101497-202952 | Uprate the Melksham – Seabank leg of Melksham – Seabank – Sandford (future Melksham – Folly Farm and Folly Farm – Seabank leg of Folly Farm – Seabank – Sandford) 400kV circuit by hotwiring the existing 4x400mm2 Zebra at 50oC section to 75oC to achieve a summer pre-fault rating of 2500MVA and reconductoring the existing 2x700mm2 Araucaria conductor with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 15/10/2037
|  | CS-08895 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 101051-202109 | Uprate A861 Walham-Cowley (future Walham-Botley West & Botley West – Cowley) 400kV circuit overhead line sections by reconductoring the 19.2km, 2x500mm2 Rubus at 75oC on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 61.7km, 4x400mm2 Zebra conductor at 50oC on L6 towers with summer prefault rating of 1862MVA to 75oC to achieve a summer pre-fault rating of 2500MVA | 15/10/2037
|  | CS-08892 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 102270-204632 | Turn in the Minety – Melksham circuit No 1. into the new Melksham B 400kV substation (new substation name to be confirmed) Construction of a new 4 bay 400kV double busbar substation called Melksham B 400kV substation (new substation name to be confirmed) consisting of 2 feeder bays, 1 User bay and 1 bus coupler bay | 15/10/2037
|  | CS-08896 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 102093-204284 | Uprate A844 Minety – Cowley 400kV circuit overhead line sections by reconductoring the 0.6km, 2x500mm2 Rubus at 75°C on L2 towers with summer pre-fault rating of 1438MVA section with 2x772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA, and hotwiring the 99.5km, 4x400mm2 Zebra conductor at 50°C on L6 towers with summer pre-fault rating of 1862MVA to 75°C to achieve a summer pre-fault rating of 2500MVA | 15/10/2037
|  | CS-08893 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 100424-200970 | Uprate the Bramley - Melksham 1 & 2 400kV circuits (81.6km, 2 x 400mm2 zebra conductor at 50oC on L2 towers with summer prefault rating of 931MVA) by reconductoring with 2 x 772mm2 Warwick conductor at 150°C to achieve a summer pre-fault rating of 2680MVA | 15/10/2037
|  | CS-08894 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 020903-020903 | Uprate the Cowley – Walham and Cowley - Minety 400kV circuits cable sections (2.1km, with a summer pre-fault rating of 877MVA) to achieve a summer pre-fault rating of at least 2222MVA | 15/10/2037
|  | CS-08899 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 102087-204278 | Uprate A87D Imperial Park – Melksham (future Imperial Park – Folly Farm – Melksham) 400kV circuit cable section (3.9km, with a summer pre-fault rating of 1424MVA) to a summer pre-fault rating of at least 1621MVA | 15/10/2037
|  | CS-08901 | ELEMENTS GREEN LIMITED | Melksham 400kV Substation | 102094-204287 | Installation of a new 200MVAr mechanically switched capacitor bank (MSC) at either Minety 400kV or Melksham 400kV Substation for pre-fault voltage compliance | 15/10/2037
Melvich Wind Energy Hub | PRO-001688 | CS-04627 | Melvich Wind Energy Hub Limited | Melvich Community Wind Farm 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2028
|  | CS-04628 | Melvich Wind Energy Hub Limited | Melvich Community Wind Farm 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/10/2028
|  | CS-04629 | Melvich Wind Energy Hub Limited | Melvich Community Wind Farm 132/33kV Substation | SHET-RI-106b | Connagil 2nd SGT – At Connagil substation, install a 2nd 275/132kV 120/240MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit. (SHET-RI-106b) | 31/10/2028
|  | CS-04630 | Melvich Wind Energy Hub Limited | Melvich Community Wind Farm 132/33kV Substation | SHET-RI-168 | Melvich to Connagill 132kV Connection - Install a new 132kV single circuit between a new 132kV switching station at Melvich Community wind farm 132/33kV substation and Connagill 275/132kV substation. | 31/10/2028
Menter Mon Morlais Anglesey Marine Energy | PRO-001134 | CS-04066 | MENTER MON CYF | Penrhos GSP | 30309 | Install Series Compensation at Pentir 400 kV substation | 31/03/2028
|  | CS-04067 | MENTER MON CYF | Penrhos GSP | 30310 | Installation of a second Wylfa – Pentir double circuit | 31/03/2028
|  | CS-04068 | MENTER MON CYF | Penrhos GSP | 30311 | Establish a second Pentir – Trawsfyndd circuit and its associated schemes which includes uprating the overhead line and cable sections, and building of Bryncir substation [30311] Uprating of Pentir – Bodelwyddan – Connah’s Quay double circuit | 31/03/2028
|  | CS-04069 | MENTER MON CYF | Penrhos GSP | 33642 | Installation of a 400/132 kV Super Grid Transformer (SGT) at Wylfa 132 kV substation, procure land and extend Wylfa 400 kV substation for this new SGT | 31/03/2028
|  | CS-04070 | MENTER MON CYF | Penrhos GSP | 33815 | Installation of a CAP76 Category 1 and 3 system to generator operational intertrip. Extensions to Reserve Busbar 1 at Wylfa 132 kV Substation. Install equipment on the spare skeletal feeder bay at Wylfa 132 kV Substation to facilitate connection. Busbar protection and substation control system modifications as required at Wylfa 132 kV Substation. Installation of a CAP76 Category 2 system to generator operational intertrip. Installation of a 400/132 kV Super Grid Transformer (SGT) at Wylfa 132 kV substation, procure land and extend Wylfa 400 kV substation for this new SGT | 31/03/2028
Mererid Offshore Wind Farm | PRO-002391 | CS-08147 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 102279-204533 | Infrastructure works for the generation connection of Mererid Offshore wind farm. | 06/12/2036
|  | CS-08153 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-08155 | South West Wind Holdco Limited | Alverdiscott 400kV Substation |  | FALSE | 06/12/2036
|  | CS-08154 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 06/12/2036
|  | CS-08148 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 06/12/2036
|  | CS-08150 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
|  | CS-08151 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 06/12/2036
|  | CS-08149 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-08152 | South West Wind Holdco Limited | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
Merlin Offshore Wind Farm | PRO-001728 | CS-04764 | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 01/11/2028
|  | CS-04765 | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101562-203112 | Reconductor both circuits between Taunton and Exeter 400kV substations in order to achieve a post-fault Summer rating of 2470MVA. | 01/11/2028
|  | CS-04766 | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 01/11/2028
|  | CS-04767 | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Hinkley Point - Exeter 400kV circuits to achieve a 3100MVA post fault winter rating. Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating | 01/11/2028
|  | CS-04768 | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101364-202684 | Install a smart wire power control device on the Feckenham - Minety circuit to mitigate to 1431MVA pre-fault Summer rating. | 01/11/2028
|  | CS-04769 | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 01/11/2028
|  | CS-04770 | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 01/11/2028
|  | CS-04762 | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101549-203089 | Infrastructure works for the connection of the Merlin offshore wind farm connecting into the Alverdiscott 400kV substation. | 01/11/2028
|  | CS-04763 | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 01/11/2028
MeyGen Tidal | PRO-000336 | CS-04447 | MEYGEN PLC | Gills Bay GSP | SHET-RI-028 Thurso to Gills Bay | Gills Bay – Thurso South 132kV Double Circuit - It is proposed to construct a new 132kV GIS double busbar arrangement substation at a suitable location around Gills Bay (west of John O’Groats) and connect in two OHL radial circuits from Thurso south. (SHET-RI-028). | 01/04/2027
|  | CS-05940 | MEYGEN PLC | Gills Bay GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 01/04/2027
|  | CS-05941 | MEYGEN PLC | Gills Bay GSP | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 01/04/2027
|  | CS-05942 | MEYGEN PLC | Gills Bay GSP | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 01/04/2027
|  | CS-05943 | MEYGEN PLC | Gills Bay GSP | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 01/04/2027
|  | CS-05944 | MEYGEN PLC | Gills Bay GSP | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 01/04/2027
Mickleham Energy Storage | PRO-003573 | CS-08528 | Penso Power Limited | Rowdown 400kV Substation | 102529-205129 | Rebuild of 400kV Rowdown substation as a Double Busbar substation, to accommodate the users generator bay, and associated works including the reconfiguration of the existing Circuits so that they connect into the new Double Busbar Substation. | 22/10/2031
Middleton BESS | PRO-002305 | CS-07449 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor. | 30/11/2026
|  | CS-07450 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 30/11/2026
|  | CS-07451 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 400kV circuits and the Cellarhead – Macclesfield and Cellarhead – Drakelow 400kV circuits | 30/11/2026
|  | CS-07452 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101466-202906 | Reconductor the existing 2x570mm2 conductor on the CellarheadDaines 1 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2800 MVA | 30/11/2026
|  | CS-07453 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm2 conductor | 30/11/2026
|  | CS-07454 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 30/11/2026
|  | CS-07455 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 30/11/2026
|  | CS-07443 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101603-203226 | 0 | 30/11/2026
|  | CS-07444 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 30/11/2026
|  | CS-07445 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101468-202908 | Reconductor the Daines – Macclesfield 400kV with 2x780mm2 conductor | 30/11/2026
|  | CS-07446 | Middleton Energy Storage Limited | Middleton 400KV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/11/2026
|  | CS-07447 | Middleton Energy Storage Limited | Middleton 400KV Substation | 100425-200971 | Reconductor the Feckenham – Ironbridge 400kV circuit with 2x620mm2 conductor | 30/11/2026
|  | CS-07448 | Middleton Energy Storage Limited | Middleton 400KV Substation | 101278-202528 | Reconductor the Legacy legs of both Connah’s Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor. | 30/11/2026
Midlands Estate Energy Park | PRO-001945 | CS-07225 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 31/10/2029
|  | CS-07220 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 31/10/2029
|  | CS-07221 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 31/10/2029
|  | CS-07222 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 31/10/2029
|  | CS-07223 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 31/10/2029
|  | CS-07224 | Renewable Energy Systems Limited | West Burton 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 31/10/2029
|  | CS-07190 | Renewable Energy Systems Limited | West Burton 400kV Substation | 030613-030613 | Reconductor the 2x500mm2 Rubus sections of the Cottam – Staythorpe 1 400kV circuit with 2x700mm2 Araucaria conductor. | 31/10/2029
|  | CS-07191 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100450-201015 | Uprate the Cottam - Keadby 1 and 2 circuits to achieve a post fault winter rating of 3300MVA to match the 6hr rating of the QB's on the same circuits. | 31/10/2029
|  | CS-07186 | Renewable Energy Systems Limited | West Burton 400kV Substation | 101779-203571 | Extension of 400kV West Burton substation for provision of one user generation bay. | 31/10/2029
|  | CS-07187 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100451-201016 | Reconductor the 2x500mm2 sections of the High Marnham – West Burton 400kV circuit with 2x570mm2 conductor and replace the cable section. | 31/10/2029
|  | CS-07188 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100459-201024 | Reconductor the 2x500mm2 section of the High Marnham – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 31/10/2029
|  | CS-07189 | Renewable Energy Systems Limited | West Burton 400kV Substation | 100590-201212 | Reconductor the 2x500mm2 sections of the Ratcliffe – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 31/10/2029
Mid Moile Wind Farm | PRO-004036 | CS-09851 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 31/10/2031
|  | CS-09854 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-2877 OHL | West Coast Onshore Reinforcement (Southern Section) - Construct a new 400kV double circuit OHL using L13 / L12X towers and a triple Araucaria conductor bundle from Dumfries North substation to the SPT/NGET border which is approximately 36km away. NGET shall then complete the circuit from the border to an appropriate substation. The Network Options Assessment (NOA7) Refresh identified the need to develop a new west coast onshore high capacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. | 31/10/2031
|  | CS-09855 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3176 - Kilmarnock South to West Coast HVDC Bussing Station | Install a 2GW HVDC link from Kilmarnock South 400kV substation to the South Ayrshire 525kV HVDC bussing station located in southwest Scotland. The DC bussing station to facilitate a multi terminal HVDC arrangement between Kilmarnock South, Machair Wind and a southern converter station located in NGET. | 31/10/2031
|  | CS-09857 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3309 | New Cumnock North 400kV GIS substation- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new 400kV substation in the vicinity of the existing New Cumnock 275kV substation. This shall be a double busbar GIS ‘New Cumnock North’ 400kV substation. This new substation shall facilitate the development of the NOA WCNC scheme (currently under review) | 31/10/2031
|  | CS-09860 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3461 - Mark Hill North 400/275kV Substation | To alleviate the thermal overloading associated with YY route, it is proposed to reinforce the South West Scotland network by creating 400kV power corridors between New Cumnock and the proposed South Ayrshire HVDC Converter station. As part of these works, a new 400/275kV substation will be established within the vicinity of the existing Mark Hill 275kV substation. The new Mark Hill North Substation shall comprise of a 400kV double busbar substation as well as a new 275kV double busbar substation, these will be connected via three 400/275kV Supergrid Transformers. | 31/10/2031
|  | CS-09852 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-2862 SS | Dumfries North 400kV Substation - Create a new 400kV substation named Dumfries North 400/132kV substation which shall connect into both sides of the new 400kV OHL double circuit proposed under SPT-RI-2877. The substation shall consist of two new double busbar AIS bays for the WCNC Route circuits, a double busbar AIS bay for the Craig Moss Farm connection, a 400kV AIS bus coupler and a 400kV bus section | 31/10/2031
|  | CS-09847 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3558 - L48 Glen App Collector Substation | To accommodate generation into Auchencrosh 275kV substation, it is proposed to establish a the L48 Glen App Collector substation. At Auchencrosh substation, install a 275kV feeder bay. From there, install approximately 0.5km of 275kV UGC to the collector substation. At the L48 Glen App Collector substation, install a 275kV single busbar with one 275kV feeder bay. | 31/10/2031
|  | CS-09849 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3560 - COYL-CARR-MAHI-AUCC LMS Scheme | IED’s will be installed at the Carrick 275kV substation and Auchencrosh 275kV substation to monitor the circuit loading along YY Route. Should any of the relevant YY Route circuit sections detailed in the below table be overlaoded, a trip signal will be sent to relevant generators. | 31/10/2031
|  | CS-09850 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 31/10/2031
|  | CS-09859 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3452 - Mark Hill North - New Cumnock North 400kV Circuit | To alleviate the thermal overloading associated with YY route, it is proposed to reinforce the South West Scotland network by creating 400kV power corridors between New Cumnock and the proposed South Ayrshire HVDC Converter station. As part of these works, a new 400kV double circuit will be established between the Mark Hill North 400kV substation (developed under SPT-RI-3461) and New Cumnock North 400kV substation (developed under SPT-RI3309). | 31/10/2031
|  | CS-09862 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3463 - Mark Hill North – South Ayrshire HVDC Bussing Station | It is proposed to establish a new HVDC Converter station at the proposed South Ayrshire HVDC Bussing Station established under SPT-RI-3176 Kilmarnock South – West Coast HVDC Bussing Station. This new converter station will provide an interface between the SPT South-West Ayrshire network and the West Coast HVDC link proposed under HNDFUE. A new 400kV power corridor will be established between the new HVDC converter station and the proposed Mark Hill North substation established under SPT-RI-3461 Mark Hill North 400/275kV substation. | 31/10/2031
|  | CS-09848 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3559 - COYL-CARR-MAHI Intertrip Scheme | IED’s will be installed at the Coylton 275kV substation, Carrick 275kV substation and Mark Hill 275kV substation to monitor the status of the 275kV circuit breakers installed along YY Route. Should any of the relevant circuit breakers detailed in the below table open, a trip signal will be sent to relevant generators. | 31/10/2031
|  | CS-09853 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-2876 - West Coast Onshore Reinforcement (North Section | Under the NOA7 Refresh the need was identified to develop a new west coast onshore highcapacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. This project is driven by the continued increase in required transfers seen across this boundary due to the need to connect renewable generation in Scotland to achieve UK and Government’s net zero target by 2050 and 2045 respectively. To facilitate generation applications in this area it is proposed to utilise this new west coast onshore corridor. This TORI shall construct a new Killoch 400kV substation to feed a new Killoch 275kV substation via three new 400/275kV SGT’s, diversion and 400kV uprating of the existing XY route between Kilmarnock South and the new Killoch 400kV substations and the 400kV uprating of the WA route between the new Killoch 400kV and New Cumnock North 400kV substations. | 31/10/2031
|  | CS-09856 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3178 - West Coast HVDC Bussing Station to NGET | Install a 4GW HVDC link from the South Ayrshire 525kV HVDC bussing station to a southern converter station within the NGET licensed area. The costs associated with this SPT reinforcement instruction are associated with the installation of the HVDC cable system from the DC bussing station to the Scotland-England maritime boundary. | 31/10/2031
|  | CS-09858 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3315 | New Cumnock North to Glenmuckloch 400kV OHL- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new double circuit OHL between (the proposed) New Cumnock North and Glenmuckloch 400kV substation. The scope of works shall consist of 2 stages: Stage 1 – establishment of a new double circuit OHL (L8 with Twin RUBUS conductor is proposed) from New Cumnock North towards Glenmuckloch. One side of the circuit shall be energised in this stage to provide a minimum scope required to enable a connection of New Cumnock BESS. Stage 2 – establishment of a second double busbar GIS switchgear bays at New Cumnock North 400kV substation to connect to the OHL No.1 circuit | 31/10/2031
|  | CS-09861 | ENERGIEKONTOR UK LTD | Arecleoch 132kV Substation | SPT-RI-3498 - Glenmuckloch 400kV - Dumfries North 400kV | Under the NOA7 Refresh the need was identified to develop a new west coast onshore highcapacity corridor over the B6 boundary between Scotland and England to increase the transfer capability across this transmission boundary. This project is driven by the continued increase in required transfers seen across this boundary due to the need to connect renewable generation in Scotland to achieve UK and Government’s net zero target by 2050 and 2045 respectively. To facilitate generation applications in this area it is proposed to utilise this new west coast onshore corridor. The TORI shall construct a new 400kV double circuit between the proposed Glenmuckloch 400kV substation (established under SPT-RI-236) and the proposed Dumfries North 400kV substation (established under SPT-RI-2862). It is proposed to string both sides of the 400kV corridor with 3x700mm2 Araucaria AAAC conductor provisionally rated at 750C with the capability to uprate the operating temperature to 900C. | 31/10/2031
Millbrook Power | PRO-000373 | CS-05948 | MILLBROOK POWER LIMITED | Marston Vale 400kV Substation | 100023-200046 | Construct a double busbar 400kV substation in the vicinity of tower ZA378 comprising of 2 feeder bays, 1 busbar coupler bay and space to accommodate the User bay. Establish a double tee connection between the new 400kV substation and the Grendon – Sundon 400kV double circuit. | 28/06/2024
Millennium South | PRO-000311 | CS-05949 | RENANTIS UK LIMITED | Millennium South 132/33kV Substation | Millennium South Item 1 | 1. The enabling works associated with the new 132/33kV substation adjacent to structure 39 of the Fort Augustus – Skye 132kV trident wood pole line (FQ1) will include the following: a. Modify structure 39 of the Fort Augustus – Skye 132kV trident wood pole line (FQ1) and erect a new terminal tower and down droppers to the new substation compound; b. Install 2 x 132kV line disconnectors (103 and 203) along with associated support structures within the substation compound. Disconnectors 103 and 203 to be located on either side of the single teed 132kV infeed to the substation. c. Install 1 x 132kV transformer circuit switcher (115), along with support structures within the substation compound. d. Provide a double 132kV tapping from either side of structure 39 to two new wood pole terminal structures located adjacent to the tower, and then extend two short trident lines over 3 – 5 spans to the new 132/33kV substation to establish a looped connection to the substation off the FFW circuit. e. Modify the existing protection and telecommunication equipment at Fort Augustus 132kV substation to suit the new teed connection at Millennium South. | 31/10/2021
|  | CS-05950 | RENANTIS UK LIMITED | Millennium South 132/33kV Substation | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 31/10/2021
|  | CS-05951 | RENANTIS UK LIMITED | Millennium South 132/33kV Substation | SHET-RI-044 | Install a new 132kV OHL between Fort Augustus 132kV double busbar and SkyeTee. Connect the new 132kV OHL to a new 132kV circuit breakers at Fort Augustus. New 132kV Overhead line to be approximately 9km and to have a minimum rating equivalent to an ACSR lynx conductor at 50°C. Reinstate existing overhead line between Fort Augustus and Fort William. Modify any protection settings at Fort Augustus and Fort William for new arrangement. | 31/10/2021
Millfield Lane BESS & Solar | PRO-002586 | CS-08616 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 30/10/2037
|  | CS-08594 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 102505-205103 | Provide a double turn in of the 400kV circuits between Sundon & Leighton Buzzard to the new Relevant Transmission License’s 400kV Dunstable (TBC) substation. Additional Busbar coupler, section breakers & 2 additional feeder bays to be added. Reconductor the quad zebra section with triple araucaria to achieve a summer pre-fault rating of 2786MVA | 30/10/2037
|  | CS-08621 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 101746-203470 | New network need from North Lincolnshire to Hertfordshire (NOA LRN4). | 30/10/2037
|  | CS-08617 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 101884-203860 | Reconductor the Enderby legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490MVA | 30/10/2037
|  | CS-08600 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 30/10/2037
|  | CS-08593 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 102362-204787 | Construction of a new 400kV AIS double busbar Dunstable substation between Sundon 400kV and Leighton Buzzard 400kV substations, comprising a busbar coupler, 2 feeder bays and User generator bay. | 30/10/2037
|  | CS-08597 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 101248-204325 | Add a new bus coupler and three new bays at Wymondley 400kV substation to facilitate the turn-in of the existing Pelham to Sundon 400kV circuit at Wymondley 400kV substation | 30/10/2037
|  | CS-08599 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 30/10/2037
|  | CS-08602 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 101885-203861 | Reconductor MILLBROOK-SUNDON 4-1 (MILB4-SUND4-1) & MILLBROOK-SUNDON 4-2 (MILB4-SUND4-2) 400kV circuit to achieve more than 1605MVA summer pre-fault rating | 30/10/2037
|  | CS-08614 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 101245-202485 | Reconductor the existing 4x400mm2 conductor on the Eaton Socon – Wymondley 2 400kV circuit with 2x850mm2 90oC conductor to achieve a pre fault summer rating of 2400 MVA | 30/10/2037
|  | CS-08618 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 30/10/2037
|  | CS-08601 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 101316-202621 | Hotwire A881 East Claydon – Cowley 400kV circuit (36.3km, 4x400mm2 zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 30/10/2037
|  | CS-08620 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 30/10/2037
|  | CS-08596 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 102012-204166 | 4. At Rye House 400kV: Replace circuit breakers X130. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2037
|  | CS-08595 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 101927-203938 | At Sundon 400kV: Replace circuit breakers X130, X510 and X710. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2037
|  | CS-08622 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 102272-204627 | Construction of a new 400kV double circuit from the Bramley area to the Slough area (route TBC) | 30/10/2037
|  | CS-08592 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 102600-205220 | Extend the busbars and associated P&C and LVAC to facilitate the User's feeder bay. | 30/10/2037
|  | CS-08619 | Chiltern Renewables Millfield Limited | Sundon 400kV Substation | 033461- 033461 | Post-completion of BTNO works, reconductor Bramford-Pelham 1 400kV circuits with 3 x700mm2 AAAC conductors to achieve a post-fault winter rating of 3100 MVA | 30/10/2037
Milligansbush Battery Storage | PRO-003430 | CS-09655 | Milligansbush Battery Storage Ltd | Milligansbush Battery Storage 132kV Substation | SPT-RI-231 | 0 | 30/10/2036
Millmoor Rig Wind Farm | PRO-001936 | CS-07229 | ESB ASSET DEVELOPMENT UK LIMITED | Hawick GSP | Millmoor Rig Wind Farm Enabling Works | 1. Installation of a 132kV line disconnector at the Millmoor Rig Windfarm 132kV substation 2. Installation of a 132kV circuit between Millmoor Rig Windfarm 132kV substation and Hawick 132kV substation. This circuit is approximately 17km in length. 3. Installation of a new 132kV circuit breaker and associated disconnectors at Hawick 132kV substation. 4. Extension of the Hawick 132kV substation platform | 30/10/2029
|  | CS-07230 | ESB ASSET DEVELOPMENT UK LIMITED | Hawick GSP | NGET - 101268-202511 | Rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. (NGET - 101268-202511) | 30/10/2029
|  | CS-07231 | ESB ASSET DEVELOPMENT UK LIMITED | Hawick GSP | SPT-RI-288 Hawick to Galashiels 132kV Reconfiguration | Hawick 132/33kV substation is currently supplied via two 132kV circuits from Gretna 400/132kV substation, with a 132kV circuit to Galashiels normally open at CB 205. With the proposed connection of Faw Side wind farm (250MW) it is proposed to reconfigure Hawick 132kV substation such that Hawick can be supplied from Galashiels and establish the Hawick / Galashiels 132kV circuit No.1 and No.2. Works at Galashiels will be required to terminate the double circuit from Hawick post reconfiguration. At Hawick, it is also proposed to install two new 132kV circuit breakers and a fourth 132kV circuit at Hawick with Poplar conductor:. The existing circuit breakers at Galashiels are of 600A and 800A. It is also proposed to replace the 600A circuit breakers 120 and 620 with a standard 2000A circuit breaker. | 30/10/2029
|  | CS-07232 | ESB ASSET DEVELOPMENT UK LIMITED | Hawick GSP | NGET-101268-202520 | Uprating of two 132kV cross border OHL circuits (Chapel Cross-Harker and Gretna-Harker-Hawick.) The preferred option is the replacement of the existing conductor with a higher rated conductor. In addition, a third circuit will be created on the single circuit V route to create Gretna-Harker-Hawick 1 and 2. On connection of further customers in Scotland these circuits will eventually become Faw Side-Gretna-Harker 1 and 2. (NGET-101268-202520) | 30/10/2029
Mill Rig Wind Farm | PRO-000892 | CS-05946 | Mill Rig Wind Farm LLP | Kilmarnock South GSP | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 31/07/2024
|  | CS-05947 | Mill Rig Wind Farm LLP | Kilmarnock South GSP | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 31/07/2024
Milltown Airfield Solar Farm | PRO-001277 | CS-05952 | MILLTOWN AIRFIELD SOLAR PV LIMITED | Elgin GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 28/02/2025
|  | CS-05953 | MILLTOWN AIRFIELD SOLAR PV LIMITED | Elgin GSP | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 28/02/2025
|  | CS-05954 | MILLTOWN AIRFIELD SOLAR PV LIMITED | Elgin GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 28/02/2025
|  | CS-09512 | MILLTOWN AIRFIELD SOLAR PV LIMITED | Elgin GSP | SHET-RI-174 | Upgrade of Keith SGTs- Replace the existing 132/275kV 240MVA SGTs at Keith 132kV Substation with larger 480/360MVA units | 28/02/2025
|  | CS-09511 | MILLTOWN AIRFIELD SOLAR PV LIMITED | Elgin GSP | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 28/02/2025
Minety | PRO-000454 | CS-04481 | HB411MIN Limited | Minety 400kV Substation | 101488-202944 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays 3. Establish new bus bar, 33kV substation at Minety to be connected via new 400/33kV SGT8B 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 31/10/2024
Minety Tertiary (2) | PRO-000432 | CS-06866 | JBM SOLAR PROJECTS 14 LIMITED | Minety GSP | 101488-202944 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays 3. Establish new bus bar, 33kV substation at Minety to be connected via new 400/33kV SGT8B 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 30/10/2024
Moelfre Energy Park | PRO-001500 | CS-06502 | MOELFRE ENERGY PARK LIMITED | Bodelwyddan 400kV Substation | 101275-202518 | 1. At Bodelwyddan 400kV substation extend the site to make provision for a new generator bay. 2. Installation of a bus coupler on the newly extended busbar sections | 31/10/2026
|  | CS-06503 | MOELFRE ENERGY PARK LIMITED | Bodelwyddan 400kV Substation | 032281-202001 | 1. Extension of Bodelwyddan 400kV substation. | 31/10/2026
|  | CS-06504 | MOELFRE ENERGY PARK LIMITED | Bodelwyddan 400kV Substation | 100570-201374 | 2. Double turn-in of PENT-BODE-CONQ 1 & 2 circuits - PENT end of circuit 2 to utilise existing OHL between T and BODE s/s (GM line). New OHL to carry CONQ end of (PENT-BODECONQ) circuit 2 turn in, and circuit 1 T. Building of 2 new bays to accommodate additional circuits | 31/10/2026
Moel y Llyn | PRO-001585 | CS-04706 | Waun Hesgog Energy Park Limited | Chirk GSP | 101323-202636 | Overhead line works to connect a new nine bay substation to the transmission network via a double circuit turn in of the existing Legacy – Ironbridge and Legacy – Ironbridge/Shrewsbury circuits 400kV circuits. | 04/02/2027
|  | CS-04707 | Waun Hesgog Energy Park Limited | Chirk GSP | 101323-202637 | Installation of a new nine bay 400kV double busbar substation consisting of four feeder bays, one busbar coupler, one busbar section and three Supergrid Transformer (SGT) bays. | 04/02/2027
|  | CS-04708 | Waun Hesgog Energy Park Limited | Chirk GSP | 131323-202638 | Install and commission three Supergrid Transformer (SGT) bays at Chirk 400/132kV Substation. Install and commission switchgear at Chirk to include SGT HV and LV circuit breakers and associated bay assets. Install and commission three 240MVA rated 400/132kV SGTs. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 04/02/2027
|  | CS-04709 | Waun Hesgog Energy Park Limited | Chirk GSP | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 04/02/2027
|  | CS-04711 | Waun Hesgog Energy Park Limited | Chirk GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 04/02/2027
Moffat BESS | PRO-004654 | CS-09707 | Conrad Energy (Developments) II Limited | Moffat 400kV Substation | SPT-RI-231 | 0 | 31/10/2031
|  | CS-09708 | Conrad Energy (Developments) II Limited | Moffat 400kV Substation | SPT-RI-3423 | Moffat 400kV Single Busbar - Given the connection applications received in the Moffat area it is required to create a new shared 400kV busbar to accommodate two connections in this area. It is proposed to install a new 400kV double busbar bay and extend the substation platform accordingly to accommodate this. From here a new 400kV cable section shall be installed to a location where a new 400kV busbar section shall be created. The contingent connections shall then connect onto this new section of busbar/ | 31/10/2031
Mona Offshore Wind Farm | PRO-001391 | CS-06373 | Mona Offshore Wind Limited | Wylfa 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 01/04/2033
|  | CS-06368 | Mona Offshore Wind Limited | Wylfa 400kV Substation | 101070-202145 | Infrastructure works necessary to connect 1500MW at the Wylfa 400kV substation, for the Project Elizabeth R4 connection application | 01/04/2033
|  | CS-06369 | Mona Offshore Wind Limited | Wylfa 400kV Substation | 100974-201953 | Construct a second double circuit between Pentir 400kV substation and the Wylfa 400kV substation (circuits No. 3 & 4) | 01/04/2033
|  | CS-06370 | Mona Offshore Wind Limited | Wylfa 400kV Substation | 101072-202151 | Extend the current Wylfa 400kV substation to enable the connection of a new Pentir - Wylfa OHL. | 01/04/2033
|  | CS-06371 | Mona Offshore Wind Limited | Wylfa 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 01/04/2033
Monets Garden | PRO-001082 | CS-05990 | MONETS GARDEN BATTERY LTD | Osbaldwick 400kV Substation | 100655-201341 | 1. Install 13kV/33kV earthing transformer on 13kV tertiary connection at Osbaldwick 400/33kV substation. 2. Install 13kV circuit breaker on the 13kV side of the 13kV / 33kV transformer at Osbaldwick 400/33kV substation 3. Install 13kV disconnector on the 13kV side of the 13kV / 33kV transformer at Osbaldwick 400kV/33kV Substation 4. Install an auto-close scheme at Osbaldwick 400/33kV substation. | 30/10/2024
|  | CS-05991 | MONETS GARDEN BATTERY LTD | Osbaldwick 400kV Substation | 100655-201342 | Attributable | 30/10/2024
|  | CS-05992 | MONETS GARDEN BATTERY LTD | Osbaldwick 400kV Substation | 100655-201375 | Attributable | 30/10/2024
Monk Fryston | PRO-001646 | CS-04574 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101610-203236 | Uprate the the Carrington - Kearsley 400kV circuit with 2x700mm2 conductor | 31/12/2029
|  | CS-04575 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101509-202974 | Replace the existing Ferrybridge 275kV substation with a new substation, to be built offline with circuits from the existing substation being transferred to the new substation | 31/12/2029
|  | CS-04576 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101611-203237 | Hotwire the 2x400mm2 section of the Rochdale - Whitegate 1 275kV circuit to operate at 65°C. | 31/12/2029
|  | CS-04555 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101561-203104 | At Monk Fryston 275kV AIS Double Busbar Substation: 1) Facilitate the installation of generator bay (User Works). 2) Replace SGT1 400/275kV Interbus Transformer with a higher rated unit. | 31/12/2029
|  | CS-04556 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101561-203105 | Uprate the cables sections on: 1) Rochdale – Whitegate 2 275kV circuit 2) Kearsley – Whitegate 1 and 2 275kV circuits | 31/12/2029
|  | CS-04557 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101508-202973 | Replace circuit breakers S10 and L25 at Monk Fryston 275kV substation with a 40kA-rated circuit breaker tested to the appropriate X/R ratio | 31/12/2029
|  | CS-04558 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101561-203106 | On the Ferrybridge – Skelton Grange 2 275kV circuit, reconductor the 1x700mm2 section of the circuit with 1x772mm2 Warwick conductor or equivalent. | 31/12/2029
|  | CS-04559 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm2 sections with 2x620mm2 GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 31/12/2029
|  | CS-04560 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101561-203108 | On the Eggborough leg of the Eggborough – Stalybridge – Stocksbridge 400kV circuit, hotwire the 4x400mm2 sections to an operating temperature of 65°C. | 31/12/2029
|  | CS-04561 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm2 sections of the circuits between towers ZZC40R and ZZC002 and towers ZZC002 and ZZC001 (13,15km total) with 2x570 mm2 strung to an operating temperature of 75°C. The remaining 1.9km section between ZZC46R and ZZC40R which is already 2x570 mm2should be hotwired to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A continuous. | 31/12/2029
|  | CS-04562 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101612-203238 | Installation of a second interbus transformer at High Marnham 400/275kV substation | 31/12/2029
|  | CS-04563 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 31/12/2029
|  | CS-04564 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101511-202976 | Hotwire the 2x400mm2 section of the Elland – Stalybridge circuit between towers ZP127 and ZP183 (17.86km) to an operating temperature of 75°C | 31/12/2029
|  | CS-04565 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 31/12/2029
|  | CS-04566 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm2 cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm2 cable. | 31/12/2029
|  | CS-04567 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 31/12/2029
|  | CS-04568 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 031380-031380 | Hotwire the 4x400mm2 sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 31/12/2029
|  | CS-04569 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 31/12/2029
|  | CS-04570 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 16 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 31/12/2029
|  | CS-04571 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 31/12/2029
|  | CS-04572 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 31/12/2029
|  | CS-04573 | IGP SOLAR 18 LIMITED | Monk Fryston 275kV Substation | 101041-202083 | Power Control technology along the Cottam – West Burton 1 (A413) 400kV circuit | 31/12/2029
| PRO-002159 | CS-08747 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101855-203810 | Reconductoring of Macclesfield to Stalybridge line (A23A) with 1590MVA pre-fault rating during Summer. | 31/10/2031
|  | CS-08745 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 033513-033513 | Uprate Keadby-West Burton 2 (4TM 1-81) with 3420MVA post-fault rating during Winter | 31/10/2031
|  | CS-08746 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101504-202965 | Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit to provide a post-fault winter rating of 3820MVA: • Reconductor the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C • At Keadby 400kV substation, replace the X1005 feeder bay for the Drax – Keadby – Thorpe Marsh circuit | 31/10/2031
|  | CS-08742 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101511-202976 | Hotwire the 2x400mm2 sections of the Elland – Stalybridge circuit 275kV to an operating temperature of 75°C | 31/10/2031
|  | CS-08744 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101610-203236 | Reconductor the 2x500mm2 sections of the Carrington – Kearsley circuit with 2x620mm2 GAP conductor | 31/10/2031
|  | CS-08749 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 31/10/2031
|  | CS-08750 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 31/10/2031
|  | CS-08735 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101899-204096 | Replace circuit breakers L85 and L45 at Monk Fryston 275kV with 40kA-rated circuit breaker tested to the appropriate X/R ratio | 31/10/2031
|  | CS-08739 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101616-203249 | Reconductor 400kV Drakelow to Hams Hall line from Rubus 500sqmm to Rubus 500sqmm at 90deg C to have summer pre fault rating of 1660MVA | 31/10/2031
|  | CS-08741 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm2 sections of the circuits with 2x570 mm2 strung to an operating temperature of 75°C. Hotwire the 2x570 mm2 sections to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A. | 31/10/2031
|  | CS-08748 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 100455-201020 | At Keadby 400kV substation: Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby –Thorpe Marsh 400kV circuit | 31/10/2031
|  | CS-08752 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 100171-200449 | Uprate the Thorpe Marsh – West Melton Circuit 2 to achieve a post fault summer rating of 1000MVA. | 31/10/2031
|  | CS-08734 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101899-203890 | Make provision for connection of generator bay at Monk Fryston new 400kV substation. | 31/10/2031
|  | CS-08736 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101508-202973 | Replace circuit breakers S10 and L25 at Monk Fryston 275kV substation with a 40kA-rated circuit breaker tested to the appropriate X/R ratio | 31/10/2031
|  | CS-08751 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 to achieve a post-fault winter rating of 1090MVA. | 31/10/2031
|  | CS-08738 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 033754-033755 | Establish a new Monk Fryston 400kV double busbar substation | 31/10/2031
|  | CS-08753 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 031380-031380 | Hotwire the 4x400mm2 sections of the Lackenby – Thornton 400kV 1 and 2 circuits for operation at 75°C. | 31/10/2031
|  | CS-08737 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 100161-200456 | Uprating of CB X120 at Eggborough 400kV substation to 63kA rating | 31/10/2031
|  | CS-08740 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 31/10/2031
|  | CS-08743 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101627-203263 | Cable uprate on the Kearsley - Whitegate 275 kV circuit 1 to achieve a pre fault summer rating of 400 MVA | 31/10/2031
|  | CS-08754 | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm2 sections with 2x620mm2 GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 31/10/2031
Monk Fryston BESS | PRO-001619 | CS-07341 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 101378-202699 | 0 | 31/10/2029
|  | CS-07342 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 101508-202973 - DUPLICATE | 0 | 31/10/2029
|  | CS-07343 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 31/10/2029
|  | CS-07344 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 100171-200448 | Uprating of the Thorpe Marsh – West Melton 1 circuit to cater for 1160/920 MVA post-fault (winter/summer), comprising: Uprating of the cable section | 31/10/2029
|  | CS-07345 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 101504-202965 | Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit to provide a post-fault summer rating of 3300 MVA:  Reconductor the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for the Drax – Keadby – Thorpe Marsh circuit. | 31/10/2029
|  | CS-07346 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 031380-031380 - DUPLICATE | 0 | 31/10/2029
|  | CS-07347 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 100449-201014 | Uprate the Drax – Eggbrough 1 circuit to achieve a post fault summer rating of 2500MVA | 31/10/2029
|  | CS-07348 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 31/10/2029
|  | CS-07349 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 033513-033513 | Hotwiring of the Keadby – West Burton 2 circuit to cater for 3100/2600 MVA post-fault (winter/autumn. | 31/10/2029
|  | CS-07350 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 100459-201024 | Reconductor the 2x500mm2 section of the High Marnham – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 31/10/2029
|  | CS-07351 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 100171-200449 | Uprating of the Thorpe Marsh – West Melton 1 circuit to cater for 1160/920 MVA post-fault (winter/summer), comprising: Reconductoring of the OHL section | 31/10/2029
|  | CS-07352 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm2 sections with 2x620mm2 GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 31/10/2029
|  | CS-07353 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 101561-203107 - DUPLICATE | 0 | 31/10/2029
|  | CS-07354 | HARMONY ENERGY LIMITED | Monk Fryston 275kV Substation | 033754-033755 - DUPLICATE | 0 | 31/10/2029
Monk Fryston Energy Park | PRO-002539 | CS-08868 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101508-202973 | Replace circuit breakers S10 and L25 at Monk Fryston 275kV substation with a 40kA-rated circuit breaker tested to the appropriate X/R ratio | 24/10/2035
|  | CS-08869 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 24/10/2035
|  | CS-08871 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 102080-204268 | Replant of Overton 275kV substation with higher rated equipment. | 24/10/2035
|  | CS-08876 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101610-203236 | Reconductor the 2x500mm2 sections of the Carrington – Kearsley circuit with 2x620mm2 GAP conductor | 24/10/2035
|  | CS-08877 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101561-203107 | On the Lackenby – Norton 400kV circuit reconductor the 2x500mm2 sections with 2x620mm2 GZTACSR conductor, and replace the cable section at Lackenby with a higher rated cable | 24/10/2035
|  | CS-08886 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100171-200449 | Uprate the Thorpe Marsh – West Melton Circuit 2 to achieve a post fault summer rating of 1000MVA. | 24/10/2035
|  | CS-08891 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 031380-031380 | Hotwire the 4x400mm2 sections of the Lackenby – Thornton 400kV 1 and 2 circuits for operation at 75°C. | 24/10/2035
|  | CS-08884 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 24/10/2035
|  | CS-08870 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 102208-204431 | Uprating of OHL double cct from 2TW110 - 2TW169 and 4YR1 - 4YR40 which is part of the current Norton-Osbaldwick double circuit but will become the new Osbaldwick-Overton-Thormanby circuit | 24/10/2035
|  | CS-08874 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101627-203263 | Cable uprate on the Kearsley - Whitegate 275 kV circuit 1 to achieve a pre fault summer rating of 400 MVA | 24/10/2035
|  | CS-08889 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 033513-033513 | Uprate Keadby-West Burton 2 (4TM 1-81) with 3420MVA post-fault rating during Winter | 24/10/2035
|  | CS-08885 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100455-201020 | At Keadby 400kV substation: Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby –Thorpe Marsh 400kV circuit | 24/10/2035
|  | CS-08867 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101899-204096 | Replace circuit breakers L85 and L45 at Monk Fryston 275kV with 40kA-rated circuit breaker tested to the appropriate X/R ratio | 24/10/2035
|  | CS-08879 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm2 sections of the circuits with 2x570 mm2 strung to an operating temperature of 75°C. Hotwire the 2x570 mm2 sections to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A. | 24/10/2035
|  | CS-08881 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101504-202965 | Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit to provide a post-fault winter rating of 3820MVA: • Reconductor the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C • At Keadby 400kV substation, replace the X1005 feeder bay for the Drax – Keadby – Thorpe Marsh circuit | 24/10/2035
|  | CS-08883 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV and High Marnham 400kV substation including all associated substation works known as Humber Trent Green | 24/10/2035
|  | CS-08887 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 to achieve a post-fault winter rating of 1090MVA. | 24/10/2035
|  | CS-08888 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 24/10/2035
|  | CS-08890 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 24/10/2035
|  | CS-08866 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 102393-204913 | Make provision for connection of generator bay at new Monk Fryston 400kV substation | 24/10/2035
|  | CS-08873 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101807-203697 | New EDN2 Chesterfield – Ratcliffe-on-Soar 400kV double circuit | 24/10/2035
|  | CS-08878 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101511-202976 | Hotwire the 2x400mm2 sections of the Elland – Stalybridge circuit 275kV to an operating temperature of 75°C | 24/10/2035
|  | CS-08875 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101616-203249 | Reconductor 400kV Drakelow to Hams Hall line from Rubus 500sqmm to Rubus 500sqmm at 90deg C to have summer pre fault rating of 1660MVA | 24/10/2035
|  | CS-08880 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101509-202974 | Replace the existing Ferrybridge C 275kV substation, new substation to be established as an offline build with phased circuit transfers. | 24/10/2035
|  | CS-08882 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 24/10/2035
|  | CS-08872 | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation | 101855-203810 | Reconductoring of Macclesfield to Stalybridge line (A23A) with 1590MVA pre-fault rating during Summer. | 24/10/2035
Monk Fryston SSE | PRO-001627 | CS-07064 | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation | 101243-202472 | Extension of the existing OTS at Lackenby 400kV substation for the connection of new generators | 31/10/2025
|  | CS-04731 | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation | 101507-202972 | Make provision for connection of generator bay (User’s Works) at Monk Fryston 275kV double busbar substation. Local works to facilitate extension of Lackenby Operational Tripping Scheme (OTS) at Monk Fryston 275kV double busbar substation. | 31/10/2025
|  | CS-04732 | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation | 101507-202972 | Make provision for connection of generator bay (User’s Works) at Monk Fryston 275kV double busbar substation. Local works to facilitate extension of Lackenby Operational Tripping Scheme (OTS) at Monk Fryston 275kV double busbar substation. | 31/10/2025
|  | CS-04733 | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation | 101508-202973 | Replace circuit breakers S10 and L25 at Monk Fryston 275kV substation with a 40kA-rated circuit breaker tested to the appropriate X/R ratio | 31/10/2025
|  | CS-04734 | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation | 101561-203104 | At Monk Fryston 275kV AIS Double Busbar Substation replace SGT1 400/275kV Interbus Transformer with a higher rated unit. | 31/10/2025
Monk Fryston Tertiary Connection | PRO-000479 | CS-07948 | HD777FRY LTD | Monk Fryston 275kV Substation | 100803-201619 | 1. Install a modified tertiary cable box on SGT2 2. Install 13kV Cable from tertiary cable box to disconnector cable sealing end (to be confirmed at detailed design stage) 3. Install 13kV Cable from CSE to the earthing transformer 4. Install an earthing transformer at the 13kV side 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets | 01/10/2024
Monquhill Wind Farm | PRO-000478 | CS-05955 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Monquhill Wind Farm 132kV/33kV | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/04/2027
|  | CS-05956 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Monquhill Wind Farm 132kV/33kV | SPT-RI-237 | 3. Enoch Hill Collector 132/33kV Substation and associated 132132kV circuit – Establish a 132/33kV substation adjacent to Enoch Hill wind farm, in East Ayrshire. A new 132kV underground cable circuit will connect this new substation into a new 132kV bay in Board C at New Cumnock 132kV substation. The 132kV circuit will comprise of approximately 4.4km of underground cable (as opposed to OHL), which has been requested by Enoch Hill wind farm. (SPT-RI-237) | 30/04/2027
|  | CS-05957 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Monquhill Wind Farm 132kV/33kV | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/04/2027
|  | CS-06401 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Monquhill Wind Farm 132kV/33kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/04/2027
Mon Solar Farm | PRO-001480 | CS-06867 | LIGHTSOURCE SPV 204 LIMITED | Wylfa 400kV Substation | 101006-202010 | 1. Uprating of the Bodelwyddan – Connahs Quay 1 and 2 400kV circuits | 31/10/2028
|  | CS-06868 | LIGHTSOURCE SPV 204 LIMITED | Wylfa 400kV Substation | 101007-202011 | Uprating of the single circuit between Pentir - Trawsfynydd to achieve a post fault summer ratings of 2375MVA | 31/10/2028
|  | CS-06869 | LIGHTSOURCE SPV 204 LIMITED | Wylfa 400kV Substation | 033708-033708 | Increase the thermal capability of the Pentir – Trawsfynydd 1 and 2 circuits by adding a second core per phase on the cable sections and uprating the OHL sections. | 31/10/2028
|  | CS-06870 | LIGHTSOURCE SPV 204 LIMITED | Wylfa 400kV Substation | 101072-202151 | Extend the current Wylfa 400kV substation to enable the connection of the new Pentir - Wylfa 400kV double circuit. | 31/10/2028
|  | CS-06871 | LIGHTSOURCE SPV 204 LIMITED | Wylfa 400kV Substation | 100975-201954 | Establish a 2nd 400kV circuit between Pentir and Trawsfynydd by rationalising the existing 132kV circuit strung on one side of the 4ZC tower route and installing new cable sections across the Glaslyn Estuary and Estuary approach. | 31/10/2028
|  | CS-06872 | LIGHTSOURCE SPV 204 LIMITED | Wylfa 400kV Substation | 101267-202510 | Establish a CUSC Category 2 system to generator intertrip scheme to monitor both of the Wylfa – Pentir 400kV double circuits, and the 400kV circuits between Pentir, Connahs Quay, Trawsfynydd and Legacy | 31/10/2028
|  | CS-06873 | LIGHTSOURCE SPV 204 LIMITED | Wylfa 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 31/10/2028
|  | CS-06874 | LIGHTSOURCE SPV 204 LIMITED | Wylfa 400kV Substation | 100974-201953 | Construct a new 400kV double circuit between Pentir and Wylfa 400kV substation | 31/10/2028
Montreathmont Moor Forest | PRO-001849 | CS-06885 | Montreathmont Energy Centre Limited | Lunanhead GSP | 132kV Protection Works - Montreathmont Moor Forest | The installation of four new protection bays, two at each of the remote ends between Tealing and Lunanhead. There is also a requirement to install two new VTs on both circuits at Lunanhead. Replacement or modification of the Battery Systems, LVAC Board and Standby Generator at Lunanhead 132/33kV GSP, along with the upgrade of communication links between Lunanhead 132/33kV GSP substation and Tealing 132kV substation. | 31/10/2025
Moray West Offshore Windfarm | PRO-001130 | CS-05959 | MORAY OFFSHORE WINDFARM (WEST) LIMITED | Moray Firth 220/33kV Platform 1 & 2 Offshore Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 01/04/2024
|  | CS-05960 | MORAY OFFSHORE WINDFARM (WEST) LIMITED | Moray Firth 220/33kV Platform 1 & 2 Offshore Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 01/04/2024
|  | CS-05961 | MORAY OFFSHORE WINDFARM (WEST) LIMITED | Moray Firth 220/33kV Platform 1 & 2 Offshore Substation | SHET-RI-025 | North East Reinforcement –- Re-insulate the 275kV double circuit overhead lines between Rothienorman – Blackhillock and Rothienorman - Kintore for 400kV operation. Move the two line connected 400/275kV, 1200MVA SGT’s from Blackhillock to Kintore for terminating the Rothienorman to Kintore double circuit overhead line onto the 275kV busbar at Kintore. Re-Profile the 275kV double circuit overhead line between Peterhead – Persley – Kintore for the maximum permissible operating temperature. Install two 400/275kV SGT’s to connect the Rothienorman GSP to the 400kV Rothienorman Busbar. (SHET-RI-025d) | 01/04/2024
Morecambe Offshore Wind Farm | PRO-001450 | CS-04361 | OFFSHORE WIND LIMITED | Penwortham 400kV Substation | 101138-202245 | 0 | 30/06/2029
|  | CS-04362 | OFFSHORE WIND LIMITED | Penwortham 400kV Substation | 101072-202151 | Extend the current Wylfa 400kV substation to enable the connection of a new Pentir - Wylfa OHL. | 30/06/2029
|  | CS-04363 | OFFSHORE WIND LIMITED | Penwortham 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 30/06/2029
|  | CS-04364 | OFFSHORE WIND LIMITED | Penwortham 400kV Substation | 100974-201953 | Construct a second double circuit between Pentir 400kV substation and the Wylfa 400kV substation (circuits No. 3 and 4) | 30/06/2029
|  | CS-04365 | OFFSHORE WIND LIMITED | Penwortham 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 30/06/2029
Moreton Estate | PRO-003920 | CS-09085 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 28/04/2037
|  | CS-09093 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101833-203761 | Uprate the Chickerel - Mannington double circuit (NASP Code: A851 and A830) to summer pre fault rating of 2200MVA. | 28/04/2037
|  | CS-09094 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101501-202957 | Reconductor the Hinkley point - Sandford CSE circuit 1 (only ZG section) in order to achieve a summer post fault rating of 2850MVA | 28/04/2037
|  | CS-09089 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 28/04/2037
|  | CS-09131 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101465-202905 | conductor the existing 2x500mm2 conductor on the FeckenhamWalham 400 kV circuit with 2x780mm2 conductor to achieve a pre fault summer rating of 2800 MVA. | 28/04/2037
|  | CS-09087 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 102674-205359 | Extension of the 400kV busbars at the new Substation for the User’s bay and Extension of the South West OTS to include this Generator | 28/04/2037
|  | CS-09095 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101501-202958 | Reconductor the Hinkley point - Sandford CSE circuit 2 (only ZG section) in order to achieve a summer post fault rating of 2850MVA. | 28/04/2037
|  | CS-09088 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 28/04/2037
|  | CS-09126 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 102109-204303 | Uprate Iver – West Weybridge circuit. | 28/04/2037
|  | CS-09122 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101592-203207 | Reconductor East Claydon – Amersham Main – Iver 400kV double circuit route (55.5km, 2x500mm2 Twin Rubus conductor on L2 Towers at 75oC with a summer pre-fault rating of 1466MVA) to 2x620mm2 Twin Matthew Conductor at 170°C to achieve a new summer pre-fault rating of 2490 MVA. | 28/04/2037
|  | CS-09130 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 102224-204456 | Installation of a 2750MVA quadbooster on the Feckenham-Walham circuit. | 28/04/2037
|  | CS-09123 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 020903-020903 | Uprating of the Cowley-Walham / Cowley Minety 400kV circuit cables to achieve 1900MVA post-fault summer rating | 28/04/2037
|  | CS-09125 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 102108-204302 | Uprate the Iver – Laleham circuit 1 | 28/04/2037
|  | CS-09129 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 102223-204455 | Installation of a 2750MVA quadbooster on the Feckenham-Minety circuit. | 28/04/2037
|  | CS-09128 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 100426-200972 | conductor the existing 2x500mm2 conductor on the FeckenhamMinety 400 kV circuit with 2x780mm2 conductor to achieve a pre fault summer rating of 2800 MVA. | 28/04/2037
|  | CS-09133 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 100425-200971 | econductor the existing 2x500mm2 conductor on the FeckenhamIronbridge 400 kV circuit with 2x620mm2. | 28/04/2037
|  | CS-09105 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101978-204103 | Uprate the Drakelow 400kV -to- Ratcliffe On Soar 400kV circuit #1 (DRAK4-RATS4-1) to summer pre-fault rating 2490MVA | 28/04/2037
|  | CS-09102 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101884-203860 | Reconductor the Enderby legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490MVA | 28/04/2037
|  | CS-09106 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101880-203857 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4-WILE4-2) to summer pre-fault rating 2490MVA | 28/04/2037
|  | CS-09090 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 28/04/2037
|  | CS-09104 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 28/04/2037
|  | CS-09114 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 28/04/2037
|  | CS-09111 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101593-203208 | Uprate the Cottam – Staythorpe circuit 1, to provide a winter post fault rating of 3300 MVA. This includes the cable section. | 28/04/2037
|  | CS-09121 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101316-202621 | Hotwire A881 East Claydon – Cowley 400kV circuit (36.3km, 4x400mm2 zebra conductor at 50 deg. C on L6 Towers, currently rated to 1862MVA summer pre-fault) to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 28/04/2037
|  | CS-09107 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101879-203856 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #1 (RATS4-WILE4-1) to summer pre-fault rating 2490 MVA | 28/04/2037
|  | CS-09120 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101247-202487 | The circuits running from Leighton Buzzard to Sundon 1&2 (LEIB4A-SUND4- 1) and LEIB4B-SUND4-2 will also be reconductored with 4 x 400mm2 conductor rating 2870MVA, 75˚C for winter intact condition. | 28/04/2037
|  | CS-09110 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 28/04/2037
|  | CS-09119 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 102362-204786 | e circuit running from Leighton Buzzard to Sundon 1 (LEIB4ASUND4-1) will also be reconductored with 4 x 400mm2 conductor rating 2870 MVA, 75˚C for winter intact condition. | 28/04/2037
|  | CS-09109 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 28/04/2037
|  | CS-09118 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 28/04/2037
|  | CS-09108 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101891-203873 | Uprate the circuit Drakelow 400kV Willington East 400kV to achieve a summer pre-fault rating of 2490MVA. | 28/04/2037
|  | CS-09113 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 100459-201024 | Reconductor the 2x500mm2 section of the High Marnham – Stoke Bardolph 400kV circuit with 2x700mm2 conductor. | 28/04/2037
|  | CS-09116 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 28/04/2037
|  | CS-09115 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a post-fault winter rating of 3100MVA | 28/04/2037
|  | CS-09112 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 28/04/2037
|  | CS-09103 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101889-203868 | Reconductor the East Claydon legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490 MVA. | 28/04/2037
|  | CS-09117 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 28/04/2037
|  | CS-09132 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101467-202907 | econductor the existing 2x500mm2 conductor on the FeckenhamHams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 28/04/2037
|  | CS-09096 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101500-202955 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 1 in order to achieve a summer post fault rating of 2850MVA | 28/04/2037
|  | CS-09092 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101497-202952 | Reconductor the single circuit between Melksham - Seabank (route 4YX and 2VL) in order to achieve a pre fault summer rating of 2500MVA and post fault summer rating of 3210MVA. | 28/04/2037
|  | CS-09086 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 102057-204228 | Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure. Construction of 400kV Busbar to accommodate the OHL feeders | 28/04/2037
|  | CS-09127 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 102110-204304 | Uprate both Ealing – Laleham circuit 1 and 2 | 28/04/2037
|  | CS-09124 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101420-202784 | Uprate the Bramley – Didcot 400kV circuits; including overhead line and cable sections. | 28/04/2037
|  | CS-09097 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 101500-202956 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 2 in order to achieve a summer post fault rating of 2850MVA | 28/04/2037
|  | CS-09091 | EPL NEWCO5 LIMITED | Chickerall B 400kV Substation | 100480-201051 | Uprate the cable section of the Seabank -Whitson section of the three-ended Seabank -Whitson - Cilfynydd circuit to a pre-fault rating of 1800MVA | 28/04/2037
Morgannwg Solar Farm | PRO-001775 | CS-07033 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 101604-203222 | Works to facilitate the use of Aberthaw 275kV substation’s spare bay for the User’s connection | 31/10/2028
|  | CS-07034 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 1990MVA | 31/10/2028
|  | CS-07035 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 020903-020903 | Uprating/replacement of the Cowley – Walham and Cowley - Minety 400kV circuits cables sections to achieve 1193MVA or greater prefault Summer rating. | 31/10/2028
|  | CS-07036 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 033769-033769 | Reconductor Hinkley Point – Taunton circuits 1 and 2 to achieve 2680MVA pre-fault summer rating. | 31/10/2028
|  | CS-07037 | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation | 101562-203112 | Reconductor Taunton - Exeter circuits 1 and 2 to achieve 2680MVA pre-fault summer rating. | 31/10/2028
Morgan Offshore Wind Farm | PRO-001594 | CS-05030 | Morgan Offshore Wind Limited | Wylfa 400kV Substation | 101072-202151 | Extend the current Wylfa 400kV substation to enable the connection of a new Pentir - Wylfa OHL. | 01/04/2033
|  | CS-05031 | Morgan Offshore Wind Limited | Wylfa 400kV Substation | 101304-202587 | Infrastructure works necessary to connect 1500MW at the Wylfa 400kV substation, for the Project Elizabeth - Yellow One North R4 connection application | 01/04/2033
|  | CS-05032 | Morgan Offshore Wind Limited | Wylfa 400kV Substation | 033708-033708 | Pentir - Trawsfynydd 1+2 - Add a second cable per phase to all cable sections and update the OHL sections to achieve required rating | 01/04/2033
|  | CS-05033 | Morgan Offshore Wind Limited | Wylfa 400kV Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 01/04/2033
|  | CS-05029 | Morgan Offshore Wind Limited | Wylfa 400kV Substation | 100974-201953 | Construct a second double circuit between Pentir 400kV substation and the Wylfa 400kV substation (circuits No. 3 and 4) | 01/04/2033
Morven A Offshore Wind Farm (Prev Phoenix 1A) | PRO-001515 | CS-06714 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | Phoenix 1A Item 1 | The Sole Enabling Works at Tealing 400kV substation shall comprise the installation of 2 x new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Relevant Transmission Licensee and the User will be the User side of the 400kV feeder circuit breaker/isolators at Tealing 400kV substation. | 31/10/2031
|  | CS-06715 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-147 | Tealing 400kV Substation - Establish a new 400kV substation close to the existing Tealing 275kV substation. | 31/10/2031
|  | CS-06716 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2031
|  | CS-06717 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 31/10/2031
|  | CS-06718 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-025d | North East Reinforcement | 31/10/2031
|  | CS-06719 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2031
|  | CS-06720 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2031
|  | CS-06721 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2031
|  | CS-06722 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2031
|  | CS-06723 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2031
|  | CS-06724 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2031
|  | CS-06725 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 31/10/2031
|  | CS-06726 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-148 | Alyth – Tealing 400kV Reinsulation - Re-insulate the 275kV double circuit overhead line between Alyth and Tealing for 400kV operation. | 31/10/2031
|  | CS-06727 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1A 275/66kV Offshore Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2031
Morwind 300 | PRO-001787 | CS-04992 | Morwind Ltd | Alverdiscott 400kV Substation | 101606-203232 | Extension of the South West OTS to incorporate the Morwind 300 Offshore Wind Farm. | 31/10/2031
|  | CS-04993 | Morwind Ltd | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 31/10/2031
|  | CS-04994 | Morwind Ltd | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-04995 | Morwind Ltd | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Hinkley Point - Exeter 400kV circuits to achieve a 3100MVA post fault winter rating. Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating | 31/10/2031
|  | CS-04996 | Morwind Ltd | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 31/10/2031
|  | CS-04997 | Morwind Ltd | Alverdiscott 400kV Substation | 020903-020903 | Uprating of the Cowley - Walham 400kV circuit cables to achieve 1500MVA post-fault summer rating. | 31/10/2031
|  | CS-04998 | Morwind Ltd | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 31/10/2031
|  | CS-04999 | Morwind Ltd | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault Summer rating of 1650MVA. | 31/10/2031
|  | CS-05000 | Morwind Ltd | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 31/10/2031
|  | CS-05001 | Morwind Ltd | Alverdiscott 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 31/10/2031
|  | CS-05002 | Morwind Ltd | Alverdiscott 400kV Substation | 101065-202138 | Reconductor the Melksham - Minety 1and 2 circuits to achieve a post-fault Summer rating of 2470MVA. | 31/10/2031
|  | CS-05003 | Morwind Ltd | Alverdiscott 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 31/10/2031
|  | CS-05004 | Morwind Ltd | Alverdiscott 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 31/10/2031
|  | CS-04990 | Morwind Ltd | Alverdiscott 400kV Substation | 101606-203230 | Infrastructure works at the substation for the generation connection of Morwind 300 Offshore Wind Farm. | 31/10/2031
|  | CS-04991 | Morwind Ltd | Alverdiscott 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 31/10/2031
Mossmorran Storage BESS | PRO-003738 | CS-09670 | MOSSMORRAN STORAGE LTD | Mossmoran 275kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 31/10/2031
|  | CS-09671 | MOSSMORRAN STORAGE LTD | Mossmoran 275kV Substation | SPT-RI-148 | Install an auto-close scheme across the three 275/132kV supergrid transformers at WindyHill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. | 31/10/2031
|  | CS-09672 | MOSSMORRAN STORAGE LTD | Mossmoran 275kV Substation | SHET-RI-149 | Tealing – Glenrothes/Westfield 400kV Rebuild - Rebuild the 275kV double circuit overhead line between Tealing and Glenrothes/Westfield for 400kV operation. | 31/10/2031
|  | CS-09673 | MOSSMORRAN STORAGE LTD | Mossmoran 275kV Substation | SHET-RI-185 | Kintore - Tealing 400kV circuit – Establish a new 400 kV double circuit overhead line between Kintore 400 kV substation and Tealing 400 kV substation. | 31/10/2031
|  | CS-09674 | MOSSMORRAN STORAGE LTD | Mossmoran 275kV Substation | Disconnector - Mossmorran Storage | At Gresham House MOSM BESS 132kV collector substation, install one new 132kV disconnector | 31/10/2031
Mossy Hill Wind Farm | PRO-000461 | CS-05962 | MOSSY HILL SHETLAND LIMITED | Mossy Hill 132kV Substation | SHET-RI-053 | Shetland 600MW HVDC Link and Kergord 132kV Substation ‒ Construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Noss Head in Caithness. The HVDC switching station works will be part of SHET-RI-062 and will integrate with the Caithness-Moray Transmission Reinforcement (part of SHET-RI-031). The HVDC link includes a 600MW HVDC converter station and 132kV Substation at Kergord in Shetland. The new 132kV Substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of subsea cable between Shetland and the HVDC switching station in Caithness. (SHET-RI-053) | 01/04/2027
|  | CS-05439 | MOSSY HILL SHETLAND LIMITED | Mossy Hill 132kV Substation | SHET-RI-152 | Shetland ANM Scheme - ANM System on Shetland to manage flows across 600MW HVDC link (established under SHET-RI-053) from Kergord 132kV substation on Shetland to the Scottish mainland at an HVDC convertor station in the vicinity of Noss Head in Caithness. (SHET-RI-152) | 01/04/2027
|  | CS-06457 | MOSSY HILL SHETLAND LIMITED | Mossy Hill 132kV Substation | SHET-RI-143 | Kengord to Gremista GSP Infrastructure - Construct a new 132kV 24km circuit between Kergord substation and Gremista GSP, terminated onto new 132kV feeder bays at Kergord and Gremista. Construct a new Tee point for the connection of a wind farm. (SHET-RI-143) | 01/04/2027
|  | CS-06458 | MOSSY HILL SHETLAND LIMITED | Mossy Hill 132kV Substation | Mossy Hill H1 Works | A 132kV feeder disconnector (103) will be installed at the User’s substation as sole use assets. | 01/04/2027
|  | CS-09752 | MOSSY HILL SHETLAND LIMITED | Mossy Hill 132kV Substation | SHET-RI-247 | Mossyhill T-connection - Loop In Loop Out Substation will be constructed to accommodate two projects from the same developer (Under different connection applications). Both these projects are hardly 200m away from each other. (SHET-RI-247) | 01/04/2027
Mount Blairy | PRO-002284 | CS-09081 | GREENTECH PROJECTS HOLDING UK LIMITED | Macduff GSP | SHET-RI-207 | Macduff to Blackhillock 132kV OHL – To Rebuild or Reconductor approx. 37.7km of the overhead line between Blackhillock 132kV Substation and Macduff GSP with a conductor capable of a minimum 120MVA Pre Fault rating | 31/10/2027
Mount Farm | PRO-000989 | CS-05963 | SP Distribution plc | Coylton GSP | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 31/10/2021
|  | CS-04305 | SP Distribution plc | Coylton GSP | SPT-RI-224 | At Coylton substation, the existing SGT1 and SGT2 275/132kV 120MVA transformers will be replaced (on line) with 240MVA units. | 31/10/2021
Muaitheabhal Wind Farm | PRO-000272 | CS-05964 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | Muaitheabhal Item 1 | The Relevant Transmission Licensee will install a 13km wood pole overhead line between Muaitheabhal Windfarm and the proposed 132kV switching station near Balallan (to be established under SHET-RI-043), with two 132kV circuit switchers at Muaitheabhal Windfarm and a 132kV circuit breaker at Balallan 132kV switching station. | 31/10/2030
|  | CS-05965 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 31/10/2030
|  | CS-05966 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | SHET-RI-042 | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHET-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly. | 31/10/2030
|  | CS-05967 | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation | SHET-RI-043 | Lewis Infrastructure - Build a new 132kV single circuit OHL between Arnish substation, and the Muaitheabhal Tee point. Dismantle the existing 132kV single circuit OHL between Stornoway Tee point, and the Muaitheabhal Tee point. | 31/10/2030
Muir Mhor Offshore Wind Farm | PRO-001698 | CS-04504 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | Cirrus H1 Enabling Works | At New Deer 2 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV circuit breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Relevant Transmission Licensee and the User (as OTSDUW User) will be the User side of the 400kV feeder circuit breakers/isolators at New Deer 2 400kV substation. | 31/10/2033
|  | CS-04505 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-04506 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-04507 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-04508 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-04509 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-04510 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-04511 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-04512 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-04513 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-04514 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-04515 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-04516 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-04517 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-04518 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-04519 | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
Murroch BESS | PRO-003610 | CS-09577 | GPC Battery Ltd | Strathleven GSP | SPT-RI- 3314 | Windyhill 132kV B board – It is proposed to establish a new Windyhill 132kV B substation within Windyhill substation in order to accommodate the connection of SEC 1 BESS (SPT-RI-2972). Once the new Windyhill B board has been established, the switchboard will be fed via two 400/132kV SGT’s. A 132kV bus section will be installed with corresponding disconnectors on the reserve busbar, a 132kV bus coupler and four 132kV feeder bays (space required within the switchgear housing to accommodate future connections) will also be installed. Two bays will be used to connect the 400/132kV SGT’s with the remaining two bays used to transfer across the Partick/Finnieston 132kV circuits from the existing Windyhill 132kV switchboard. Two new 400kV DBB GIS feeder bays with associated switchgear (circuit breaker and DBB disconnectors) will be installed at Windyhill 400kV to connect the new 400/132kV 360MVA Super Grid Transformer. The new Windyhill B board will be subject to the completion of SPT-RI-2815 | 22/05/2031
|  | CS-09576 | GPC Battery Ltd | Strathleven GSP | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 22/05/2031
Mwdwl Eithin Energy Park | PRO-001511 | CS-06500 | MOEL CHWA ENERGY PARK LIMITED | Gwyddelwern 400kV Substation | 101212-202434 | 1. Establish a new four bay 400kV double busbar substation1 adjacent to the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. Substation to comprise two feeder bays, a bus coupler bay and a skeletal bay for the User to connect their generator circuit 2. Connect the substation to the Main interconnected system via a turn in of the Trawsfynydd leg of the Connahs Quay – Legacy – Trawsfynydd circuit. | 31/10/2026
|  | CS-06501 | MOEL CHWA ENERGY PARK LIMITED | Gwyddelwern 400kV Substation | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor. | 31/10/2026
Nairn BESS | PRO-002533 | CS-08582 | ANESCO LIMITED | Nairn GSP | SHET-RI-170 | 3rd SGT at Keith 132/275kV Substation - Install a new 480MVA 275/132kV SGT at Keith 132kV Substation. In addition, install approx. 2.5km of Cable between the new SGT and Blackhillock 275kV Substation. (SHET-RI-170) | 31/10/2026
Nant Ceiment Energy Park | PRO-001610 | CS-06875 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 11/09/2027
|  | CS-06876 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 11/09/2027
|  | CS-06877 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 101051-202109 | Uprating of the Cowley – Walham 400kV circuit cable section only to achieve 1341MVA pre-fault summer rating. | 11/09/2027
|  | CS-06878 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 101256-202608 | Install and commission 3 Supergrid Transformer (SGT) bays at Pont Abraham 400/132kV Substation Install and commission switchgear at Pont Abraham to include SGT HV and LV Circuit Breakers and associated bay assets Install and commission 3 460MVA rated 400/132/132kV SGT’s Install 132kV cabling from the LV side of the SGT to the relevant bay at the Users 132kV substation for each SGT circuit Install HAM (High Accuracy Metering) units and associated metering equipment in accordance with metering Code of Practice. | 11/09/2027
|  | CS-06879 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 033769-033769 | Reconductor the Exeter – Hinkley Point – Taunton 400kV circuits to achieve a 2787MVA pre-fault summer rating. | 11/09/2027
|  | CS-06880 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 100424-200970 | Reconductor the Bramley – Melksham 400kV circuits 1 and 2 to achieve a pre-fault summer rating of 1581MVA. | 11/09/2027
|  | CS-06881 | NANT CEIMENT ENERGY PARK LIMITED | Pont Abraham GSP | 101052-202110 | Install power flow control devices along the Imperial Park – Melksham 400kV circuit | 11/09/2027
Nant Y Maen Wind Farm | PRO-001158 | CS-04611 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202058/ 101032-202059/ 101032-202069 | 1. Establish a new 400kV double busbar substation comprising 2 feeder bays, a bus coupler, a MSCDN bay and 4 SGT bays. 2. Establish a new 3.5kA continuous current rated 132kV double busbar substation comprising a bus coupler,4 SGT bays, an earthing transformer bay and 2 feeder bays. 3. Install a 225MVAr MSCDN at the 400kV substation. 4. Connect an earthing transformer to the 132kV substation 5. Install an earthing transformer at the 132kV substation. 6. Connect the 400kV substation to the 132kV substation via 4 240MVA rated SGT’s 7. Establish a system to generator operational intertripping scheme to perform as per the requirements of the TOF3 8. Connect the 400kV substation to the Legacy – Shrewsbury – Ironbridge and Legacy – Ironbridge circuits via a double tee arrangement. 9. Connect the new Cefn Coch – Lower Frankton 132kV double circuit to Lower Frankton 132kV substation | 01/05/2032
|  | CS-04612 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202066 | Establish a new 132kV double circuit route between Lower Frankton and Cefn Coch | 01/05/2032
|  | CS-04613 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202060 | 1. Establish a new 4 bay new 3.5kA continuous current rated 132kV double busbar substation comprising a bus coupler, 4 feeder bays, 2 SVC bays. 2. Installation of 2 SVC’s 3. Connect the Cefn Coch – Lower Frankton 132kV double circuit into Cefn Coch substation EdF (Nant Y Maen) ConsAg v1 Ref: A/NANTY/20/0503-1EN(0) Date: August 2020 4. Connect the new Garn Fach – Cefn Coch 132kV double circuit to Cefn Coch 132kV substation | 01/05/2032
|  | CS-04614 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202067 | Establish a new 132kV double circuit route between Cefn Coch and Garn Fach | 01/05/2032
|  | CS-04615 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202061 | 1.Establish a new 132kV substation comprising 4 feeder bays and space for User to connect their generator bay. 2. Connect the new Cefn Coch – Garn Fach 132kV double circuit to Garn Fach 132kV substation 3. Connect the new Garn Fach – Nant y Maen 132kV double circuit to Garn Fach 132kV substation | 01/05/2032
|  | CS-04616 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202062 | Establish a new 132kV substation comprising 2 feeder bays and space for the User to connect their generator bay | 01/05/2032
|  | CS-04617 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202068 | Establish a new 132kV double circuit route between Garn Fach and Nant y Maen. | 01/05/2032
|  | CS-04618 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202063 | 1. Establish a new 400kV single switch mesh substation 2. Reconnect the HV side of the existing Shrewsbury SGT to Mesh Corner 2 of the newly established mesh substation. 3. Install a circuit intertripping scheme | 01/05/2032
|  | CS-04619 | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation | 101032-202064 | Installation of a new 225MVAR MSCDN at Ironbridge 400kV substation. | 01/05/2032
Narachan Wind Farm | PRO-001926 | CS-07706 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 30/11/2028
|  | CS-07707 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 30/11/2028
|  | CS-07708 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 30/11/2028
|  | CS-07709 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 30/11/2028
|  | CS-07704 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 30/11/2028
|  | CS-07705 | ENERGYFARM UK NARACHAN LLP | Carradale 1 GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 30/11/2028
Native River (Capenhurst) | PRO-001557 | CS-06882 | NATIVE RIVER LTD | Capenhurst 275kV Substation | 101250-202491 | Install a tertiary cable box or bushing on SGT3A. Install a 13kV cable (if required) from tertiary cable box or bushing to earthing transformer. Install an earthing transformer. Install 13kV Disconnector at the 13kV side connecting the tertiary connection to Connection Assets. | 30/05/2024
Neart Na Gaoithe Offshore Wind Farm | PRO-000273 | CS-05968 | NEART NA GAOITHE OFFSHORE WIND LIMITED | Neart Na Gaoithe 220/66KV Offshore Substation | Neart Na Gaoithe H1 Works Item 2 | Replacement of the existing AIS X130 bus coupler and associated plant and apparatus at Crystal Rig 400kV Substation with a new 400kV GIS X130 circuit breaker | 01/06/2023
|  | CS-05969 | NEART NA GAOITHE OFFSHORE WIND LIMITED | Neart Na Gaoithe 220/66KV Offshore Substation | Neart Na Gaoithe H1 Works Item 1 | Modification of the existing Crystal Rig 400kV Substation, including civils works, and the installation of 400kV GIS plant and apparatus which will form the connections to the two Transmission Interface Points, including busbars, circuit breakers, disconnectors, earth switches, surge arresters, current and voltage transformers | 01/06/2023
|  | CS-06680 | NEART NA GAOITHE OFFSHORE WIND LIMITED | Neart Na Gaoithe 220/66KV Offshore Substation | SPT-RI-204 Wishaw - Smeaton - Torness - Eccles Overload Protection Scheme | An overload protection scheme installed within Wishaw - Smeaton - Torness - Eccles 275kV and 400kV network in order to protect the system in compliant Category 2 Intertripping Scheme as defined by the Grid Code. The Interrtripping Scheme will disconnect the generation within the area following system outage conditions being met. | 01/06/2023
Necton Greener Grid Park | PRO-002562 | CS-09500 | STATKRAFT UK LTD | Necton 400kV Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 31/10/2026
|  | CS-09488 | STATKRAFT UK LTD | Necton 400kV Substation | 033804-033804 | At Necton 400kV substation: extend the substation by 5 bays; 1 main and 1 reserve section bay, 1 bus coupler bay and 2 feeder bays | 31/10/2026
|  | CS-09489 | STATKRAFT UK LTD | Necton 400kV Substation | 033804-201295 | At Necton 400kV substation: double turn in of the existing Walpole – Norwich Main OHL circuits | 31/10/2026
|  | CS-09491 | STATKRAFT UK LTD | Necton 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 31/10/2026
|  | CS-09492 | STATKRAFT UK LTD | Necton 400kV Substation | 021847-021847 | Construct a new 400 kV double circuit between the Bamford 400 kV substation and the Twinstead Tee point strung with 3x700mm2 AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford-Pelham double circuit and Bramford-Braintree-Bulls Lodge and Bramford-Braintree-Rayleigh Main 400 kV double circuit (BTNO Works). | 31/10/2026
|  | CS-09495 | STATKRAFT UK LTD | Necton 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 31/10/2026
|  | CS-09496 | STATKRAFT UK LTD | Necton 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 31/10/2026
|  | CS-09493 | STATKRAFT UK LTD | Necton 400kV Substation | 033461- 033461 | Post-completion of BTNO works, reconductor Bramford-Pelham 1 400kV circuits with 3 x700mm2 AAAC conductors to achieve a post-fault winter rating of 3100 MVA | 31/10/2026
|  | CS-09497 | STATKRAFT UK LTD | Necton 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm2 and 3M curlew 2x490 mm2 @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm2 conductor (at 90˚C). | 31/10/2026
|  | CS-09502 | STATKRAFT UK LTD | Necton 400kV Substation | 100875-202041 | At Tilbury 400kV Substation: Extension of busbars for the provision of 2 feeder bays for the CLAC-TILB OHL | 31/10/2026
|  | CS-09499 | STATKRAFT UK LTD | Necton 400kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 31/10/2026
|  | CS-09503 | STATKRAFT UK LTD | Necton 400kV Substation | 100875-201761 | Build a new 400 kV double circuit between Bramford 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter post-fault. | 31/10/2026
|  | CS-09490 | STATKRAFT UK LTD | Necton 400kV Substation | 100926-201852 | At Necton 400kV Substation: Extend the substation by 4 bays; A Main & Reserve Bus Section Bay, One Feeder Bay and one OFTO Bay. Transfer a circuit into the extended busbar section's feeder bay. Extension of the existing East Anglia Operational intertripping scheme. | 31/10/2026
|  | CS-09498 | STATKRAFT UK LTD | Necton 400kV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400kV with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 31/10/2026
|  | CS-09501 | STATKRAFT UK LTD | Necton 400kV Substation | 100875-202039 | Build a new 400 kV double circuit between East Anglia Coastal 400 kV and Tilbury 400 kV substations with a minimum rating of 3000 MVA winter postfault. | 31/10/2026
|  | CS-09494 | STATKRAFT UK LTD | Necton 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 31/10/2026
Neilston 132kV Greener Grid Park | PRO-001343 | CS-09417 | STATKRAFT UK LTD | Neilston 132kV Substation | SPT-RI-1741 | 1. Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service. (SPT-RI-1741) | 31/05/2024
|  | CS-09418 | STATKRAFT UK LTD | Neilston 132kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 31/05/2024
Neilston 400kV Greener Grid Park | PRO-001419 | CS-07248 | STATKRAFT UK LTD | Neilston 400kV Substation | Neilston 2 400kV H1 Works | Hunterston East – Neilston 400kV Reinforcements - Modification of the Hunterston East - Devol Moor 400kV circuit to become the Hunterston East - Neilston 400kV double circuit OHL and development of a new 400/275kV supergrid transformer (SGT4) at Neilston 400kV substation. (NOA HNNO) | 17/05/2027
|  | CS-07249 | STATKRAFT UK LTD | Neilston 400kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 17/05/2027
Neilston Synchronous Compensation | PRO-001405 | CS-04550 | NEILSTON GRID SERVICES LIMITED | Neilston 400kV Substation | Hunterston Syn Comp (WP) Reinforcement Works | Hunterston East – Hunterston East – Neilston 400kV Reinforcements, protection and control, civils | 31/07/2024
Net Zero Teesside Power Project | PRO-001400 | CS-06460 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 101163-202347 | Install two single switch mesh busbar extensions and (if required (subject to detailed design)) replacement of the existing short bar section at Tod Point 275kV substation. Install two new disconnectors on the new busbar extensions at Tod Point 275kV substation for the User’s connection. | 30/04/2026
|  | CS-06461 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 100158-200400 | Extension of the N-1-D Lackenby/Greystones Operational Tripping Scheme (new communications links to a marshalling kiosk at Tod Point 275kV substation) | 30/04/2026
|  | CS-06462 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | CTP2 | Additional Power Control Technology along Creyke Beck – Thornton 1 (A319) 400kV Circuit | 30/04/2026
|  | CS-06463 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 101164- 202350 | At Lackenby 275kV Substation, replacements of circuit breakers H30, H20 and H10 | 30/04/2026
|  | CS-06464 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 031380-031380 | Hotwire the 4x400mm2 sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 30/04/2026
|  | CS-06465 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | TDP2 | Additional Power Control Technology along the Drax – Thornton 1 (A34C) 400kV Circuit | 30/04/2026
|  | CS-06466 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 020640-020640 | Reconductor the 2x500mm2 sections of the Norton – Osbaldwick 1 400kV circuit with 2x700mm2 conductor strung for operation at 90°C | 30/04/2026
|  | CS-06467 | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors and protection on both Thornton circuits at Drax substation to equipment with an equal rating to provide a post-fault winter rating of 3420MVA | 30/04/2026
NeuConnect Interconnector | PRO-001288 | CS-05970 | NEUCONNECT BRITAIN LTD | Grain West 400kV Substation | 33694 | Construction of a new double busbar 400kV substation with two feeder bays, coupler bay and provisions for the connection of the User’s bay. Double tee connection of the new substation to the Grain - Tilbury/Grain - Kingsnorth double over head line circuit and associated works. | 01/08/2026
Newark BESS | PRO-002556 | CS-08541 | SSE DE SOLAR HOLDCO LIMITED | Cottam 400kV Substation | 102426-204956 | 1. Build a new double busbar 400kV substation with 2 feeder bays and 1 coupler bay. 2. Establish a single turn in connection between the new 400kV substation and Cottam – Eaton Socon – Wymondley line-2 (A483). 3. Extension of 400kV busbars to connect user bay | 30/09/2033
Newchurch | PRO-002056 | CS-07538 | SSE UTILITY SOLUTIONS LIMITED | Newchurch 400kV Substation | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 04/10/2031
|  | CS-07539 | SSE UTILITY SOLUTIONS LIMITED | Newchurch 400kV Substation | 101701-203401 | 1. Uprate the Dungeness – Ninfield OHL circuits to increase capacity. | 04/10/2031
|  | CS-07541 | SSE UTILITY SOLUTIONS LIMITED | Newchurch 400kV Substation | 101749-203473 | Investigation into Sellindge X305 and X405 infrastructure de-rating, replacing if necessary, to allow higher fault level ratings at Sellindge 400kV (a milestone has been added for this investigation in the Appendix J of this agreement). | 04/10/2031
|  | CS-07540 | SSE UTILITY SOLUTIONS LIMITED | Newchurch 400kV Substation | 101701-203403 | Uprate the Dungeness – Sellindge 1& 2 OHL circuits to increase capacity | 04/10/2031
|  | CS-07537 | SSE UTILITY SOLUTIONS LIMITED | Newchurch 400kV Substation | 101901-203894 | Replacement, or modification, of existing towers and associated OHL works to facilitate a single turn-in connection to Newchurch via the Dungeness – Sellindge 2 overhead line circuit. Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure Construction of 400kV Busbar to accommodate the OHL Turn-In connection and the Users Generator Bay. | 04/10/2031
New Cumnock BESS | PRO-003485 | CS-09532 | NEW CUMNOCK BESS LTD | New Cumnock 275/132kV Substation | SPT-RI-231 | 0 | 30/10/2030
|  | CS-09531 | NEW CUMNOCK BESS LTD | New Cumnock 275/132kV Substation | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 30/10/2030
|  | CS-09533 | NEW CUMNOCK BESS LTD | New Cumnock 275/132kV Substation | SPT-RI-3309 | New Cumnock North 400kV GIS substation- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new 400kV substation in the vicinity of the existing New Cumnock 275kV substation. This shall be a double busbar GIS ‘New Cumnock North’ 400kV substation. This new substation shall facilitate the development of the NOA WCNC scheme (currently under review) | 30/10/2030
|  | CS-09530 | NEW CUMNOCK BESS LTD | New Cumnock 275/132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 30/10/2030
|  | CS-09534 | NEW CUMNOCK BESS LTD | New Cumnock 275/132kV Substation | SPT-RI-3315 | New Cumnock North to Glenmuckloch 400kV OHL- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new double circuit OHL between (the proposed) New Cumnock North and Glenmuckloch 400kV substation. The scope of works shall consist of 2 stages: Stage 1 – establishment of a new double circuit OHL (L8 with Twin RUBUS conductor is proposed) from New Cumnock North towards Glenmuckloch. One side of the circuit shall be energised in this stage to provide a minimum scope required to enable a connection of New Cumnock BESS. Stage 2 – establishment of a second double busbar GIS switchgear bays at New Cumnock North 400kV substation to connect to the OHL No.1 circuit | 30/10/2030
New Deer Battery Storage | PRO-001987 | CS-07542 | WEAVER POWER LIMITED | New Deer 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
New Deer BESS Station | PRO-001856 | CS-06798 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-06799 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-06800 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-06801 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-06802 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-06803 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-06804 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-06790 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-06791 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-06792 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-06793 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-06794 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-06795 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-06796 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-06797 | IGP SOLAR 25 LIMITED | New Deer 2 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
Newhouse Energy Storage | PRO-001817 | CS-07068 | NEWHOUSE ENERGY STORAGE LIMITED | Burghmuir GSP | SHET-RI-121 | Charleston - Abernethy 132kv reconductoring; approx 25km of 132 kv ohl between abernrethy substation and Charleston. | 31/10/2026
Newlands Hill Wind Energy Hub | PRO-002549 | CS-08590 | NEWLANDS HILL WIND ENERGY HUB LIMITED | Newlands Hill 132/33kV | SPT-RI-204 | Wishaw-Smeaton-Torness-Eccles Overload Protection Scheme -An overload protection scheme is proposed to be installed within the Wishaw – Smeaton – Torness – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following system outage conditions as specified in Appendix F of the Bilateral Connection Agreement - | 30/04/2029
|  | CS-08591 | NEWLANDS HILL WIND ENERGY HUB LIMITED | Newlands Hill 132/33kV | Newlands Hill | 1. Installation of a new 400kV double busbar bay at the Fallago Rig substation including a 400kV circuit breaker and associated disconnectors. 2. Installation of a 400/132kV 240MVA transformer at Fallago Rig substation. 3. Installation of a 132kV circuit breaker and associated disconnectors at Fallago Rig substation. 4. Installation of a new 132kV cable and OHL circuit between Fallago Rig and the User’s site. 5. Installation of a 132kV line disconnector at the Newlands Hill Wind Energy Hub site. 6. Installation of two 132kV transformer disconnectors at Newlands Hill Wind Energy Hub site. 7. 400kV GIS substation in Torness Area - A new 400kV double busbar substation, utilising | 30/04/2029
|  | CS-08589 | NEWLANDS HILL WIND ENERGY HUB LIMITED | Newlands Hill 132/33kV | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 30/04/2029
|  | CS-08588 | NEWLANDS HILL WIND ENERGY HUB LIMITED | Newlands Hill 132/33kV | SPT-RI-124 | 400kV GIS substation in Torness Area - A new 23 Bay double busbar 400kV GIS substation will be installed at a site yet to be determined in the Torness Area of East Lothian. This new substation is currently named as “Branxton 400kV Substation”. (SPT-RI-124 | 30/04/2029
Ninfield | PRO-001215 | CS-05971 | SOUTH EASTERN POWER NETWORKS PLC | Ninfield GSP | NGET-RI-11642 | Hotwiring of the Lovedean - Ninfield - Bolney circuits to increase their thermal rating. | 08/12/2023
|  | CS-05972 | SOUTH EASTERN POWER NETWORKS PLC | Ninfield GSP | NGET-RI-21588 | Re-conductor the Dungeness - Sellindge OHL circuits to increase capacity. | 08/12/2023
|  | CS-05973 | SOUTH EASTERN POWER NETWORKS PLC | Ninfield GSP | NGET-RI-30967 & NGET-RI-30968 | Construction of a new Sellindge double busbar bypass 400kV Substation. | 08/12/2023
|  | CS-05974 | SOUTH EASTERN POWER NETWORKS PLC | Ninfield GSP | NGET-RI-31338, NGET-RI-31339 & NGET-RI-21497-5 | Installation of Flexible AC Transmission Solutions (FACTS) at Bolney, Ninfield and Richborough and associated works. | 08/12/2023
Ninfield Greener Grid Park | PRO-001756 | CS-09681 | STATKRAFT UK LTD | Ninfield 400kV Substation | 101572-206183 | Extension of Sellindge OTS to include the User’s Battery Energy Storage system connection | 30/04/2027
|  | CS-09680 | STATKRAFT UK LTD | Ninfield 400kV Substation | 101572- 203150 | Installation of a new disconnector at a tee point on the HV side of Ninfield SGT4 | 30/04/2027
|  | CS-09683 | STATKRAFT UK LTD | Ninfield 400kV Substation | 031867-031867 | Thermal reinforcement to the South Coast; new Offshore HVDC link between Suffolk and Kent | 30/04/2027
|  | CS-09682 | STATKRAFT UK LTD | Ninfield 400kV Substation | 033773-033773 | Thermal upgrade of Bramley – Fleet 400kV double circuits. | 30/04/2027
Norfolk001 | PRO-001996 | CS-08274 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 101786-203723 | Reconductor BRIMSDOWN-HACKNEY4-1 (BRIM4C-HACK4-1) & BRIMSDOWN-HACKNEY4-2 (BRIM4D-HACK4-2) 400 kV circuit to achieve a higher MVA rating winter pre-fault. | 30/11/2031
|  | CS-08268 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 101872-203845 | Replace circuit breakers X110, X510 with higher ratings fault capability at Walpole 400kV Substation Replace circuit breakers X305, X705 with higher ratings fault capability at Walpole 400kV Substation | 30/11/2031
|  | CS-08270 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 101248-202488 | Reconductor SUNDON4-WYMONDLEY4-1 (SUND4-WYMO4-1) & SUNDON4-WYMONDLEY4-2 (SUND4-WYMO4-2) 400kV circuits to achieve a higher MVA rating summer pre-fault. | 30/11/2031
|  | CS-08276 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3820 MVA | 30/11/2031
|  | CS-08278 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 30/11/2031
|  | CS-08281 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 100875-201761 | Build a new 400 kV double circuit between Bramford 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter post-fault. | 30/11/2031
|  | CS-08269 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 30/11/2031
|  | CS-08275 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 30/11/2031
|  | CS-08267 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 101872-203844 | Extension of busbar to accommodate new generator bay at Walpole 400kV Substation | 30/11/2031
|  | CS-08272 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 100468-201037 | Reconductor EAST CLAYDON-LEIGHTON BUZZARD (ECLA4- LEIB4B- 1) 400kV circuit to achieve higher MVA rating summer pre-fault. | 30/11/2031
|  | CS-08271 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 101247-202487 | Reconductor LEIGHTON BUZZARD-SUNDON4-1 (LEIB4A-SUND4-1) & LEIGHTON BUZZARD-SUNDON4-2 (LEIB4B-SUND4-2) 400kV circuit to achieve a minimum rating of 2450MVA summer pre-fault rating. | 30/11/2031
|  | CS-08273 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 101885-203861 | Reconductor MILLBROOK-SUNDON 4-1 (MILB4-SUND4-1) & MILLBROOK-SUNDON 4-2 (MILB4-SUND4-2) 400kV circuit to achieve more than 1605MVA summer pre-fault rating | 30/11/2031
|  | CS-08277 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 30/11/2031
|  | CS-08279 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 100875-202039 | Build a new 400 kV double circuit between East Anglia Coastal 400 kV and Tilbury 400 kV substations with a minimum rating of 3000 MVA winter postfault. | 30/11/2031
|  | CS-08280 | EVOLUTION POWER LIMITED | Walpole 400kV Substation | 100875-202041 | At Tilbury 400kV Substation: Extension of busbars for the provision of 2 feeder bays for the CLAC-TILB OHL | 30/11/2031
Norfolk Boreas | PRO-000399 | CS-05493 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 20834-2 | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 01/10/2029
|  | CS-05494 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 20315L | At Bramford 400kV substation carry out OHL and cable works to enable the turn in of the Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 01/10/2029
|  | CS-05495 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 20315S | Construct an initial 9 bay 400kV GIS substation at Bramford as a 2 section substation with one bus coupler and two bus sections to be subsequently extended by a further section turning in existing Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 01/10/2029
|  | CS-05496 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 11630I | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 01/10/2029
|  | CS-05497 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 20834-3 | Install two switchable series reactors on the Tilbury and Coryton South feeder circuits at Rayleigh main. | 01/10/2029
|  | CS-05498 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 21847 | Building a new double circuit overhead line between the Bramford, Twinstead Tee and Pelham substation strung with 3x 700mm2 AAAC conductor at 750C (28km), connecting into the new Bramford 400kV GIS substation. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Twinstead Tee -Pelham double circuit and Bramford – Twinstead Tee – Braintree – Rayleigh Main double circuit. | 01/10/2029
|  | CS-05499 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 30637-1 | Build a new five bay 400kV AIS double busbar substation in the Lowestoft area, including two skeleton generator feeder bays, two feeder bays ad a bus coupler and additional works to enable the connection of 800MW. | 01/10/2029
|  | CS-05500 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 30637-2 | Tee in the Norwich to Bramford circuit to the new Lowestoft substation. | 01/10/2029
|  | CS-05501 | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 30641-1 | Cable sealing end work for the new OHL. | 01/10/2029
NorthConnect | PRO-001285 | CS-06299 | NORTHCONNECT LIMITED | Peterhead GSP | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 30/06/2027
North East Offshore Wind Farm | PRO-001436 | CS-06774 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-06775 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-06776 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-06777 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-06778 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 31/10/2033
|  | CS-06779 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-06780 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-06781 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-06782 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-06783 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-06784 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2033
|  | CS-06785 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-06786 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-06787 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-06788 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-06789 | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation | NEOWF Enabling Works | At New Deer 2 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Onshore Transmission Licensee and the User will be the User side of the 400kV feeder circuit breaker/isolators at New Deer 2 400kV substation. | 31/10/2033
North Falls Offshore Wind Farm | PRO-000451 | CS-06309 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100874-201758 | Build a new 11 bay East Anglia Coastal 400 kV double busbar substation – 2off busbar couplers, 1 Main & Reserve section, 8 feeder bays | 31/10/2030
|  | CS-06310 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100532-201151 | At East Anglia Coastal 400kV Substation: Single Bay Extension to facilitate 100532-201151 the User’s connection. | 31/10/2030
|  | CS-06311 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 31/10/2030
|  | CS-06312 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100875-201762 | Build a second new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent | 31/10/2030
|  | CS-06313 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100874-201760 | Build a new 400 kV double circuit between Sizewell 400 kV and East Anglia Coastal 400 kV substations with a minimum rating of 3000 MVA winter postfault. Extension of Sizewell 400 kV substation to accommodate 2 feeders from East Anglia Coastal 400 kV. | 31/10/2030
|  | CS-06314 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100879-201769 | Install 2-off 225 Mvar MSCs at Bramford 400 kV substation.Extension of Bramford 400 kV substation to accommodate the new MSCs. | 31/10/2030
|  | CS-06315 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 31/10/2030
|  | CS-06316 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation |  | FALSE | 31/10/2030
|  | CS-06317 | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 31/10/2030
NorthFleet 2 BESS | PRO-002322 | CS-08574 | CSE41 LIMITED | NorthFleet 400kV Substation | 102186-204403 | 1. Extension of the GIS building and busbars at Northfleet 400kV Substation to accommodate User bay. 2. Database updates to capture additional signals from customer populated bay. 3. SAP commissioning resource for bay population. | 31/10/2028
NorthFleet Tertiary | PRO-002038 | CS-08575 | CSE29 LIMITED | NorthFleet 400kV Substation | 101918-203917 | 1. Make connections on the SGT 4. 2. Condition assessment of 13kV cable and other assets to confirm suitability for reuse. 3. Install earthing transformer on 13kV Tertiary connection. 4. Install 13kV Cable (if required) from 13kV Tertiary connection to the 13kV Disconnector. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 30/06/2026
North Killingholme Power Project | PRO-001038 | CS-05975 | C.GEN KILLINGHOLME LIMITED | Killingholme 400kV Substation | NGET-RI-30544 | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | 31/10/2026
|  | CS-05976 | C.GEN KILLINGHOLME LIMITED | Killingholme 400kV Substation | NGET-RI-21406S | Extension of 400kV busbars and substation building and installation of series reactor for generation connections at Killingholme 400kV Substation. Extension to the existing South Humber Bank Operational Tripping Scheme | 31/10/2026
|  | CS-05977 | C.GEN KILLINGHOLME LIMITED | Killingholme 400kV Substation | NGET-RI-32278SI | Extend the busbar and a GIS skeletal bay and the associated foundation to provide 490MW CCGT connection. | 31/10/2026
North Kyle New Cumnock | PRO-000474 | CS-05978 | NORTH KYLE WIND FARM LIMITED | New Cumnock 132kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/04/2024
|  | CS-05979 | NORTH KYLE WIND FARM LIMITED | New Cumnock 132kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 30/04/2024
|  | CS-05980 | NORTH KYLE WIND FARM LIMITED | New Cumnock 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/04/2024
North Lanrigg Battery Storage | PRO-002671 | CS-09182 | North Lanrigg Battery Storage Ltd | North Lanrigg Substation | Newarthill line works | Replace / reconfigure the downleads from the terminal tower into Newarthill 275kV substation and rebuild the line entry on the Wishaw-Newarthill double circuit overhead line route (XR Route). | 30/10/2028
|  | CS-09184 | North Lanrigg Battery Storage Ltd | North Lanrigg Substation | Line Disconnector - North Lanrigg | Install a 275kV line disconnector on the cable side of the User’s connection | 30/10/2028
|  | CS-09186 | North Lanrigg Battery Storage Ltd | North Lanrigg Substation | Line Disconnector (User SS) - North Lanrigg | Install a 275kV line disconnector at the North Lanrigg 275kV substation | 30/10/2028
|  | CS-09185 | North Lanrigg Battery Storage Ltd | North Lanrigg Substation | 275kV Circuit - North Lanrigg | Install a 275kV cable circuit to the User’s site. As part of the desktop exercise the cable circuit length is circa 2km | 30/10/2028
|  | CS-09183 | North Lanrigg Battery Storage Ltd | North Lanrigg Substation | Newarthill Substation Works | Tee off the 275kV busbars at Newarthill 275kV Substation and install a 275kV line disconnector and new “S50” 275kV circuit breaker. | 30/10/2028
North Lowther Energy Initiative | PRO-000344 | CS-05981 | NLEI LTD | NLEI GSP | NLEI H1 Sole enabling works | 3. Installation of two 132kV line isolators at NLEI Wind Farm. 2. Installation of approximately 14km overhead line between Elvanfoot 132kV substation and NLEI wind farm. 1. Installation of a 132kV circuit breaker at Elvanfoot substation with transformer and line disconnectors Protection and control modifications as required Associated civil works Miscellaneous and Minor works | 01/04/2028
|  | CS-05982 | NLEI LTD | NLEI GSP | SPT-RI-226 | Installation of a new 275/132kV 360MVA transformer and a new 132kV busbar at Elvanfoot substation, to allow new generators to connect. | 01/04/2028
North Mains Battery Storage Park | PRO-001659 | CS-04480 | RELAY SUTTIESIDE LIMITED | Lunanhead GSP | North Mains Battery Storage Park H1 Works item 3 | 3. An intertrip is required for the loss of one of the Grid Transformers at Lunanhead 132/33kV GSP. a. These signals shall be provided by the Host Distribution Network Operator via a separate relay panel within the 33kV Switchroom from the signals described below. b. Provision of status signals are required for the following: i. 1TO and 2TO 33kV circuit breakers at Lunanhead GSP. ii. 1T7 and 2T7 33kV disconnectors at Lunanhead GSP. iii. 115 and 215 132kV circuit breakers at Lunanhead GSP. | 31/10/2025
|  | CS-04478 | RELAY SUTTIESIDE LIMITED | Lunanhead GSP | North Mains Battery Storage Park H1 Works item 2 | 2. Replacement or modification of the Battery Systems, LVAC Board and Standby Generator at Lunanhead 132/33kV GSP, along with the upgrade of communication links between Lunanhead 132/33kV GSP substation and Tealing 132kV substation. | 31/10/2025
|  | CS-04479 | RELAY SUTTIESIDE LIMITED | Lunanhead GSP | North Mains Battery Storage Park H1 Works item 1 | 1. The installation of four new protection bays, two at each of the remote ends between Tealing substation and Lunanhead substation. There is also a requirement to install two new VTs on both circuits at Lunanhead substation. | 31/10/2025
North Sea | PRO-001375 | CS-04384 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 16 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 01/01/2033
|  | CS-04385 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100909-201825 | Uprate the existing bays in the Creyke Beck – Thornton 2 circuit (A323) to achieve a post fault summer rating of 3300MVA. | 01/01/2033
|  | CS-04386 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm2 AAAC sections of the circuits with 2×591mm2 ACCR conductor and the 2x700mm2 AAAC sections with 3x700mm2 AAAC conductor | 01/01/2033
|  | CS-04387 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100161-200456 | At Eggborough 400kV: Replace circuit breakers X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/01/2033
|  | CS-04388 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100987-201984 | Uprate the existing bays in the Creyke Beck – Thornton 1 circuit to achieve a post fault summer rating of 3300MVA. | 01/01/2033
|  | CS-04389 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100594-201224 | At Eggborough 400kV: Replace circuit breakers X105, X205, X605, X160, X305, X405 and X805. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/01/2033
|  | CS-04390 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 01/01/2033
|  | CS-04391 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 01/01/2033
|  | CS-04392 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100941-201873 | At Cottam 400kV Substation: Install a 2750MVA QB on the COTT-WBUR circuit | 01/01/2033
|  | CS-04393 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 01/01/2033
|  | CS-04394 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100951-201898 | Uprate West Burton - High Marnham (A403) cable section to provide a postfault winter rating of 3100MVA | 01/01/2033
|  | CS-04395 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 01/01/2033
|  | CS-04396 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 01/01/2033
|  | CS-04366 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100975-201954 | Convert the current 132kV circuit up to 400kV refurbishing/replacing where necessary | 01/01/2033
|  | CS-04367 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 101093-202180 | 0 | 01/01/2033
|  | CS-04368 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 101093-202181 | Construct a new 400 kV double circuit out of North Humber Coastal substation to a new Killingholme South 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit | 01/01/2033
|  | CS-04369 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 033837-201648 | At Creyke Beck 400kV Substation: Move Creyke Beck - Thornton 2 circuit and Creyke Beck - Humber Refinery - Keadby circuit to the new GIS Creyke Beck 400kV Compound. | 01/01/2033
|  | CS-04370 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/01/2033
|  | CS-04371 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 101093-202182 | Build a new 400kV North Humber Coastal Substation with 6 Bays - 4 Feeder bays, 1 Coupler Bay, 2 Section Breakers Main and Reserve | 01/01/2033
|  | CS-04372 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 033837-201012 | At Creyke Beck 400kV Substation: Build a new 400kV double busbar compound with 2 feeders bays, 1 coupler bay, 1 section bay, 2 transformer bays and transfer SGT1 and SGT2 from the existing substation to the new compound. Connect 2 new interconnectors to Creyke Beck 400kV substation by utilising the vacated SGT1 and SGT2 bays. | 01/01/2033
|  | CS-04373 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100206-200545 | Installation of a 225MVAr MSC at West Burton 400kV substation | 01/01/2033
|  | CS-04374 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 033837-201650 | At Creyke Beck 400kV: Replace circuit breakers X110, X130 and X210. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/01/2033
|  | CS-04375 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100944-201880 | Build a new 400kV Killingholme South Substation with: 8 feeder bays, 1 section bay and 2 couplers. | 01/01/2033
|  | CS-04376 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100944-201881 | Build a new 400 kV double circuit between Killingholme South and 100944-201881 Mablethorpe substations Build a new 400kV Mablethorpe | 01/01/2033
|  | CS-04377 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100946-201889 | At Killingholme 400kV GIS substation: Replace circuit breakers X430, X460, X420, X530, X130, X120, X960, X920, X930, X140, X305. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/01/2033
|  | CS-04378 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100944-201883 | Build a new 400 kV double circuit between Mablethorpe and Weston Marsh Substations | 01/01/2033
|  | CS-04379 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main & Reserve | 01/01/2033
|  | CS-04380 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100946-201893 | At Killingholme 400kV GIS substation: Replace circuit breakers X145 (R9 Series Reactor Breaker). Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/01/2033
|  | CS-04381 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100821-201659 | Uprating of the Creyke Beck - Humber Refinery – Keadby and Creyke Beck - Keadby – Killingholme 4ZQ circuits to achieve a post-fault summer rating of 3320MVA | 01/01/2033
|  | CS-04382 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100821-201989 | Uprating of the Creyke Beck - Humber Refinery – Keadby and Creyke Beck - Keadby – Killingholme circuits to achieve at least 3320MVA post fault summer - On 2KN and 2AC legs as required | 01/01/2033
|  | CS-04383 | RWE RENEWABLES UK LIMITED | RWE North Sea Offshore Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors and protection on both Thornton circuits at Drax substation to equipment with an equal rating to provide a post-fault winter rating of 3420MVA | 01/01/2033
Norton | PRO-001537 | CS-06903 | BAYWA R.E. UK LIMITED | Norton 400kV Substation | 101241 -202468 | 1. Extend the Norton site as required to facilitate the transmission works. 2. Install a tertiary cable box or bushings on the SGT 2. 3. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 4. Install an earthing transformer. 5. Install a 13kV disconnector at the 13kV side connecting the tertiary winding to the Connection Assets. | 01/05/2025
| PRO-002157 | CS-08712 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 100035-200062 | Uprating/Replacement of the following Circuit Breakers at Spennymoor 132kV substation: 120 and 130 | 31/10/2032
|  | CS-08713 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101714-203420 | Installation of 2x200 MVAr MSC at the new High Marnham 400 kV double busbar substation | 31/10/2032
|  | CS-08725 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 100459-201024 | Uprate the new High Marnham - Stoke Bardolph 400kV circuit (A41E) to provide a pre-fault summer rating of 2800MVA | 31/10/2032
|  | CS-08730 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101717-203426 | Installation of 2x200 MVAr MSC at Thorpe Marsh 400 kV substation | 31/10/2032
|  | CS-08707 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101333-202653 | Establish a new 400kV substation, provisionally referred to as Norton East. A 400kV 6-bay AIS DBB Substation, compromising of 2 feeder bays, one bus coupler, three generator bays. The new substation will be connected via a turn in of the existing 400kV Norton - Saltholme cct to form the new Norton East-Norton-Salthold cct. | 31/10/2032
|  | CS-08714 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 31/10/2032
|  | CS-08723 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 100450-201015 | Uprate the Cottam - Keadby 1 and 2 circuits to achieve a post fault winter rating of 3300MVA. | 31/10/2032
|  | CS-08728 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101667-203320 | Installation of 2x200 MVAr MSC at Cottam 400kV substation | 31/10/2032
|  | CS-08733 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101718-203427 | Installation of 2x200MVAr MSC at West Burton 400kV substation | 31/10/2032
|  | CS-08715 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 31/10/2032
|  | CS-08724 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 31/10/2032
|  | CS-08729 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101386-202715 | Uprate the Lackenby - Thornton 1 and 2 circuits to achieve a pre fault summer rating of 2250MVA | 31/10/2032
|  | CS-08716 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 31/10/2032
|  | CS-08710 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 31/10/2032
|  | CS-08719 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101041-202083 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +8 ohms along the Cottam – West Burton 1 (A413) 400kV circuit | 31/10/2032
|  | CS-08721 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 31/10/2032
|  | CS-08726 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 31/10/2032
|  | CS-08732 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101719-203428 | Uprate the Norton leg of the new Norton- Osbaldwick/ Poppleton 400 kV circuits to provide a pre-fault summer rating of 2350 MVA | 31/10/2032
|  | CS-08727 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 31/10/2032
|  | CS-08706 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 31/10/2032
|  | CS-08708 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101990-204121 | Busbar extension at Norton East 400kV to provide required space for connection of a new user generator bay | 31/10/2032
|  | CS-08731 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101576-203163 | Uprate the Osbaldwick leg of the new Norton- Osbaldwick/ Poppleton 400kV circuits to provide a pre-fault summer rating of 1700 MVA | 31/10/2032
|  | CS-08717 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 100455-201020 | At Keadby 400kV substation: • Transpose the Cottam 1 circuit with the West Burton 1 circuit. Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax –Keadby – Thorpe Marsh 400 kV circuit | 31/10/2032
|  | CS-08718 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101663-203316 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pulling mode capable of injecting up to -8 ohms along the Bicker Fen – West Burton 1 (A685) 400kV circuit | 31/10/2032
|  | CS-08720 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 31/10/2032
|  | CS-08709 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV and High Marnham 400kV substation including all associated substation works known as Humber Trent Green | 31/10/2032
|  | CS-08722 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101504-202965 | Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit to provide a post-fault summer rating of 3300 MVA:  Reconductor the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for the Drax – Keadby – Thorpe Marsh circuit. | 31/10/2032
|  | CS-08711 | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation | 101712-203416 | Uprating/Replacement of the following CB at Stella West 275 kV substation: H10, H20, H40, H50, H90, S10 and W10 | 31/10/2032
Norton PV and BESS | PRO-001437 | CS-04647 | Darlington Solar 1 Limited | Norton 400kV Substation | 101158-202333 | 1. Extend the Norton site as required to facilitate the transmission works 2. Install a tertiary cable box or bushings on the SGT 1 3. Install a 13kV cable (if required) from the tertiary cable box or bushings to the earthing transformer 4. Install an earthing transformer 5. Install a 13kV disconnector at the 13kV side connecting the tertiary winding to the User’s Assets. | 31/10/2024
Norton Solar Farm | PRO-001875 | CS-07285 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 31/10/2031
|  | CS-07286 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 100455-201020 | 1. Transpose the Cottam 1 circuit with the West Burton 1 circuit at Keadby 400kV substation. 2. Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby – Thorpe Marsh 400 kV circuit | 31/10/2031
|  | CS-07287 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101663-203316 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pulling mode capable of injecting up to -8 ohms along the Bicker Fen – West Burton 1 (A685) 400kV circuit | 31/10/2031
|  | CS-07288 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101041-202083 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +8 ohms along the Cottam – West Burton 1 (A413) 400kV circuit | 31/10/2031
|  | CS-07289 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101703-203406 | Install a power control device along the Drax -Thornton circuit to limit power flows | 31/10/2031
|  | CS-07290 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 100459-201024 | 0 | 31/10/2031
|  | CS-07291 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 31/10/2031
|  | CS-07292 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 31/10/2031
|  | CS-07293 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101504-202965 | Uprate the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit to provide a post-fault summer rating of 3300 MVA:  Reconductor the Drax and Thorpe Marsh legs of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for the Drax – Keadby – Thorpe Marsh circuit. | 31/10/2031
|  | CS-07294 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 100450-201015 | Uprate the Cottam - Keadby 1 and 2 circuits to achieve a post fault winter rating of 3300MVA. | 31/10/2031
|  | CS-07295 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors on both Thornton circuits at Drax substation, to equipment with an equal rating to provide a post fault winter rating of 3420MVA | 31/10/2031
|  | CS-07296 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101667-203320 | Installation of 2x200 MVAr MSC at Cottam 400kV substation | 31/10/2031
|  | CS-07297 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-07298 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101386-202715 | 0 | 31/10/2031
|  | CS-07299 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101717-203426 | Installation of 2x200 MVAr MSC at Thorpe Marsh 400 kV substation | 31/10/2031
|  | CS-07300 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101576-203163 | 0 | 31/10/2031
|  | CS-07301 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101719-203428 | Uprate the Norton leg of the new Norton- Osbaldwick/ Poppleton 400 kV circuits to provide a pre-fault summer rating of 2350 MVA | 31/10/2031
|  | CS-07274 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101665-203318 | Uprating/Replacement of the following CB at Norton 275 kV substation: H10, H30 and H50 | 31/10/2031
|  | CS-07275 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101333-202653 | Establish a new 400kV substation, provisionally referred to as Norton East 400kV, to the East of the existing Norton 400kV substation. Connect the new substation to the transmission system via a turn in of the existing Norton – Saltholme 400kV circuit to form a new Norton – Norton East 400kV and Norton East – Saltholme 400kV circuit | 31/10/2031
|  | CS-07276 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 31/10/2031
|  | CS-07278 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101710-203413 | Busbar extension at Norton East 400kV to provide required space for connection of a new high impedance 240 MW 400/132 kV Supergrid Transformers (SGT) | 31/10/2031
|  | CS-07279 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 31/10/2031
|  | CS-07280 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101712-203416 | Uprating/Replacement of the following CB at Stella West 275 kV substation: H10, H20, H40, H50, H90, S10 and W10 | 31/10/2031
|  | CS-07281 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 31/10/2031
|  | CS-07282 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 100035-200062 | Uprating/Replacement of the following Circuit Breakers at Spennymoor 132kV substation: 120 and 130 | 31/10/2031
|  | CS-07283 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101714-203420 | Installation of 2x200 MVAr MSC at the new High Marnham 400 kV double busbar substation | 31/10/2031
|  | CS-07284 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 31/10/2031
|  | CS-07302 | JBM SOLAR PROJECTS 29 LIMITED | Norton GSP | 101718-203427 | 0 | 31/10/2031
Norwich | PRO-001077 | CS-05277 | PIVOTED POWER LLP | Norwich GSP | 100549-201125 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 72.5kV, 40kA Disconnecting Circuit Breaker (DCB) at 13kV side connecting Tertiary to Connection Assets for User’s connection. | 31/10/2024
|  | CS-05278 | PIVOTED POWER LLP | Norwich GSP | 033804-201295 | 1. Construction of Norwich Main 400kV – Necton 400kV double turn in. *Norwich Main 400kV – Necton 400kV double turn in works required for SQSS compliance under the circuit complexity. | 31/10/2024
Norwich 100MW BESS | PRO-002126 | CS-08130 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 31/10/2031
|  | CS-08134 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 31/10/2031
|  | CS-08131 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400kV with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 31/10/2031
|  | CS-08120 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100952-201899 | Reconductor EAST CLAYDON-LEIGHTON BUZZARD (ECLA4- LEIB4B-1) 400kV circuit to achieve a minimum rating of 2450MVA summer pre-fault rating | 31/10/2031
|  | CS-08124 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 31/10/2031
|  | CS-08128 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100944-201883 | Build a new 400 kV double circuit between Lincolnshire Coastal and Weston Marsh Substations | 31/10/2031
|  | CS-08118 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 030477-030447 | 1. Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 31/10/2031
|  | CS-08127 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 31/10/2031
|  | CS-08132 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 033461- 033461 | Post-completion of BTNO works, reconductor Bramford-Pelham 1 400kV circuits with 3 x700mm2 AAAC conductors to achieve a post-fault winter rating of 3100 MVA | 31/10/2031
|  | CS-08135 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 31/10/2031
|  | CS-08136 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 101883-203859 | Uprating of the Coryton South – Rayleigh Main (A68A) 400kV circuit cables to achieve 3002MVA pre-fault summer rating | 31/10/2031
|  | CS-08126 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 31/10/2031
|  | CS-08119 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100468-201037 | COWLEY – LEIGHTON BUZZARD (COWL4-LEIB4A-1) to achieve a minimum rating of 2010MVA summer pre-fault. | 31/10/2031
|  | CS-08121 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 101247-202487 | Reconductor LEIGHTON BUZZARD-SUNDON4-1 (LEIB4A-SUND4-1) & LEIGHTON BUZZARD-SUNDON4-2 (LEIB4B-SUND4-2) 400kV circuit to achieve a minimum rating of 2450MVA summer pre-fault rating. | 31/10/2031
|  | CS-08117 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 101975-204100 | 1. At Kings Lynn 400kV: Ensure circuit break X130 to be rated to 63kA with tested X/R ration of at least 28 and a peak withstand of at least 2.7 x RMS break | 31/10/2031
|  | CS-08123 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100590-201212 | Reconductor the existing 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit to achieve more than 1800MVA summer prefault rating. | 31/10/2031
|  | CS-08116 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 31/10/2031
|  | CS-08113 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 31/10/2031
|  | CS-08133 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 31/10/2031
|  | CS-08115 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 31/10/2031
|  | CS-08114 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 31/10/2031
|  | CS-08112 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 102187-204404 | 1. Undertake substation database change to accommodate the tee connection of Norwich 100MW BESS 2. Protection and control modification as a result of Norwich 100MW BESS | 31/10/2031
|  | CS-08122 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm2 and 3M curlew 2x490mm2 @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm2 conductor | 31/10/2031
|  | CS-08125 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-08129 | FLEXION ENERGY SPV 2 LTD | Norwich Main 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 31/10/2031
Norwich Green Energy Centre | PRO-001771 | CS-05314 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 101343-202663 | Extension of MBB4 and RBB4 bus of Norwich Main 400kV substation on west side to accommodate the user’s connection. | 30/04/2031
|  | CS-05315 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 100709-201476 | At Norwich Main 400kV Substation: Extend substation by 1 bay to accommodate a new circuit Bramford - Norwich Main 4. Transfer existing Bramford 1 circuit to the spare bay to accommodate the second new circuit Bramford - Norwich Main 3. | 30/04/2031
|  | CS-05316 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 101294-202560 | At Norwich Main 400kV: Replace circuit breakers X120, X230, X210, X410 and X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 30/04/2031
|  | CS-05317 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 30/04/2031
|  | CS-05319 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 100881-201773 | Install two 225 Mvar MSCs at Norwich Main 400 kV substation. Extension of Norwich Main 400 kV substation to accommodate the new MSCs. | 30/04/2031
|  | CS-05320 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 30/04/2031
|  | CS-05321 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 30/04/2031
|  | CS-05322 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 032452-203187 | Extension of the existing 400kV substation for the construction of fully populated main and reserve bus section bays with circuit breakers, one new bus coupler bay and one new feeder bay to accommodate transfer of the Norwich Main – Bramford 1 feeder circuit | 30/04/2031
|  | CS-05323 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 30/04/2031
|  | CS-05324 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 30/04/2031
|  | CS-05325 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3820 MVA | 30/04/2031
|  | CS-05326 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 033750-033750 | Uprate the circuit bay Busbar, CT and Circuit Breaker attached to existing A654 circuit (BRFO-PELH) and uprate the circuit bay Busbar, CT, Circuit Breaker, disconnector and main protection system on the newly formed second Bramford – Pelham circuit (currently part of A646 BRFO-BRAI circuit) to achieve a post fault winter rating of 3820MVA | 30/04/2031
|  | CS-05329 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 021071-021073 | Loop into the new Kings Lynn B 400kV substation with the near side Norwich-Walpole 400kV circuit to form a Walpole- Kings Lynn B and Kings Lynn - Necton - Norwich Main circuit connection. Construction of a new 2.7km double circuit | 30/04/2031
|  | CS-05331 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 30/04/2031
|  | CS-05332 | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 30/04/2031
NPI A Offshore | PRO-001628 | CS-04422 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-04423 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-04424 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-04425 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-04426 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2033
|  | CS-04427 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 31/10/2033
|  | CS-04428 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-04429 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-04430 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-04431 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-04432 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-04433 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-04434 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-04435 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-04436 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 31/10/2033
|  | CS-04437 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-04420 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | NPI A H1 Enabling Works | At Dounreay 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV circuit breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Onshore Transmission Licensee and the User will be the User side of the new 400kV disconnectors (X603/X703) at New Dounreay 400kV substation. | 31/10/2033
|  | CS-04421 | Northland Power UK Limited | NPI A 275/66kV Offshore Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
Oaklands Farm Solar PV | PRO-001004 | CS-05368 | BAYWA R.E. UK LIMITED | Drakelow 132kV Substation | 100867-201733 | 1. Asset transfer of spare skeletal bay at Drakelow 132kV substation from the Relevant Transmission Licensee to the User 2. Database changes and protection modifications to facilitate connection of the Users bay | 01/06/2025
Oakley | PRO-003818 | CS-08921 | SSE DE SOLAR HOLDCO LIMITED | Oakley 400kV Substation | 102602-205224 | 1. New 400kV double busbar (M2/R2) Oakley substation to provide space for User’s generation connection bay in a strategic location between Cowley & East Claydon. (*Substation name, design and location subject to further engineering assessment during the Relevant Transmission Licensee option selection phase). 2. Build temporary overhead line to divert the Cowley – East Claydon 400kV transmission circuit to allow for turning in this circuit and to feed the new 400kV substation. Establish a single turn in connection between Cowley – East Claydon circuit to connect the new substation. 3. Extension of 400 kV busbars to connect user bay. | 20/10/2037
Ocker Hill Tertiary Connection | PRO-000462 | CS-06906 | HD143OCK LTD | Ocker Hill 275kV Substation | 100785-201585 | 1. Install a tertiary cable box or bushings on SGT1 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer at the 13kV side. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 31/10/2023
Oldbury (Tertiary) | PRO-001074 | CS-05279 | PIVOTED POWER LLP | Oldbury 275kV Substation | 100625-201291 | 1. Install earthing transformer on 13kV Tertiary connection. 2. Install 13kV cable from 13kV Tertiary connection to Disconnecting Circuit Breaker (DCB). 3. Install Disconnecting Circuit Breaker (DCB) at the 13kV side connecting tertiary to connection assets for Users connection. | 01/11/2025
Old Flatts Farm | PRO-001894 | CS-07321 | Net Zero One Limited | Brinsworth 275kV Substation | 101713-203417 | 0 | 01/09/2027
Old Forest of Ae | PRO-001075 | CS-04273 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Old Forest of Ae 33kV Substation | Old Forest of Ae H1 SS | Installation of 132kV line disconnector at Old Forest of Ae WF substation | 31/10/2027
|  | CS-04274 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Old Forest of Ae 33kV Substation | Old Forest of Ae H1 OHL | Installation of a 20km 132kV OHL circuit using AAAC “Poplar” conductor. | 31/10/2027
Old Greenock Road | PRO-000834 | CS-04419 | SP Distribution plc | Erskine GSP | SPT-RI-243 - Devol Moor-Erskine-Braehead Park Circuit LMS | A Load Management Scheme (LMS) is required to manage connections in the Neilston – Devol Moor 132 kV group to prevent overloads on the Devol Moor-Erskine-Braehead Park Circuit. The overload will be removed by the LMS tripping the appropriate non-firm connections. | 31/10/2023
Olivers Forest Wind Farm | PRO-002648 | CS-09436 | Oliver Forest Wind Farm Limited | Olivers Forest Wind Farm 132kV Substation | SPT-RI-3060 | Redshaw 132kV “B” Board - Establish a new 132kV double busbar substation, indicatively named Redshaw 132kV “B” board at the new Redshaw 400/132kV substation. The location of the SPT’s new 400kV substation (which this 132kV double busbar site will connect into) will be connected in the existing ZV Route corridor (STHA-ELVA / COAL-ELVA) as well as facilitate the new double circuit from Glenmuckloch under SPT-RI-236. The 400kV substation at Redshaw is being constructed under SPT-RI-2060. The 132kV double busbar substation to be established here will also require installation of two 400/132kV 360MVA transformers. (SPT-RI3060) | 30/04/2031
|  | CS-09434 | Oliver Forest Wind Farm Limited | Olivers Forest Wind Farm 132kV Substation | Olivers Forest Wind Farm H1 | Installation of a new 132kV feeder bay at Redshaw 132kV substation on the new “B” board. This feeder bay shall include the associated main and reserve busbar disconnectors and line disconnector. Installation of a new 132kV circuit between Redshaw 132kV and Oliver’s Forest Wind Farm 132kV substations comprising of both 132kV cable and OHL. The indicative length of the circuit is 21.9km using an L4 steel tower construction. Installation of a 132kV line disconnector at Oliver’s Forest Wind Farm 132kV substation | 30/04/2031
|  | CS-09435 | Oliver Forest Wind Farm Limited | Olivers Forest Wind Farm 132kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 30/04/2031
One Planet Solar Farm | PRO-001505 | CS-06913 | ONE PLANET SOLAR FARM LIMITED | Eaton Socon 400kV Substation | 101298-202581 | Install a Power Control Technology along Sundon-Wymondley 400kV circuits 1 and 2 | 31/10/2029
|  | CS-06907 | ONE PLANET SOLAR FARM LIMITED | Eaton Socon 400kV Substation | 101245-202485 | Reconductor the existing 4x400mm2 conductor on the Eaton Socon – Wymondley 2 400kV circuit with 2x850mm2 90oC conductor to achieve a pre fault summer rating of 2400 MVA | 31/10/2029
|  | CS-06908 | ONE PLANET SOLAR FARM LIMITED | Eaton Socon 400kV Substation | 100591-201213 | Reconductor Ratcliffe – Staythorpe 400kV circuit; reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 2780MVA | 31/10/2029
|  | CS-06909 | ONE PLANET SOLAR FARM LIMITED | Eaton Socon 400kV Substation | 100952-201899 | Uprate all three downdroppers on the East Claydon - Leighton Buzzard - Sundon circuit to provide a pre-fault summer rating of 2400MVA | 31/10/2029
|  | CS-06910 | ONE PLANET SOLAR FARM LIMITED | Eaton Socon 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 31/10/2029
|  | CS-06911 | ONE PLANET SOLAR FARM LIMITED | Eaton Socon 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 31/10/2029
|  | CS-06912 | ONE PLANET SOLAR FARM LIMITED | Eaton Socon 400kV Substation | 021742-021742 | Two of the existing four Tottenham–Brimsdown–Waltham Cross circuits are uprated to 400kV operation [B623, B624, B625, B626). | 31/10/2029
|  | CS-04631 | ONE PLANET SOLAR FARM LIMITED | Eaton Socon 400kV Substation | 101236-202460 | Extension of the existing Eaton Socon 400kV substation Main and Reserve Busbars to accommodate the User’s bay | 31/10/2029
Orkney Finstown Embedded Generation | PRO-000729 | CS-04439 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/04/2023
|  | CS-04440 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-019 | Establish a 220kV HVAC circuit over a distance of approximately 68km between the 275kV GIS substation at Dounreay on the mainland and the new 132kV substation in the vicinity of Finstown on Orkney. The HVAC circuit comprises of approximately 15km of land cable and 53km of subsea cable. Voltage Compensation devices will be installed at both cable ends within the substation compounds at Dounreay and Finstown. | 30/04/2023
|  | CS-04441 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 30/04/2023
|  | CS-04442 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 30/04/2023
|  | CS-04443 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 30/04/2023
|  | CS-04444 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-036 | Beauly – Loch Buidhe 275kV BUW Reconductoring – Re-conductor part of the first 275kV circuits (BT1-Beauly-Kilbraur-Gordonbush-Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substations (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay completed as part of SHET-RI-006 works. (SHET-RI-036). | 30/04/2023
|  | CS-04445 | Scottish Hydro Electric Power Distribution Plc | Finstown (Orkney) GSP | SHET-RI-020 | Establish an HVDC link from Orkney to Peterhead in a phased manner to allow connection of marine and other renewable generation on and around the coast of Orkney. The works included in comprise an extension to the 132kV double busbar substation and a 600MW HVDC link from the northwest coast of Orkney to a HVDC switching station located inland in the vicinity of Sinclair’s Bay in Caithness. The HVDC link between Northwest Orkney and Sinclair’s Bay will have both land and subsea cable sections. | 30/04/2023
Orsted Celtic Sea (OCS01) | PRO-003100 | CS-08227 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 102303-204527 | Infrastructure works for the generation connection of OCS01 offshore wind farm | 06/12/2036
|  | CS-08231 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 06/12/2036
|  | CS-08229 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-08233 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-08228 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 06/12/2036
|  | CS-08234 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 06/12/2036
|  | CS-08230 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
|  | CS-08232 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
Orsted Celtic Sea 2 (OCS02) | PRO-003101 | CS-08239 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 06/12/2036
|  | CS-08235 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 102292-204530 | Infrastructure works for the generation connection of OCS02 offshore wind farm. | 06/12/2036
|  | CS-08236 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 06/12/2036
|  | CS-08237 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-08240 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
|  | CS-08241 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-08242 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 06/12/2036
|  | CS-08238 | ORSTED POWER (UK) LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
Osprey | PRO-002654 | CS-08092 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-08091 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 06/12/2036
|  | CS-08096 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-08093 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
|  | CS-08095 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
|  | CS-08097 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 06/12/2036
|  | CS-08090 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Alverdiscott 400kV Substation | 102154-204358 | Infrastructure works for the generation connection of BP Osprey offshore wind farm | 06/12/2036
|  | CS-08094 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 06/12/2036
Ourack Wind Farm | PRO-001490 | CS-07663 | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation | Ourack Wind Farm Enabling Works | 1. Installation of a new 132kV double busbar feeder bay comprising of 1 x 132kV line circuit breaker, 1 x 132kV line disconnector and associated protection and control equipment at Clash Gour 275/132kV Collector Substation. 2. Establish a new 132kV single circuit connection between Clash Gour 275/132kV Collector Substation and the Ourack 132/33kV substation at the wind farm site. This will comprise of a 10km section of 132kV overhead steel structure line. The new 132kV circuit will terminate into a new 132kV line disconnector and circuit breaker installed at Ourack 132/33kV substation | 31/10/2030
|  | CS-07666 | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2030
|  | CS-07664 | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation | SHET-RI-007A | Replace the existing Beauly/Inverness/Nairn/Elgin/Keith 132kV double circuit line with 400kV construction. One circuit will be operated at 400kV and the other circuit at 132kV to serve the Inverness and Elgin substations. Establish a 400/132kV substation at Nairn to serve Nairn substation and to secure the group demand served from the 132kV circuit. | 31/10/2030
|  | CS-07665 | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 31/10/2030
|  | CS-07667 | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation | SHET-RI-146 | Clash Gour 275/132kV Collector Substation - The Clash Gour 275/132kV Collector Substation works include establishment of a double 132kV busbar and installation of two 240/480MVA 275/132kV transformers. | 31/10/2030
Ouse Energy Storage | PRO-001861 | CS-06890 | Ouse Energy Limited | Kemsley 400kV Substation | 101685-203354 | 1. Relocation of existing Kemsley 400kV Main and Reserve Busbar disconnectors to accommodate Users Bay 2. Reconfiguration of Kemsley 400kV Main and Reserve Busbars to accommodate Users Bay | 24/08/2026
|  | CS-06891 | Ouse Energy Limited | Kemsley 400kV Substation | 020865-020865 | Uprate Kemsley - Rowdown - Littlebrook double OHL circuit to achieve a post-fault winter rating of 2800MVA | 24/08/2026
|  | CS-06892 | Ouse Energy Limited | Kemsley 400kV Substation | 100116-200307 | Uprate Kingsnorth - Tilbury and Grain - Tilbury 400 kV circuits to achieve a 2350 MVA pre-fault and 3200 post fault winter rating | 24/08/2026
|  | CS-06893 | Ouse Energy Limited | Kemsley 400kV Substation | 100116-200654 | New GRAI - TILB/KINO - TILB tunnel to achieve required 3300 MVA rating (2 cables per phase) | 24/08/2026
Overhill Wind Farm | PRO-000472 | CS-06712 | ENERGYFARM UK OVERHILL LLP | Overhill WF 132kV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 30/06/2027
|  | CS-06713 | ENERGYFARM UK OVERHILL LLP | Overhill WF 132kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 30/06/2027
|  | CS-03728 | ENERGYFARM UK OVERHILL LLP | Overhill WF 132kV Substation | Overhill H1 | At Overhill 132kV substation install 132kV line isolator. Install approximately 3km underground cable circuit from Overhill 132kV substation to New Cumnock 132kV substation (Board B). At New Cumnock substation on the middle section of Board B install 132kV feeder bay. | 30/06/2027
|  | CS-03729 | ENERGYFARM UK OVERHILL LLP | Overhill WF 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/06/2027
|  | CS-03730 | ENERGYFARM UK OVERHILL LLP | Overhill WF 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 30/06/2027
|  | CS-03731 | ENERGYFARM UK OVERHILL LLP | Overhill WF 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/06/2027
OWF1 Offshore | PRO-001392 | CS-06352 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF1 275/66kV Offshore Substation | OWF1 - H1 Enabling Works | Extend Hunterston East 400kV GIS substation to add one new bay at each side of bus section X120 to provide the offshore developer with two interface points | 30/04/2028
OWF3 | PRO-001406 | CS-06274 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-025d | North East Reinforcement | 31/10/2031
|  | CS-06275 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2031
|  | CS-06276 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2031
|  | CS-06277 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2031
|  | CS-06278 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2031
|  | CS-06279 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2031
|  | CS-06280 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2031
|  | CS-06281 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2031
|  | CS-06282 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2031
|  | CS-06283 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2031
|  | CS-06284 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | OWF3 H1 Works | 400kV GIS Bay | 31/10/2031
|  | CS-06285 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | NGET-RI-30669-1 & SHET-RI-033 | Install a second 2GW HVDC converter station with associated equipment. HVDC cables to be routed between Aberdeenshire and North East England. | 31/10/2031
|  | CS-06286 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 31/10/2031
|  | CS-06273 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2031
OWPL Windfarm | PRO-000568 | CS-05993 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | OWPL H1 Enabling | Establishment of two new fully equipped 275kV metering circuit breaker bays and associated disconnectors at the new Spittal 2 275kV substation to connect the OWPL offshore wind farm development. The ownership boundary between the Onshore Transmission Licensee and the User (as OTSDUW User) will be the line side terminal of the 275kV disconnectors (L53, L63, L73, L83 and L93). | 31/10/2029
|  | CS-06613 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2029
|  | CS-06614 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 31/10/2029
|  | CS-06615 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2029
|  | CS-06616 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 31/10/2029
|  | CS-06617 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2029
|  | CS-06618 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2029
|  | CS-06619 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/10/2029
|  | CS-06620 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2029
|  | CS-06621 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | no Scheme | 0 | 31/10/2029
|  | CS-06608 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 31/10/2029
|  | CS-06609 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2029
|  | CS-06610 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2029
|  | CS-06611 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-025d | North East Reinforcement | 31/10/2029
|  | CS-06612 | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2029
Oykel Wind Farm | PRO-002711 | CS-09280 | STATKRAFT UK LTD | Oykel Wind Farm 132kV Substation | SHET-RI-230 | Loch Buidhe – Dalchork 132 kV Reinforcement- Construction of approximately 17 km 132 kV double circuit between Dalchork - Loch Buidhe substations with same rating OHLs as of existing double circuit i.e. 414 MVA post fault summer ratings. Scope also includes construction of two feeder bays each at Dalchork substation and Loch Buidhe substation | 31/10/2032
|  | CS-09282 | STATKRAFT UK LTD | Oykel Wind Farm 132kV Substation | OHL - Oykel WF | The 132kV OHL will be connected to Dalchork substation via a new fully equipped 132kV double busbar feeder bay, comprising 132kV line disconnector, 132kV feeder circuit breaker and 132kV double busbar selection disconnectors and associated protection equipment. | 31/10/2032
|  | CS-09278 | STATKRAFT UK LTD | Oykel Wind Farm 132kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2032
|  | CS-09277 | STATKRAFT UK LTD | Oykel Wind Farm 132kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/10/2032
|  | CS-09281 | STATKRAFT UK LTD | Oykel Wind Farm 132kV Substation | Disconnector - Oykel WF | Installation of a new 132kV line disconnector at User’s site at Oykel Wind Farm 132kV substation. The line disconnector will connect to the incoming 500m 132kV underground cable connected to the 23km 132kV overhead line trident wood pole line coming from Dalchork substation | 31/10/2032
|  | CS-09279 | STATKRAFT UK LTD | Oykel Wind Farm 132kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2032
Paul's Hill II Wind Farm | PRO-000890 | CS-05994 | PAUL'S HILL II LIMITED | Glenfarclas GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 05/04/2023
|  | CS-05995 | PAUL'S HILL II LIMITED | Glenfarclas GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 05/04/2023
|  | CS-05996 | PAUL'S HILL II LIMITED | Glenfarclas GSP | SHET-RI-015a | Knocknagael – Tomatin 275/132kV Reinforcement - Reinforce the existing 132kV transmission network between Beauly–Farr–Boat of Garten (Circuits BR1/RG1/BR2/RG2). Note that the existing 132kV OHL passes close to Knocknagael substation. Establish a new 275/132kV substation station including a 132kV double busbar arrangement near Tomatin and connected to a new 275kV double circuit OHL from the Knocknagael 275kV busbar via 275/132kV SGTs. | 05/04/2023
|  | CS-05997 | PAUL'S HILL II LIMITED | Glenfarclas GSP | SHET-RI-015b | Beauly-Farr-Boat of Garten 132kV OHL Reconfiguration - The existing section of 132kV OHL (BR1 & BR2) between Beauly and Farr will be terminated on the 132kV busbar at Knocknagael Substation. The OHL sections of the existing 132kV OHL will be dismantled between Knocknagael and Farr as part of the 132kV OHL reconfiguration. The existing section of double circuit 132kV OHL (RG1 & RG2) between Farr and Boat of Garten will be reconfigured as radial circuits between Tomatin and Boat of Garten. A normally open (N/O) point will be required at Keith on the circuit (FK) between Glenfarclas and Keith. This arrangement will leave Glenfarclas on a radial circuit fed from Boat of Garten under normal operating conditions. | 05/04/2023
Peattie Farm - Coupar Angus | PRO-002989 | CS-09227 | GREENTECH PROJECTS HOLDING UK LIMITED | Peattie Farm 33kV | Peattie Farm - Coupar Angus 2 Works | Installation of 2 x 132kV circuit breakers and 132kV disconnectors at the new Coupar Angus 2 132/33kV GSP substation compound, including 132kV cabling and works to connect the grid transformers. | 31/10/2029
|  | CS-09226 | GREENTECH PROJECTS HOLDING UK LIMITED | Peattie Farm 33kV | SHET-RI-184 | Coupar Angus 2 Tee – Establish a new 132kV tee point of the HCS circuit between Coupar Angus GSP and Tealing/Charleston Tee for the connection to a new Coupar Angus 2 132/33kV GSP substation | 31/10/2029
|  | CS-09225 | GREENTECH PROJECTS HOLDING UK LIMITED | Peattie Farm 33kV | SHET-RI-090 | Errochty – Clunie 132kV Reconductoring – Reconductor approximately 15.4km of the existing 132kV double circuit OHL between Errochty and Clunie substations. This double circuit is to be reconductored with UPAS conductor (1 x 300mm2) and will operate at 75 C to give a minimum summer pre-fault rating of 176MVA | 31/10/2029
Pembroke (spare bay) | PRO-000538 | CS-06914 | ENSO GREEN HOLDINGS LIMITED | Pembroke 132kV Substation | 100904-201818 | 1. Works to facilitate the connection of User’s plant into a spare bay at Pembroke 132kV substation 2. Extension of Pembroke OTS (Category 2 and Commercial intertripping schemes as explained in F3) | 30/10/2026
|  | CS-06915 | ENSO GREEN HOLDINGS LIMITED | Pembroke 132kV Substation | 100838-201680 | Replacement of feeder circuit breakers X105 and X305 of Pembroke –Swansea North Circuit 1 and 3 and modification of feeder protection. | 30/10/2026
|  | CS-06916 | ENSO GREEN HOLDINGS LIMITED | Pembroke 132kV Substation | 33746 | 1. Thermal uprate of Whitson leg of Tremorfa - Uskmouth – Whitson circuit. 2. Replacement of Cowley – Walham cables. 3. Thermal uprate of Imperial Park – Melksham and Cilfynydd – Whitson – Seabank circuits. 4. Thermal uprate of the Iron Acton – Melksham circuits 1 and 2. 5. Thermal uprate of Iron Acton – Whitson circuits 1 and 2. 6. Replace the Quad boosters 1 and 2 at Whitson for larger units. 7. Replacement of Whitson SGT5 for a larger rated unit. 8. Thermal uprate of Cardiff East – Uskmouth Whitson (Cardiff East leg). 9. Thermal uprate of Cardiff East – Uskmouth – Whitson (Whitson leg). 10. Thermal uprate of Aberthaw – Tremorfa circuit. 11. Thermal uprate of Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit. 12. Thermal uprate of Tremorfa - Uskmouth – Whitson circuit 13. Thermal uprate of Cardiff East – Uskmouth – Whitson (Uskmouth leg). 14. Thermal uprate of Uskmouth – Whitson 2 circuit. | 30/10/2026
Pembroke BESS | PRO-000337 | CS-05945 | RWE GENERATION UK PLC | Pembroke 400kV Substation | 33793 | • Extension of Pembroke 400kV substation to accommodate one new GIS generator bay, including busbar protection and SCS update • Installation of a generator to system intertripping scheme (thermal and stability) • Replacement of feeder circuit breakers of Pembroke – Swansea North #1 and #3 and modification of feeder protection • Thermal uprate of the Whitson leg of Tremorfa - Uskmouth – Whitson circuit • Replacement of the Cowley – Walham cables • Thermal uprate of Imperial Park – Melksham and Cilfynydd – Whitson – Seabank circuits • Thermal uprate of the Iron Acton – Melksham circuits 1 and 2 • Thermal uprate of Iron Acton – Whitson circuits 1 and 2 • Remove the Quad boosters 1 and 2 at Whitson • Replacement of Whitson SGT5 for a larger rated unit • Thermal uprate of the Cardiff East – Uskmouth – Whitson (Cardiff East leg) • Thermal uprate of the Cardiff East – Uskmouth – Whitson (Whitson leg) • Thermal uprate of the Aberthaw – Tremorfa circuit. • Thermal uprate of the Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit | 01/10/2026
Pembroke Green Hydrogen | PRO-003052 | CS-08540 | RWE GENERATION UK PLC | Pembroke 132kV Substation | 102469-205045 | Accommodation of the new user bay for RWE | 01/09/2028
|  | CS-08539 | RWE GENERATION UK PLC | Pembroke 132kV Substation | 102470-205046 | Provision of a Fourth SGT at Pembroke including:  Extension of Pembroke substation  Provision, Installation, and Commission of Fourth SGT at Pembroke including the SGT transformer, 132kV and 400kV bay equipment | 01/09/2028
Pembroke Hydrogen | PRO-002448 | CS-07414 | RWE GENERATION UK PLC | Pembroke 132kV Substation | 101895-203882 | 0 | 16/10/2026
|  | CS-07415 | RWE GENERATION UK PLC | Pembroke 132kV Substation | 101903-203897 | 0 | 16/10/2026
Pencloe Windfarm | PRO-000323 | CS-06000 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-116B | Construction of Black Hill 132/33kV Substation including two 132kV circuit breakers (double busbar), two 132/33kV 90MVA transformers and 33kV B switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 01/07/2024
|  | CS-06001 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 01/07/2024
|  | CS-06002 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 01/07/2024
|  | CS-05998 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 01/07/2024
|  | CS-05999 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill Substation, heading east, to 132kV Black Hill Substation. Black Hill Substation will include three new 132kV circuit breaker (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 01/07/2024
|  | CS-06677 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 01/07/2024
|  | CS-06678 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 01/07/2024
|  | CS-08225 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 01/07/2024
|  | CS-08226 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 01/07/2024
|  | CS-08224 | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | SPT-RI-136 | Reconductor the 275kV single circuit overhead line (YY route) between Coylton 275kV substation and Mark Hill 275kV substation. | 01/07/2024
Penketh Hall Farm | PRO-001932 | CS-07469 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101743-203463 | At Fiddlers Ferry 275kV Substation: 1. Provision of an ex-SSE owned generator bay for the User to connect into – this is subject to SSE agreeing an asset transfer of the bay to The Relevant Transmission Licensee. Specific bay to be confirmed during the development phase of the project. 2. Modifications to protection and control systems / database changes as required. | 01/09/2027
|  | CS-07470 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101474-202196 | Uprate the Cellarhead – Drakelow 400kV circuits | 01/09/2027
|  | CS-07471 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 01/09/2027
|  | CS-07472 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connah’s Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor. | 01/09/2027
|  | CS-07473 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101279-202529 | Reconductor the 2 x Rubus and 2 x Sorbus sections of the Connahs Quay legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor triggered from R4 connection | 01/09/2027
|  | CS-07474 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 01/09/2027
|  | CS-07475 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101285-202535 | Establish a system run back scheme for the Western Link to monitor the circuits between Connahs Quay and Connahs Quay – Legacy – Trawsfynydd 1 and 2 400kV circuits and the Cellarhead – Macclesfield and Cellarhead – Drakelow 400kV circuits | 01/09/2027
|  | CS-07476 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x760mm2 conductor or equivalent and uprating of the cable section of the circuit | 01/09/2027
|  | CS-07477 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101468-202908 | Reconductor the Daines – Macclesfield 400kV with 2x780mm2 conductor | 01/09/2027
|  | CS-07478 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101697-203381 | Reconductor the Cellarhead – Macclesfield 400kVcircuit with 2x780mm2 conductor | 01/09/2027
|  | CS-07479 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 100425-200971 | Reconductor the Feckenham – Ironbridge 400kV circuit with 2x620mm2 conductor | 01/09/2027
|  | CS-07480 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 01/09/2027
|  | CS-07481 | Net Zero One Limited | Fiddlers Ferry 275kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 01/09/2027
Pentland Floating Offshore Wind Farm | PRO-001472 | CS-06496 | HIGHLAND WIND LIMITED | OWF-100 Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/08/2025
|  | CS-06497 | HIGHLAND WIND LIMITED | OWF-100 Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/08/2025
Pentland Road | PRO-000361 | CS-06003 | PENTLAND ROAD WINDFARM LIMITED | Stornoway GSP | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 31/03/2027
|  | CS-06004 | PENTLAND ROAD WINDFARM LIMITED | Stornoway GSP | SHET-RI-042 | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHET-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly. | 31/03/2027
Penwortham BESS | PRO-001804 | CS-07028 | Penwortham (BES) Ltd | Penwortham 400kV Substation | 101607-203231 | Extension Works of the existing fence to provide a 13kV Connection Install Earthing Transformer on 13kV SGT9 Tertiary connection. Install 13kV cable from 13kV SGT9 Tertiary connection to 13 kV Line Disconnector. Install 13 kV Line Disconnector. | 31/10/2024
| PRO-002037 | CS-08904 | CSE28 LIMITED | Penwortham 400kV Substation | 101946-203996 | 1. Install Earthing Transformer on 13kV Tertiary Connection, 2. Install 13kV Cable from Tertiary connection to 13kV Disconnector, 3. Install 13kV Disconnector at the 13kV side connecting the Tertiary connection to Connection Assets for User’s connection, 4. Buy and make good additional land for the tertiary bay. | 01/06/2027
Penwortham Green Energy Centre | PRO-001694 | CS-04645 | PENWORTHAM GREEN ENERGY LIMITED | Penwortham 400kV Substation | 101569-203135 | At Penwortham 400kV Substation:At Penwortham 400kV Substation: . 1) Western extension of the site, subject to provision of land and temporary land by the User. 2) Extend the Main and Reserve Busbar 2 to make provision for connection of generator bay (User Works). 3) Local Works to connect User into Heysham Intertripping Scheme. | 31/10/2026
Peterhead Battery | PRO-001999 | CS-07254 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-07255 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-07256 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-07257 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-07258 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | Peterhead 400 kV Substation | Install one new 400kV feeder bay complete with 2 x 400kV busbar selection switches,1 x 400kV circuit breaker, 1 x 400kV line disconnector and associated protection equipment. The construction of approximately 3km of 400kV Circuit between Peterhead 400kV Substation and Peterhead Battery substation. At Peterhead Battery Substation the sole use enabling works will include the construction of a 400kV Line disconnector including all associated civil and protection work. | 31/10/2033
|  | CS-07259 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-07260 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-07261 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-07262 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-07263 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-07264 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-07265 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-07266 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-07267 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-07270 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-07271 | PETERHEAD FLEXPOWER LTD | Peterhead GSP | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
Peterhead Carbon Capture | PRO-004529 | CS-09624 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-09633 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-09622 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-09626 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-09634 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-09635 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-09630 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-09637 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-180 | Second Peterhead 400kV Busbar - Construct a second 400kV Substation at Peterhead | 31/10/2033
|  | CS-09629 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2033
|  | CS-09632 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-09636 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-09623 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-09627 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-09631 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-09625 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-09628 | SSE THERMAL GENERATION (SCOTLAND) LIMITED | PETERHEAD 275KV SUBSTATION | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
Peterhead PV and BESS Station | PRO-002775 | CS-09325 | ETP UK 2 LTD | New Deer 2 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
Petroc Extension Offshore Wind Farm | PRO-002404 | CS-07766 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault Summer rating of 1650MVA. | 06/12/2036
|  | CS-07768 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-07769 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to achieve a Summer post fault rating of 2450MVA. | 06/12/2036
|  | CS-07764 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-07765 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
|  | CS-07762 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 102155-204359 | 0 | 06/12/2036
|  | CS-07767 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
|  | CS-07763 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Hinkley Point - Exeter 400kV circuits to achieve a 3100MVA post fault winter rating. Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating | 06/12/2036
Petroc Offshore Wind Farm | PRO-001661 | CS-07430 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101460-202897 | Local substation works to enable the generation connection of 300MW Connection Entry Capacity (CEC) for Dewnens Floating Offshore Wind Farm at Alverdiscott substation. Extension of the busbars by 1 bay to enable connection of the generator’s bay. | 31/03/2029
|  | CS-07431 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 31/03/2029
|  | CS-07432 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 31/03/2029
Phoenix 1B Offshore Wind Farm | PRO-001519 | CS-06728 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | Phoenix 1B Item 1 | Installation of 400kV plant and apparatus at Cousland 400kV Substation which will form the connections to the three Phoenix 1B Transmission Interface Points, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers. | 31/10/2033
|  | CS-06729 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | Phoenix 1B Item 2 | Provision of communications, alarms and indications, as described in Appendix F of the Bilateral Connection Agreement. | 31/10/2033
|  | CS-06730 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 31/10/2033
|  | CS-06731 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 31/10/2033
|  | CS-06732 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | SPT-RI-1796 | Cousland 400kV GIS Substation - A new 400kV double busbar substation, utilising Gas Insulated Switchgear (GIS), will be established south of Cockenzie in the Cousland area in the vicinity of the Torness/Fallago to Smeaton/Wishaw 400kV double circuit (ZS route) and Cockenzie to Eccles 400kV double circuit (ZA Route) crossing. Both the ZA and the ZS routes will be turned into the new substation. | 31/10/2033
|  | CS-06733 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 31/10/2033
|  | CS-06734 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 31/10/2033
|  | CS-06735 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | SPT-RI-267 | Eccles 400kV Shunt Compensation - In order maintain to post-fault voltages within statutory limits, the installation of voltage control in the east of the network is required. As such, dynamic shunt compensation will be installed at Eccles 400kV substation with associated switchgear. | 31/10/2033
|  | CS-06736 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | SPT-RI-304 | East Coast B6 onshore reinforcement - Installation of a new 400kV double circuit overhead line, of approximately 185km, between the Torness area (Branxton 400kV substation) in South East Scotland, and Lackenby in North East England. | 31/10/2033
|  | CS-06737 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | SPT-RI-1795 | This project will construct a new 400kV double circuit over the boundary from the South East of Scotland and the North West of England | 31/10/2033
|  | CS-06738 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | SPT-RI-1873 | Second East Coast HVDC Link - Installation of a 2 GW HVDC subsea link between the East Lothian area in South East Scotland, and the South Humber area in North East England | 31/10/2033
|  | CS-06739 | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation | SPT-RI-1791 | Cockenzie to Eccles (ZA route) Uprating. - The project will uprate the 400kV double circuit between Cockenzie 400kV substation and Eccles 400kV substation from twin Totara to triple Totara operating at 90℃. | 31/10/2033
Pines Burn Wind Farm | PRO-000897 | CS-06194 | PINES BURN WIND FARM LLP | Hawick GSP | SPT-RI-151b | In order to provide GBSQSS compliant connections for additional generation requiring to export from Hawick/Galashiels to Eccles, it is proposed to construct a new 132kV double circuit tower line between Galashiels and Eccles, and remove the existing U and AT Routes. | 02/08/2023
Pitkerro Road | PRO-002457 | CS-09599 | Vital Energi Solutions Limited | Milton of Craigie GSP | SHET-RI-183 | New Dundee 132kV Substation – Construction of a new 132kV double busbar substation in Dundee, to replace Dudhope GSP. This busbar will be fed by turning in the current Dudhope/Milton of Craigie 132kV circuits. (SHET-RI-183) | 31/10/2033
|  | CS-09598 | Vital Energi Solutions Limited | Milton of Craigie GSP | Pitkerro Road H1 Works | 1. Installation of 2x 120MVA transformers within the existing substation with associated 33kV 2x circuit breakers and 2x disconnectors. 2. Installation of 132kV 2x circuit breakers and 2x disconnectors on the HV side of the new Grid Transformers at Milton of Craigie GSP which have been installed as part of the Transmission Connection Asset Works. | 31/10/2033
Pitkerro Road (DNO) | PRO-003028 | CS-09596 | Scottish Hydro Electric Power Distribution Plc | Milton of Craigie GSP | Pitkerro Road H1 | Installation of 132kV 2x circuit breakers and 2x disconnectors on the HV side of the new Grid Transformers at Milton of Craigie GSP which have been installed as part of the Transmission Connection Asset Works. | 31/10/2033
|  | CS-09597 | Scottish Hydro Electric Power Distribution Plc | Milton of Craigie GSP | SHET-RI-183 | New Dundee 132kV Substation – Construction of a new 132kV double busbar substation in Dundee, to replace Dudhope GSP. This busbar will be fed by turning in the current Dudhope/Milton of Craigie 132kV circuits. (SHET-RI-183) | 31/10/2033
Pivot Power Harker Hybrid | PRO-001065 | CS-05135 | PIVOTED POWER LLP | Harker 400kV Substation | NGET-R1-100247-200628 (Infra) | 1.Install earthing transformer on 13kV Tertiary connection 2. Install 72.5kV, 40kA Disconnecting Circuit Breaker (DCB) at the 13kV side connecting Tertiary to Connection Assets for Users connection. | 31/10/2029
Plas Power Estate North Tertiary | PRO-001050 | CS-06917 | LIGHTSOURCE SPV 192 LIMITED | Legacy 400kV Substation | 100861-201721 | 1. Install a tertiary cable box or bushings on the SGT 3. 2. Install 13kV Cable from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 01/08/2026
PM AB Energy Storage | PRO-002140 | CS-07742 | P&M Energy Ltd | Abernethy GSP | PM AB Energy Storage Item | An intertrip for the loss of one of the Grid Transformers at Abernethy 132/33kV GSP. These signals will be provided to the host Distribution Network Operator via a separate relay panel within the 33kV Switchroom from the signals described below. Provision of status signals are required for the following: Status signals from the 33kV circuit breakers and disconnectors at Abernethy GSP Status signals from 132kV circuit breakers and disconnectors at Abernethy GSP Modification to the existing LV Directional Overcurrent (DOC) protection settings at Abernethy 132/33kV Substation. | 31/10/2026
|  | CS-07743 | P&M Energy Ltd | Abernethy GSP | SHET-RI-121 | Charleston - Abernethy 132kv reconductoring; approx 25km of 132 kv ohl between abernrethy substation and Charleston. | 31/10/2026
Pond Flexible Energy Park | PRO-003201 | CS-09408 | Pond Flexible Energy Park Limited | Bathgate 132/33kV Substation | SPT-RI-3002 | Harburn 400kV Substation- Establish a new 400kV double busbar substation, indicatively named Harburn substation. The location of the SPT’s new 400kV substation is currently under review, with an initial view that it will tie into the existing XJ Route (STHA-TORN / WISH-SMEA/FALL) as well as facilitate a turn in of the XM Route (Kincardine-Currie circuit) following uprating as part of the HND process | 30/06/2031
|  | CS-09480 | Pond Flexible Energy Park Limited | Bathgate 132/33kV Substation | SPT-RI-3168 | Harburn 132kV Substation | 30/06/2031
Pond Hill Farm 1 | PRO-001637 | CS-06918 | PD688IRO LTD | Minety 400kV Substation | 101488-202945 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new busbar 33kV substation at Minety to be connected via new 400/33kV SGT8A. 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 30/04/2025
|  | CS-06919 | PD688IRO LTD | Minety 400kV Substation | 020903-020903 | Uprating of Cowley-Minety 400kV circuit and Cowley-Minety 400kV cables to achieve 1300 MVA pre-fault Summer rating. | 30/04/2025
|  | CS-06920 | PD688IRO LTD | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 1990MVA | 30/04/2025
Pond Hill Farm 2 BESS | PRO-001635 | CS-06921 | PD688IRO LTD | Minety 400kV Substation | 101488-202945 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new busbar 33kV substation at Minety to be connected via new 400/33kV SGT8A. 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 31/05/2025
|  | CS-06922 | PD688IRO LTD | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 1990MVA | 31/05/2025
|  | CS-06923 | PD688IRO LTD | Minety 400kV Substation | 020903-020903 | Uprating of Cowley-Minety 400kV circuit and Cowley-Minety 400kV cables to achieve 1300 MVA pre-fault Summer rating. | 31/05/2025
Pont Abraham iDNO | PRO-001562 | CS-04746 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Pont Abraham GSP | 101256-202607 | Overhead line works to connect a new six bay substation to the transmission network via single circuit turn in of the Pembroke – Walham (future Pembroke – Swansea North) 400kV circuit. | 31/10/2028
|  | CS-04747 | GREEN GENERATION ENERGY NETWORKS CYMRU LIMITED | Pont Abraham GSP | 101256-202497 | Installation of a new six bay 400kV substation consisting of two feeder bays, bus coupler and three Supergrid Transformer (SGT) bays. | 31/10/2028
Port of Mostyn | PRO-000421 | CS-06924 | MOSTYN SEAPOWER LIMITED | Connah's Quay 400kV Substation | 100534-201153 | Extend the existing GIS busbars at Connah’s Quay 400kV Substation to provide space for a single generator bay. | 01/04/2027
Priestgill Wind Farm | PRO-000448 | CS-06005 | PRIESTGILL WIND FARM LIMITED | Elvanfoot 275/132/33kV | SPT-RI-226 | Installation of a new 275/132kV 360MVA transformer and a new 132kV busbar at Elvanfoot substation, to allow new generators to connect. | 06/12/2024
|  | CS-07367 | PRIESTGILL WIND FARM LIMITED | Elvanfoot 275/132/33kV | SPT-RI-1876 | 2. Elvanfoot 132/33kV Grid Transformer - Install a 132/33kV 60MVA transformer at Elvanfoot to accommodate the increased generation connecting at 33kV into the site. (SPT-RI-1876) | 06/12/2024
Progress Power Station | PRO-000274 | CS-06006 | PROGRESS POWER LIMITED | Yaxley 400kV Substation | 020340-020340 | Reconductor the re-configured Bramford – Norwich Main (4YM route) with 3 x 700 mm2 AAAC conductor operating at 75oC. | 28/06/2024
|  | CS-06007 | PROGRESS POWER LIMITED | Yaxley 400kV Substation | 032473-032486 | Installation of a new GIS double busbar 400kV substation at Yaxley with associated two feeder bays, coupler bay and provide double tee connection of the new substation to the Bramford – Norwich Main double OHL circuit. New terminal tower on the Bramford – Norwich Main 1 & 2 circuits and removal of the existing suspension tower(s). Installation of cable circuit to provide a duck tee connection underneath OHL. Install an additional circuit breaker on the LV side of SGT3 at Norwich Main to maintain compliance with the SQSS circuit complexity guidance. Extension of the existing East Anglia Operational Tripping Scheme to include this connection. | 28/06/2024
Protos Power Station | PRO-002823 | CS-09367 | KEADBY GENERATION LIMITED | Elton 400kV Substation | 102739-205531 | 1. Establish a new 400kV double busbar substation on land near Elton, beside Capenhurst - Frodsham 400kV double circuit. (Provisionally referred to as Elton 400kV). Substation to comprise two feeder bays, a bus coupler bay and a skeletal SGT bay. 2. Connect the Elton 400kV substation via a turn in of the Capenhurst - Frodsham double circuit to create a new Capenhurst – Elton 400kV circuit and a new Elton – Frodsham 400kV circuit. | 01/11/2037
Quantans Hill Wind Farm | PRO-001247 | CS-08213 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-2094 | Quantans Hill to Holmhill 132kV Circuit – At the proposed Quantans Hill wind farm site establish a 132kV substation and establish a 132kV busbar to which a 132kV line isolator is connected. Install around 6km of wood pole overhead line with HTLS conductor to connect Quantans Hill substation to Holmhill substation. At Holmhill substation install a 132kV circuit breaker to connect the OHL. | 30/04/2027
|  | CS-08212 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/04/2027
|  | CS-06213 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | Quantans Hill H1 Works | 132kV busbar with three 132kV disconnectors at Quantans Hill 132/33kV Substation 6km of 132kV wood pole overhead line short cable dip to connect the 132kV circuit to Holmhill Holmhill substation, install one 132kV circuit breaker to the Quantans Hill 132kV circuit Kilmarnock South 400kV and 275kV uprating Kendoon to Glenlee 132kV Reinforcement Glenlee to Tongland 132kV Modernisation New Cumnock substation a third 275/132 240MVA transformer GEMS | 30/04/2027
|  | CS-06214 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 30/04/2027
|  | CS-06215 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/04/2027
|  | CS-06216 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-1507 | Holmhill 132kV Substation | 30/04/2027
|  | CS-06217 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 30/04/2027
|  | CS-06218 | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 30/04/2027
Race Bank Extension | PRO-000468 | CS-06008 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100592-201219 | At Mablethorpe 400kV Substation: Extend busbar by one bay to facilitate an OFTO bay | 30/04/2030
|  | CS-06382 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100944-201880 | Build a new 400kV Killingholme South Substation with: 8 feeder bays, 1 section bay and 2 couplers. | 30/04/2030
|  | CS-06383 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100944-201881 | Build a new 400 kV double circuit between Killingholme South and 100944-201881 Mablethorpe substations Build a new 400kV Mablethorpe | 30/04/2030
|  | CS-06384 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100944-201882 | Build a new 400kV Mablethorpe Substation with 6 Bays - 4 Feeder bays, 1 Coupler Bay, 2 Section Breakers Main & Reserve | 30/04/2030
|  | CS-06385 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100946-201889 | At Killingholme 400kV GIS substation: Replace circuit breakers X430, X460, X420, X530, X130, X120, X960, X920, X930, X140, X305. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 30/04/2030
|  | CS-06386 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 30/04/2030
|  | CS-06387 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 30/04/2030
|  | CS-06388 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 021847-021847 | Construct a new 400 kV double circuit between the Bamford 400 kV substation and the Twinstead Tee point strung with 3x700mm2 AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford-Pelham double circuit and Bramford-Braintree-Bulls Lodge and Bramford-Braintree-Rayleigh Main 400 kV double circuit (BTNO Works). | 30/04/2030
|  | CS-06389 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100637-201311 | Uprate the existing Rayleigh Main to Tibury 400kV circuit to provide a post fault winter rating of 2210MVA | 30/04/2030
|  | CS-06390 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main & Reserve | 30/04/2030
|  | CS-06391 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 031867-200324 | Build a new HVDC bi-pole link with capacity of 2 GW between Suffolk and Kent. | 30/04/2030
|  | CS-06392 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 30/04/2030
|  | CS-06393 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100944-201883 | Build a new 400 kV double circuit between Mablethorpe and Weston Marsh Substations | 30/04/2030
|  | CS-06394 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 30/04/2030
|  | CS-06395 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 30/04/2030
|  | CS-06396 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 30/04/2030
|  | CS-06397 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm2 AAAC sections of the circuits with 2×591mm2 ACCR conductor and the 2x700mm2 AAAC sections with 3x700mm2 AAAC conductor | 30/04/2030
|  | CS-06398 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100941-201873 | At Cottam 400kV Substation: Install a 2750MVA QB on the COTT-WBUR circuit | 30/04/2030
|  | CS-06399 | ORSTED POWER (UK) LIMITED | Racebank Extension 220/66kV Offshore | 100637-201311 | Uprate the existing Rayleigh Main to Tibury 400kV circuit to provide a post fault winter rating of 2210MVA | 30/04/2030
Rampion Extension Offshore Wind Farm | PRO-000467 | CS-06372 | RAMPION EXTENSION DEVELOPMENT LIMITED | Rampion Offshore Wind Farm | 100732-201514 | AIS Extension of Reserve and Main busbar 2 at Bolney 400kV Substation for the provision of one User Bay. | 01/08/2026
|  | CS-06374 | RAMPION EXTENSION DEVELOPMENT LIMITED | Rampion Offshore Wind Farm | 33773 | Thermal upgrade of the Bramley to Fleet 1 & 2 circuits | 01/08/2026
|  | CS-06375 | RAMPION EXTENSION DEVELOPMENT LIMITED | Rampion Offshore Wind Farm | 100732-201610 | Extension of the Sellindge Operational Tripping Scheme (OTS) to include Rampion Extension Wind Farm. | 01/08/2026
|  | CS-06376 | RAMPION EXTENSION DEVELOPMENT LIMITED | Rampion Offshore Wind Farm | 100298 | Re-Conductor Fleet – Lovedean 1 & 2 circuit | 01/08/2026
|  | CS-06377 | RAMPION EXTENSION DEVELOPMENT LIMITED | Rampion Offshore Wind Farm | 33411 | Thermal reinforcement to the South Coast | 01/08/2026
Ranby | PRO-002557 | CS-08512 | SSE DE SOLAR HOLDCO LIMITED | Jubilee Farm 275kV Substation | 102427-204957 | 1. Build a new double busbar 275kV substation with 2 feeder bays and 1 coupler bay 2. Establish a single turn in connection between the new 275kV substation and High Marnham – Thurcroft – West Melton (High Marnham Leg) line (B48X) 3. Extension of 275kV busbars to connect user bay | 30/08/2034
Ratcliffe EMERGE | PRO-001462 | CS-06748 | UNIPER UK LIMITED | Ratcliffe GSP | 101178-202385 | Busbar protection and database/labelling changes to enable the connection of the User’s power station into the existing spare bay at Ratcliffe-On-Soar 132kV substation. | 01/07/2024
Ratcliffe-on-Soar II | PRO-002158 | CS-08251 | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation | 100478-201049 | Reconductor the Drakelow-Willington East 400kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA | 31/10/2030
|  | CS-08246 | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 31/10/2030
|  | CS-08248 | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 31/10/2030
|  | CS-08252 | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation | 101593-203208 | Uprate the Cottam- Staythorpe circuit to provide a post-fault summer rating of 2800 MVA | 31/10/2030
|  | CS-08243 | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation | 102151-204353 | The User to connect at the spare bay available at Ratcliffe on Soar 400kV substation. | 31/10/2030
|  | CS-08247 | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation | 101889-203868 | East Claydon legs of ECLA4-ENDE4-PAFB4 cctReconductor the East Claydon legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490MVA | 31/10/2030
|  | CS-08245 | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation | 101884-203860 | Reconductor the Enderby legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490MVA | 31/10/2030
|  | CS-08244 | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation | 101879-203856 | Uprate the Ratcliffe 400kV to Willington East 400kV circuit 1 (RATS4- WILE4 1) to summer pre-fault rating of 2490MVA. | 31/10/2030
|  | CS-08249 | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post fault winter rating of 3420MVA | 31/10/2030
|  | CS-08250 | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 31/10/2030
Rawhills Battery Energy Storage Facility | PRO-001503 | CS-06745 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | Rawhills BESS H1 Works | 1. Installation of a new 400kV double busbar bay at Coalburn North 400kV substation including a 400kV circuit breaker and associated equipment. 2. Installation of a new 400kV cable circuit (approx. 4.5km) between Coalburn North 400kV substation and the User’s site. 3. Installation of a 400kV line disconnector at the User’s site. 4. . Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 16/04/2027
|  | CS-07651 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 16/04/2027
|  | CS-07652 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 16/04/2027
|  | CS-07660 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-2378 | Teviot 400/132kV substation - Construct a new 400/132kV substation to facilitate the new 400kV OHL connections into the site as well as install two new 400/132kV 360MVA transformers and a 132kV double busbar substation for the Teviot windfarm connection. It is proposed to install Gas Insulated Switchgear (GIS) rated at 5000A. (SPT-RI-2378) | 16/04/2027
|  | CS-07661 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-2417 | Teviot to Gala North Reinforcements - A new 400kV double circuit OHL using L13 towers and triple Araucaria conductor from Teviot 400kV substation to Gala North 400kV substation which is approximately 57km. (SPT-RI-2417) | 16/04/2027
|  | CS-07653 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 16/04/2027
|  | CS-07658 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-1796 | Cousland 400kV GIS Substation - A new 400kV double busbar substation, utilising Gas Insulated Switchgear (GIS), will be established south of Cockenzie in the Cousland area in the vicinity of the Torness/Fallago to Smeaton/Wishaw 400kV double circuit (ZS route) and Cockenzie to Eccles 400kV double circuit (ZA Route) crossing. Both the ZA and the ZS routes will be turned into the new substation. | 16/04/2027
|  | CS-07654 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 16/04/2027
|  | CS-07655 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-267 | Eccles 400kV Shunt Compensation - In order maintain to post-fault voltages within statutory limits, the installation of voltage control in the east of the network is required. As such, dynamic shunt compensation will be installed at Eccles 400kV substation with associated switchgear. | 16/04/2027
|  | CS-07656 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-1738 | 1. Teviot to Harker Reinforcements - It is proposed to construct at a location in the vicinity of Teviot wind farm site a double busbar 132kV AIS substation to which two 400/132kV 360MVA interbus supergrid transformers will be connected. A double busbar AIS 400kV substation will also be established at the wind farm site to which the interbusing transformers will be connected and two further bays will be provided to connect a double circuit OHL. From the 400kV substation a double circuit OHL of around 43km built on L8 towers and installed with twin Totara conductors will be constructed to Harker 400kV substation. SPT will build the OHL to SPT/NGET boundary and NGET will complete the construction of the scheme from the boundary to Harker. (SPT-RI-1738) | 16/04/2027
|  | CS-07657 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-1791 | Cockenzie to Eccles (ZA route) Uprating. - The project will uprate the 400kV double circuit between Cockenzie 400kV substation and Eccles 400kV substation from twin Totara to triple Totara operating at 90℃. | 16/04/2027
|  | CS-07659 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 16/04/2027
|  | CS-07662 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-1873 | Second East Coast HVDC Link - Installation of a 2 GW HVDC subsea link between the East Lothian area in South East Scotland, and the South Humber area in North East England | 16/04/2027
|  | CS-08290 | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation | SPT-RI-2058 | Coalburn North 400kV Substation - construction of a new 400kV substation, indicatively called Coalburn North, to connect into the Strathaven-Elvanfoot 400kV circuit. Construction of a new 400kV double busbar substation with a bus coupler circuit breaker, two feeder bays to connect onto the Strathaven-Elvanfoot 400kV circuit. | 16/04/2027
Rayleigh 1 Tertiary | PRO-000460 | CS-06929 | RAYLEIGH GREEN LIMITED | Rayleigh Main 400kV Substation | 100914 - 201831 | 1. Install earthing transformer 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install a tertiary cable box or bushings on SGT 6. 4. Install a 13kV Disconnector at the 13kV side connecting the tertiary to the Connection Assets for Users connection. | 31/10/2023
Rayleigh 2 Tertiary | PRO-000466 | CS-06930 | ENSO GREEN HOLDINGS LIMITED | Rayleigh Main 400kV Substation | 100914 - 201845 | 1. Install earthing transformer 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install a tertiary cable box or bushings on SGT 3. 4. Install a 13kV Disconnector at the 13kV side connecting the tertiary to the Connection Assets for Users connection. | 31/10/2025
REBD / MURPHY IDNO PENRHOS REDEVELOPMENT | PRO-002730 | CS-09264 | MUA ELECTRICITY LIMITED | Penrhos GSP | 101558-203101 | Install a second cable between the OHL from Penrhos and the Wylfa 132kV substation. | 30/11/2026
|  | CS-09262 | MUA ELECTRICITY LIMITED | Penrhos GSP | 101458-202894 | Infrastructure works for the Orthios Distribution connection at Penrhos 132kV substation. | 30/11/2026
|  | CS-09263 | MUA ELECTRICITY LIMITED | Penrhos GSP | 101557-203099 | Rebuild Penrhos 132kV substation as a double busbar substation to allow for 2 feeder bays and 2 demand bays. | 30/11/2026
Recell at Penrhos (BEGA) | PRO-000330 | CS-05171 | Recell Energy Bloom Developments Limited | Penrhos GSP | 101459-202896 | Infrastructure works for the Orthios Power connection at Penrhos 132kV substation. | 30/10/2025
|  | CS-05172 | Recell Energy Bloom Developments Limited | Penrhos GSP | 101557-203099 | Rebuild Penrhos 132kV substation as a double busbar substation to allow for 2 feeder bays and 2 demand bays. | 30/10/2025
|  | CS-05173 | Recell Energy Bloom Developments Limited | Penrhos GSP | 101458-202894 | Infrastructure works for the Orthios Distribution connection at Penrhos 132kV substation. | 30/10/2025
|  | CS-05174 | Recell Energy Bloom Developments Limited | Penrhos GSP | 101558-203101 | Install a second cable between the OHL from Penrhos and the Wylfa 132kV substation. | 30/10/2025
|  | CS-05175 | Recell Energy Bloom Developments Limited | Penrhos GSP | 101458-203111 | Connection works for Orthios Distribution at Penrhos 132kV substation – Building of 2 generator bays as requested by the customer | 30/10/2025
Red John PSH | PRO-000570 | CS-06338 | ILI (HIGHLANDS PSH) LIMITED | Red John 275kV Switching Station | SHET-RI-132 | Beauly - Blackhillock High Temperature Reconductoring | 31/07/2028
|  | CS-06339 | ILI (HIGHLANDS PSH) LIMITED | Red John 275kV Switching Station | Red John - 275kV AIS bays | Extension of the existing Knocknagael 275kV AIS double busbar to create two new 275kV AIS bays to connect the new circuits from Red John 275kV Switching Station. The removal and subsequent replacement of the existing 275kV bus couplers is required to facilitate the connection. | 31/07/2028
|  | CS-06340 | ILI (HIGHLANDS PSH) LIMITED | Red John 275kV Switching Station | Red John - 275kV underground cable double circuit | Red John 275kV Switching Station will be connected to the existing Knocknagael 275kV by approximately 9km of double circuit 275kV underground cable. The User has requested an underground cable option instead of an overhead line connection. The additional cost of the underground cable compared to the original overhead line solution would be payable by the User as a One-Off Works cost. | 31/07/2028
|  | CS-06341 | ILI (HIGHLANDS PSH) LIMITED | Red John 275kV Switching Station | Red John - New 4-bay 275kV GIS double busbar Switching Station | At Red John 275kV Switching Station, a new 4-bay 275kV GIS double busbar Switching Station complete with a bus-section and two bus couplers will be constructed. | 31/07/2028
Red Moss Farm | PRO-002613 | CS-09294 | Greenswitch Capital Limited | Red Moss GSP | Red Moss - Redshaw Transformer | Installation of a 400/132kV 360MVA transformer at Redshaw 400/132 substation | 30/10/2030
|  | CS-09292 | Greenswitch Capital Limited | Red Moss GSP | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 30/10/2030
|  | CS-09291 | Greenswitch Capital Limited | Red Moss GSP | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 30/10/2030
|  | CS-09297 | Greenswitch Capital Limited | Red Moss GSP | Red Moss - Line Disconnector | Installation of a 132kV line disconnector at the Red Moss Farm 132kV substation | 30/10/2030
|  | CS-09293 | Greenswitch Capital Limited | Red Moss GSP | Red Moss - Redshaw GIS Bay | Installation of a 400kV GIS bay at Redshaw 400kV substation | 30/10/2030
|  | CS-09295 | Greenswitch Capital Limited | Red Moss GSP | Red Moss - AIS Bay at Redshaw | Installation of a 132kV AIS bay at Redshaw 400/132kV substation | 30/10/2030
|  | CS-09296 | Greenswitch Capital Limited | Red Moss GSP | Red Moss - 132kV Circuit | Installation of a 132kV circuit between Redshaw 400/132kV substation and Red Moss Farm 132kV substation. As part of the desktop exercise this 132kV circuit shall use two cables per phase to meet the capacity of the connection. The indicative cable route length is 4.7km | 30/10/2030
Redshaw Energy Park | PRO-003982 | CS-09742 | BAYWA R.E. UK LIMITED | Linmill 132/33kV Substation | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 30/10/2031
|  | CS-09743 | BAYWA R.E. UK LIMITED | Linmill 132/33kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 30/10/2031
|  | CS-09741 | BAYWA R.E. UK LIMITED | Linmill 132/33kV Substation | SPT-RI-231 | 0 | 30/10/2031
Redshaw GSP | PRO-003212 | CS-09438 | SP Distribution plc |  | SPT-RI-3060 | Redshaw 132kV “B” Board - Establish a new 132kV double busbar substation, indicatively named Redshaw 132kV “B” board at the new Redshaw 400/132kV substation. The location of the SPT’s new 400kV substation (which this 132kV double busbar site will connect into) will be connected in the existing ZV Route corridor (STHA-ELVA / COAL-ELVA) as well as facilitate the new double circuit from Glenmuckloch under SPT-RI-236. The 400kV substation at Redshaw is being constructed under SPT-RI-2060. The 132kV double busbar substation to be established here will also require installation of two 400/132kV 360MVA transformers. (SPT-RI3060) | 30/04/2030
|  | CS-09437 | SP Distribution plc |  | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 30/04/2030
Richborough | PRO-001214 | CS-04232 | SOUTH EASTERN POWER NETWORKS PLC | Richborough GSP | NGET-RI-21497-3 | At Canterbury North 400kV substation, construct a new 400kV GIS double busbar substation linked to mesh corners 3 and 4 of the existing substation, consisting of 6 feeder bays, one bus-coupler bay, and one bus-section. In addition, two bays for MSCs or SVCs would be required if there is sufficient space. Turn the Canterbury North – Sellindge 2 and Canterbury - Kemsley 2 into the new 400kV GIS double busbar substation at Canterbury North. | 08/12/2023
|  | CS-04233 | SOUTH EASTERN POWER NETWORKS PLC | Richborough GSP | Thermal overload relief work. | Thermal overload relief work. | 08/12/2023
|  | CS-04230 | SOUTH EASTERN POWER NETWORKS PLC | Richborough GSP | NGET-RI-21497-1 | At Richborough construct a new 400kV GIS double busbar substation to provide one HVDC connection and two circuit connection from Richborough to Canterbury North. | 08/12/2023
|  | CS-04231 | SOUTH EASTERN POWER NETWORKS PLC | Richborough GSP | NGET-RI-21497-2 | Build a new 400kV OHL double circuit from Richborough 400kV GIS substation to the new 400kV double busbar GIS substation at Canterbury North, strung with 2 x 500mm SQ AAAC conductor operating 65°C. | 08/12/2023
Richborough 1 | PRO-001165 | CS-06931 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation | 100873 – 201755 | 1. Extension of the existing Richborough 400kV substation. 2. Install a tertiary cable box or bushings on the SGT 1. 3. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 4. Install an earthing transformer. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to User Assets. 6. Extension of the Sellindge OTS to include Richborough Energy Park. | 24/11/2023
|  | CS-06932 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation | 100298-200724 | 1. Re-conductor Fleet-Lovedean 400kV double circuits. | 24/11/2023
|  | CS-06933 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation | 033773-033773 | Thermal upgrade of Bramley – Fleet 400kV double circuits. | 24/11/2023
|  | CS-06934 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation | 033735-200981 | Increase the thermal capacity of the 400kV overhead line from Richborough to Canterbury | 24/11/2023
|  | CS-06935 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation | 31867 | 1. Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent | 24/11/2023
Richborough 2 | PRO-001164 | CS-06936 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation | 100876 –201764 | 1. Extension of the existing Richborough 400kV substation. 2. Install a tertiary cable box or bushings on the SGT 2. 3. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 4. Install an earthing transformer. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to User Assets. 6. Extension of the Sellindge OTS to include Richborough Energy Park. | 25/08/2023
|  | CS-06937 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation | 100298-200724 | 1. Re-conductor Fleet-Lovedean 400kV double circuits. | 25/08/2023
|  | CS-06938 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation | 033773-033773 | Thermal upgrade of Bramley – Fleet 400kV double circuits. | 25/08/2023
|  | CS-06939 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation | 033735-200981 | Increase the thermal capacity of the 400kV overhead line from Richborough to Canterbury | 25/08/2023
|  | CS-06940 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation | 31867 | 1. Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent | 25/08/2023
Ridham Battery Storage | PRO-002565 | CS-07729 | CAMBRIDGE POWER LIMITED | Kemsley 400kV Substation | 101747-203693 | 1. Build temporary overhead line to divert the Grain – Kemsley 2 400kV transmission circuit to allow for turning in this circuit and to feed the new 400kV substation. 2. Turn-in the Grain – Kemsley 2 400kV transmission circuit in to the Kemsley B Substation*, creating new “Kemsley – Kemsley B” and “Kemsley B – Grain” 400kV transmission circuits. (*Substation name, design and location subject to further engineering assessment during the Relevant Transmission Licensee’s option selection phase). 3. Reconductoring of the new Kemsley – Kemsley B 400kV transmission circuit to achieve 2700MVA pre-fault summer rating. | 31/10/2031
|  | CS-07731 | CAMBRIDGE POWER LIMITED | Kemsley 400kV Substation | 031867-200324 | Completion of Sea Link, the planned high voltage undersea electricity link between Suffolk and Kent. | 31/10/2031
|  | CS-07730 | CAMBRIDGE POWER LIMITED | Kemsley 400kV Substation | 101747-203471 | 1. Consenting, design and build of a new 4 bay double busbar 400kV AIS substation consisting of 2 feeder bays, bus section and generator bay adjacent to Grain – Kemsley 2 circuit | 31/10/2031
Rivox Wind Farm | PRO-001944 | CS-07192 | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV | Rivox Item 1 | Installation of a new 400kV double busbar bay at Moffat substation including a platform extension of the existing substation | 10/10/2031
|  | CS-07193 | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV | Rivox Item 2 | Installation of a 400kV cable circuit (approx. 700m) between the new switch bay and the location of the new 400/132kV supergrid transformer | 10/10/2031
|  | CS-07194 | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV | Rivox Item 3 | Installation of a new 400kV transformer disconnector | 10/10/2031
|  | CS-07195 | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV | Rivox Item 4 | Installation of a new 400/132kV 360MVA transformer. | 10/10/2031
|  | CS-07196 | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV | Rivox Item 5 | Civil works to extend the existing Moffat substation compound. | 10/10/2031
|  | CS-07197 | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV | Rivox Item 6 | Installation of a new 132kV circuit breaker at Moffat substation. | 10/10/2031
|  | CS-07198 | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV | Rivox Item 7 | Installation of a new 132kV cable/OHL circuit between Moffat and Rivox WF substation. | 10/10/2031
|  | CS-07199 | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV | Rivox item 8 | Installation of three new 132kV line disconnectors at Rivox WF substation | 10/10/2031
|  | CS-07200 | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV | NGET - 101268-202511 | Rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. (NGET - 101268-202511) | 10/10/2031
|  | CS-07201 | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV | NGET-101268-202520 | Uprating of two 132kV cross border OHL circuits (Chapel Cross-Harker and Gretna-Harker-Hawick.) The preferred option is the replacement of the existing conductor with a higher rated conductor. In addition, a third circuit will be created on the single circuit V route to create Gretna-Harker-Hawick 1 and 2. On connection of further customers in Scotland these circuits will eventually become Faw Side-Gretna-Harker 1 and 2. (NGET-101268-202520) | 10/10/2031
Rochdale BESS | PRO-001805 | CS-07027 | Rochdale (BES) Ltd | Rochdale 275kV Substation | 101605-203230 | 1. Install Earthing Transformer on 13kV SGT1 Tertiary connection. 2. Install 13kV cable from 13kV SGT1 Tertiary connection to 13 kV Line Disconnector. 3. Install 13 kV Line Disconnector | 30/06/2024
Rosefield | PRO-001044 | CS-03697 | Rosefield Energyfarm Limited | East Claydon 400kV Substation | 100893-201792 | Extension of the existing East Claydon 400kV Substation Main and Reserve Busbars to accommodate the generator bay. | 30/10/2028
|  | CS-03698 | Rosefield Energyfarm Limited | East Claydon 400kV Substation | 100893-201795 | 1. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT1. 2. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT2. | 30/10/2028
Rothes III Wind Farm | PRO-000900 | CS-06009 | ROTHES III LIMITED | Dallas GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/06/2025
Rothienorman Battery | PRO-001971 | CS-07418 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-07419 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-07420 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-07421 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-07422 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-07423 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-07424 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-07425 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-07426 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-07427 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-07428 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-07429 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-07416 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-07417 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
Rothienorman Flexpower Synchronous Compensation | PRO-001639 | CS-04689 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 15/07/2024
|  | CS-04690 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-025d | North East Reinforcement | 15/07/2024
|  | CS-04691 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 15/07/2024
|  | CS-04692 | ROTHIENORMAN FLEXPOWER LTD | Rothienorman 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 15/07/2024
Rothienorman Sync Comp | PRO-001445 | CS-04551 | ROTHIENORMAN GRID SERVICES LIMITED | Rothienorman 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/03/2024
|  | CS-04552 | ROTHIENORMAN GRID SERVICES LIMITED | Rothienorman 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/03/2024
|  | CS-04553 | ROTHIENORMAN GRID SERVICES LIMITED | Rothienorman 400kV Substation | SHET-RI-025d | North East Reinforcement | 31/03/2024
|  | CS-04554 | ROTHIENORMAN GRID SERVICES LIMITED | Rothienorman 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/03/2024
Rowancraig Wind Farm | PRO-002455 | CS-09230 | Koehler Renewable Energy UK Limited | Glenglass 132/33kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 30/10/2028
|  | CS-09232 | Koehler Renewable Energy UK Limited | Glenglass 132/33kV Substation | Cloud Hill SS Works - Rowancraig | At Cloud Hill substation, extend the substation compound and install one 132kV disconnector | 30/10/2028
|  | CS-09228 | Koehler Renewable Energy UK Limited | Glenglass 132/33kV Substation | SPT-RI-3102 | Glenglass to Cloud Hill 132kV circuit - A new 132kV circuit will be constructed between the Glenglass 132kV substation and the new Cloud Hill 132kV collector substation. At Glenglass 132kV substation, install a new 132kV feeder bay and associated DBB switchgear (circuit breaker, line isolator and DBB disconnector). From here install a new 132kV circuit to the Cloud Hill 132kV collector substation. The collector substation will accommodate the connection of the Cloud Hill 50MW Windfarm and Rowancraig 40MW Windfarm | 30/10/2028
|  | CS-09229 | Koehler Renewable Energy UK Limited | Glenglass 132/33kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 30/10/2028
|  | CS-09231 | Koehler Renewable Energy UK Limited | Glenglass 132/33kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 30/10/2028
Rugeley | PRO-001630 | CS-04577 | IGP SOLAR 17 LIMITED | Rugeley GSP | 101469-202909 | 1. Extension of the existing Rugeley 400kV substation Main and Reserve Busbars to accommodate the User’s bay. 2. Works to facilitate the Category 4 Operational Tripping Scheme as described in the Bilateral Connection Agreement Appendix F3. | 30/08/2029
|  | CS-04578 | IGP SOLAR 17 LIMITED | Rugeley GSP | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/08/2029
|  | CS-04579 | IGP SOLAR 17 LIMITED | Rugeley GSP | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/08/2029
|  | CS-04580 | IGP SOLAR 17 LIMITED | Rugeley GSP | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/08/2029
|  | CS-04581 | IGP SOLAR 17 LIMITED | Rugeley GSP | 100425-200971 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Ironbridge 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/08/2029
|  | CS-04582 | IGP SOLAR 17 LIMITED | Rugeley GSP | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 30/08/2029
|  | CS-04583 | IGP SOLAR 17 LIMITED | Rugeley GSP | 101466-202906 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/08/2029
|  | CS-04584 | IGP SOLAR 17 LIMITED | Rugeley GSP | 101467-202907 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 1820 MVA. | 30/08/2029
|  | CS-04585 | IGP SOLAR 17 LIMITED | Rugeley GSP | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/08/2029
|  | CS-04586 | IGP SOLAR 17 LIMITED | Rugeley GSP | 101278-202528 | 1. Reconductor the Legacy legs of both Connahs Quay – Legacy – Trawsfynydd 1 and 2 circuits with 2x780mm2 conductor. | 30/08/2029
|  | CS-04587 | IGP SOLAR 17 LIMITED | Rugeley GSP | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/08/2029
|  | CS-04588 | IGP SOLAR 17 LIMITED | Rugeley GSP | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/08/2029
Rye House (Tertiary) | PRO-000564 | CS-06941 | ENSO GREEN HOLDINGS LIMITED | Rye House 400kV Substation | 100961-201916 | 1. Install a tertiary cable box or bushings on Rye House (SGT1). 2. Install a 13 kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13 kV Disconnector at the 13 kV side connecting tertiary to Connection Assets. 5. Extension of Rye House 400 kV substation to accommodate the works required for connection to the SGT1 tertiary. | 31/10/2025
Salamander Offshore Wind Farm | PRO-001512 | CS-04885 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | Salamander Item 1 | Teeing off the existing 132V overhead lines between Peterhead Grange and St Fergus Substation and constructing a single 2km steel lattice tower 132kV double overhead circuit to the Salamander Offshore Wind Farm 132kV substation. This includes the installation of 2 x 132kV disconnector at the User’s site, on the Transmission Network side of the metering circuit breakers. | 31/10/2029
|  | CS-04886 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2029
|  | CS-04887 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2029
|  | CS-04888 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2029
|  | CS-04889 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2029
|  | CS-04890 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | SHET-RI-025d | North East Reinforcement | 31/10/2029
|  | CS-04891 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2029
|  | CS-04892 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | SHET-RI-151 | Peterhead – St Fergus 132kV Line Works – Overhead line works to bring the 132kV circuit to ground, including any required modifications. Design and installation of one 132kV circuit breaker with three 132kV disconnectors and associated protection and control equipment for each of the two circuits. | 31/10/2029
|  | CS-04893 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2029
|  | CS-04894 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2029
|  | CS-04895 | SIMPLY BLUE ENERGY (SCOTLAND) LTD. | Peterhead GSP | SHET-RI-150 | Inverguie Tee – Peterhead 132kV Reconductoring – Reconductor approximately 6.7km of 132kV OHL between the Inverguie Tee and Peterhead 132kV substation. The circuit should be reconductored with a conductor capable of a minimum summer pre-fault rating of 226MVA | 31/10/2029
Sallachy Wind Farm | PRO-002137 | CS-07710 | WKN SALLACHY LIMITED | Cassley GSP | Sallachy Wind Farm | The sole use enabling works will include the offline installation of a 132kV Transformer Circuit Breaker, 110 and transformer disconnector,113 at Cassley 132/33kV GSP Substation | 31/08/2027
|  | CS-07711 | WKN SALLACHY LIMITED | Cassley GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/08/2027
Saltend North | PRO-002666 | CS-08415 | NORTHERN POWERGRID (YORKSHIRE) PLC | Saltend North GSP | 102686-205376 | 1. Construct a new Saltend North 275kV GIS substation with a double busbar arrangement to consist of space for 4 SGT bay, 4 feeder bays, 1 bus section and 2 bus couplers. 2. Establish a new 275kV turn-in circuit at the new Saltend North 275kV substation on the Hedon to Saltend South 275kV OHL circuit including all associated OHL droppers including bay population and reconfiguration works. | 31/10/2037
SANDFORD | PRO-002600 | CS-08922 | SSE DE SOLAR HOLDCO LIMITED | Sandford 400kV | 102609-205237 | Turn in the Hinkley Point B – Seabank circuit to form Hinkley Point B – Sandford B and Sandford B – Seabank. Construct a new 400kV double busbar AIS substation (Sandford B) near the existing Sandford 400kV substation, consisting of two feeder bays and a space for the connection of the User’s bay. | 20/10/2037
Sandy Knowe Wind Farm | PRO-000345 | CS-06016 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | Sandy knowe Item 1 | At Sandy Knowe wind farm 132kV substation, installation of one line isolator to connect to the Sandy Knowe-Glenglass 132kV circuit. | 31/10/2027
|  | CS-06017 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 31/10/2027
|  | CS-06018 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 31/10/2027
|  | CS-06019 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill Substation, heading east, to 132kV Black Hill Substation. Black Hill Substation will include three new 132kV circuit breaker (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 31/10/2027
|  | CS-06020 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-022 | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 31/10/2027
|  | CS-06021 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | Sandy Knowe Item 2 | Installation of 132kV underground cable (approximately 7km), and an optical fibre, between Glenglass 132/33kV substation and Sandy Knowe wind farm substation. | 31/10/2027
|  | CS-06022 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | Sandy Knowe Item 3 | Installation of a line isolator in Glenglass substation. | 31/10/2027
|  | CS-06023 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 31/10/2027
|  | CS-06024 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 31/10/2027
|  | CS-06025 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 31/10/2027
|  | CS-07226 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 31/10/2027
|  | CS-07227 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 31/10/2027
|  | CS-07228 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 31/10/2027
|  | CS-03704 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | Sandy Knowe Item 4 | Establish a tee point for the Sandy Knowe circuit into the Blackhill to Glenglass 132kV circuit. | 31/10/2027
|  | CS-03705 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | Sandy Knowe Item 5 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 31/10/2027
|  | CS-03708 | SANDY KNOWE WIND FARM LIMITED | Sandy Knowe Wind Farm 132kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 31/10/2027
Sanquhar II Wind Farm | PRO-000352 | CS-06026 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 30/04/2024
|  | CS-06027 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/04/2024
|  | CS-06028 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill Substation, heading east, to 132kV Black Hill Substation. Black Hill Substation will include three new 132kV circuit breaker (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 30/04/2024
|  | CS-06029 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-022 | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 30/04/2024
|  | CS-06030 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 30/04/2024
|  | CS-06031 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 30/04/2024
|  | CS-06032 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | Sandy Knowe Wind Farm H1 Works | At Glenglass 132/33kV substation a new 132kV double switchbay (consisting of five line isolators and two circuit breakers owned by the relevant transmission licensee) and associated apparatus will be installed. | 30/04/2024
|  | CS-06033 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/04/2024
|  | CS-06034 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/04/2024
|  | CS-03706 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | Sanquhar II Item 2 | Installation of a 132kV underground cable (approximately 4km), and an optical fibre, betweenSanquhar II 132kV and Glenglass 132kV Substation. | 30/04/2024
|  | CS-03707 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | Sanqhuar II Item 3 | At Glenglass substation, install a new 132kV switch bay and associated equipment and apparatus. | 30/04/2024
|  | CS-03709 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 30/04/2024
|  | CS-03710 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | Sanquhar II Item 1 | At Sanquhar II Substation, install one 132kV line disconnector to connect to the Sanquhar II to Glenglass 132kV circuit. | 30/04/2024
|  | CS-03711 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | Sanquhar II Item 4 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F to the Bilateral Connection Agreement. | 30/04/2024
|  | CS-03712 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 30/04/2024
|  | CS-03713 | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/04/2024
Scaraben Offshore Wind Farm | PRO-002401 | CS-07858 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-180 | Second Peterhead 400kV Busbar - Construct a second 400kV Substation at Peterhead | 31/10/2033
|  | CS-07843 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-25c | 0 | 31/10/2033
|  | CS-07847 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-07852 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-07848 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-07857 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-179 | 0 | 31/10/2033
|  | CS-07841 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-25a | 0 | 31/10/2033
|  | CS-07842 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-25b | 0 | 31/10/2033
|  | CS-07849 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-07844 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-25d | 0 | 31/10/2033
|  | CS-07851 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-07853 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-07846 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-07845 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-07840 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-07854 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-07856 | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
Scatsta1 Greener Grid Park | PRO-002669 | CS-08410 | STATKRAFT UK LTD | Scatsta 132kV Substation | Scatsta1 ESS H1 SS Works | The construction of a new 20.35 km double 132 kV circuits, comprising for one circuit, 15 km Overhead Line (OHL) and 5.35 km Under Ground Cable (UGC) sections and for the other circuit, 18 km Overhead Line (OHL) and 2.35 km Under Ground Cable (UGC) sections, from Kergord substation terminating on two new indoor 132 kV line disconnectors (1113 / 1213) installed within a Relevant Transmission Licensee’s building at Scatsta 132 kV substation | 31/10/2028
|  | CS-08411 | STATKRAFT UK LTD | Scatsta 132kV Substation | Scatsta1 ESS H1 SS Works | The 132 kV circuits will be connected to Kergord substation via two new fully equipped 132 kV feeder circuit breaker bays, complete with 2 x 132 kV busbar selection switches (1104 and 1106 / 1204 and 1206), 1 x 132 kV circuit breaker (1105 / 1205), 1 x 132 kV line disconnector (1103 / 1203) and associated protection equipment | 31/10/2028
|  | CS-08413 | STATKRAFT UK LTD | Scatsta 132kV Substation | SHET-RI-152 | Shetland ANM Scheme - ANM System on Shetland to manage flows across 600MW HVDC link (established under SHET-RI-053) from Kergord 132kV substation on Shetland to the Scottish mainland at an HVDC convertor station in the vicinity of Noss Head in Caithness. (SHET-RI-152) | 31/10/2028
|  | CS-08412 | STATKRAFT UK LTD | Scatsta 132kV Substation | SHET-RI-053 | Shetland 600MW HVDC Link and Kergord 132kV Substation ‒ Construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Noss Head in Caithness. The HVDC switching station works will be part of SHET-RI-062 and will integrate with the Caithness-Moray Transmission Reinforcement (part of SHET-RI-031). The HVDC link includes a 600MW HVDC converter station and 132kV Substation at Kergord in Shetland. The new 132kV Substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of subsea cable between Shetland and the HVDC switching station in Caithness. (SHET-RI-053) | 31/10/2028
Scira-Dudgeon Extension | PRO-000507 | CS-06378 | EQUINOR NEW ENERGY LIMITED | Norwich Main 400kV Substation | 100381-200905 | 1. Extension of the Norwich Main 400kV AIS Substation at Main Busbar (M2) and Reserve Busbar (R2) to accommodate an OFTO bay. 2. Extension of the existing East Anglia operational intertripping scheme to include the connection. | 01/01/2029
|  | CS-06379 | EQUINOR NEW ENERGY LIMITED | Norwich Main 400kV Substation | 100409-200941 | East Anglia NPS mitigation strategies. | 01/01/2029
|  | CS-08266 | EQUINOR NEW ENERGY LIMITED | Norwich Main 400kV Substation | 100709-201476 | Extension of the existing Norwich Main 400 kV substation by 2 bays to accommodate a new double circuit Bramford - Norwich Main | 01/01/2029
|  | CS-08265 | EQUINOR NEW ENERGY LIMITED | Norwich Main 400kV Substation | 100881-201773 | Install two 225 Mvar MSCs at Norwich Main 400 kV substation. Extension of Norwich Main 400 kV substation to accommodate the new MSCs. | 01/01/2029
|  | CS-08264 | EQUINOR NEW ENERGY LIMITED | Norwich Main 400kV Substation | 032452-203187 | Extension of the existing 400kV substation for the construction of fully populated main and reserve bus section bays with circuit breakers, one new bus coupler bay and one new feeder bay to accommodate transfer of the Norwich Main – Bramford 1 feeder circuit | 01/01/2029
|  | CS-09731 | EQUINOR NEW ENERGY LIMITED | Norwich Main 400kV Substation | 102875-206098 | At Norwich Main 400kV: Replace circuit breakers X305, X605, X805 and X105. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/01/2029
|  | CS-09730 | EQUINOR NEW ENERGY LIMITED | Norwich Main 400kV Substation | 101294-202560 | At Norwich Main 400kV: Replace circuit breakers X120 and X320 Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 01/01/2029
Sclenteuch Energy Park | PRO-002195 | CS-08478 | Renewable Energy Systems Limited | Sclenteuch Energy Park 132kV | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 31/10/2029
|  | CS-08477 | Renewable Energy Systems Limited | Sclenteuch Energy Park 132kV | SPT-RI-224 | At Coylton substation, the existing SGT1 and SGT2 275/132kV 120MVA transformers will be replaced (on line) with 240MVA units. | 31/10/2029
Scoop Hill Wind Farm | PRO-000327 | CS-06035 | COMMUNITY WINDPOWER LIMITED | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Item 1 | At Moffat 132kV substation install two 132kV feeder circuit breakers and associated switch bays. | 28/08/2025
|  | CS-06036 | COMMUNITY WINDPOWER LIMITED | Scoop Hill Wind Farm 132kV Substation | SPT-RI-229 - Moffat SGT3 | A new 400/132kV 240MVA transformer, and associated 400kV and 132kV circuit breaker bays, shall be installed at Moffat 400/132kV substation to increase the available generation capacity at the 132kV substation. | 28/08/2025
|  | CS-06037 | COMMUNITY WINDPOWER LIMITED | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Item 2 | Install two sections of 2000mm2 Cu XLPE cable out of Moffat 132kV substation of approximately 300m in length each. | 28/08/2025
|  | CS-06038 | COMMUNITY WINDPOWER LIMITED | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Item 3 | Establish 2x 132kV circuit, incorporating 10km of underground cable and associated auxiliary cable, between Moffat 132kV Substation and Scoop Hill Wind Farm Substation | 28/08/2025
|  | CS-03714 | COMMUNITY WINDPOWER LIMITED | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Item 4 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of this Bilateral Connection Agreement. | 28/08/2025
Scotsburn Road | PRO-002376 | CS-09283 | TBC 002 LIMITED | Fyrish 275kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/10/2030
|  | CS-09284 | TBC 002 LIMITED | Fyrish 275kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2030
|  | CS-09285 | TBC 002 LIMITED | Fyrish 275kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2030
Seabank (Tertiary) | PRO-001068 | CS-05280 | PIVOTED POWER LLP | Seabank 400kV Substation | 100767-201874 | 1. Install earthing transformer on 13kV Tertiary connection 2. Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets for Users connection 4. Installation of a system to generator Category 4 operational intertripping scheme required for the conditions outlined in Appendix F Schedule 1. 5. Works required to connect the User to the Melksham Operational Tripping Scheme as described in Appendix F3 | 01/11/2023
|  | CS-05281 | PIVOTED POWER LLP | Seabank 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 01/11/2023
|  | CS-05282 | PIVOTED POWER LLP | Seabank 400kV Substation | 030572–030752 | . Creation of a new Melksham Operational Tripping Scheme. | 01/11/2023
|  | CS-05283 | PIVOTED POWER LLP | Seabank 400kV Substation | 100298-200724 | Re-conductor Fleet - Lovedean OHL circuits to increase capacity. | 01/11/2023
Seagreen 1A Offshore Wind Farm | PRO-000703 | CS-03694 | SEAGREEN 1A LIMITED | Cockenzie 275kV Substation | Seagreen 1+ Enabling Works | 1. Installation of 275kV plant and apparatus at Cockenzie 275kV Substation which will form the connection to the transmission interface point, including busbars, disconnectors, earth witches, surge arresters, current and voltage transformers. 2. Modification of existing Bay No.3 at Cockenzie 275kV Substation, including relocation and replacement of existing assets as required. | 01/04/2026
|  | CS-04280 | SEAGREEN 1A LIMITED | Cockenzie 275kV Substation | SPT-RI-1742 Cockenzie LMS (Cat 2) | 4. Cockenzie Load Management Scheme (Cat 2) – An overload protection scheme is proposed to be installed within the Cockenzie – Smeaton – Kaimes – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following defined system outage conditions. (SPT-RI-1742) | 01/04/2026
Seagreen 1 Offshore Wind Farm | PRO-000527 | CS-05700 | Seagreen Wind Energy Limited | Tealing 275/33kV Substation | Seagreen 1 Offshore Wind Farm H1 Stage 1 | Install two 275kV double-busbar feeder bay (L85 & L135) (275kV circuit breaker and busbar selector isolators) and the associated line isolators | 15/02/2022
|  | CS-05701 | Seagreen Wind Energy Limited | Tealing 275/33kV Substation | SHET-RI-117 | Tealing 275kV Busbar Upgrade – At Tealing substation, upgrade the 275kV busbar to a rating of 4000A, and install a new 275kV bus coupler circuit breaker on the east side of the busbar. | 15/02/2022
|  | CS-08515 | Seagreen Wind Energy Limited | Tealing 275/33kV Substation | Seagreen 1 Offshore Wind Farm H1 Stage 2 | The Enabling Works (Stages 2-5) comprise the completion of the Enabling Works (Stage 1) and the following | 15/02/2022
Sealtainn Offshore Wind Farm | PRO-002670 | CS-08779 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-08781 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-08778 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 31/10/2033
|  | CS-08784 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-08774 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-08775 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-08777 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-08771 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 31/10/2033
|  | CS-08780 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 31/10/2033
|  | CS-08782 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-08772 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-08785 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 31/10/2033
|  | CS-08783 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-08773 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-08776 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-08786 | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
Sellindge (Tertiary) | PRO-001067 | CS-05284 | PIVOTED POWER LLP | Sellindge 400kV Substation | 100536-201122 | 1. Install earthing transformer on 13kV Tertiary connection 2. Install 13kV cable from 13kV Tertiary connection to 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets for Users connection. 4. Works required to connect User to the Sellindge Operational Tripping Scheme as described in Appendix F3. | 01/11/2024
|  | CS-05285 | PIVOTED POWER LLP | Sellindge 400kV Substation | 021497-033111 | Installation of Flexible AC Transmission Solutions (FACTS) and MSCs at Bolney, Ninfield and Richborough and associated works | 01/11/2024
|  | CS-05286 | PIVOTED POWER LLP | Sellindge 400kV Substation | 100298-200724 | Re-conductor Fleet - Lovedean OHL circuits to increase capacity. | 01/11/2024
|  | CS-05287 | PIVOTED POWER LLP | Sellindge 400kV Substation | 021497-021497 | The works to establish the new Richborough 400/132kV Grid Supply Point. Including any Connection Asset works required for the Third Party supplied via the Grid Supply Point. | 01/11/2024
|  | CS-05288 | PIVOTED POWER LLP | Sellindge 400kV Substation | 031885-031885 | Re-conductor the Bramley — Fleet OHL circuits to increase capacity | 01/11/2024
|  | CS-05289 | PIVOTED POWER LLP | Sellindge 400kV Substation | 31867 | 1. Thermal reinforcement to the South Coast, New Offshore HVDC link between Suffolk and Kent | 01/11/2024
Sellindge Grid Stability Services | PRO-002206 | CS-07063 | SELLINDGE GRID SERVICES LIMITED | Sellindge 400kV Substation | 101670-203325 | GIS building extension and double GIS busbar extension of R3 and M3 at the new Sellindge Compound B 400kV substation to facilitate the connection of The User’s bay with ownership boundary as per CUSC 2.12.1 (f) (ii). | 31/10/2025
Selms Muir Solar & Battery Storage | PRO-001885 | CS-07365 | SP Distribution plc | Livingston East GSP | SPT-RI-2323 | 0 | 31/07/2026
|  | CS-07366 | SP Distribution plc | Livingston East GSP | Selms Muir Sole Enabling Works | 0 | 31/07/2026
SHBEC | PRO-001096 | CS-04748 | EP SHB LIMITED | South Humber Bank 400kV Substation | 101810-203711 | 1. Extend GIS busbar at South Humber Bank 400kV Substation and install the GIS interface point for the new bay 2. Install the Operational Tripping Schemes at South Humber Bank 400kV Substation | 31/07/2026
|  | CS-04749 | EP SHB LIMITED | South Humber Bank 400kV Substation | 100711-201483 | Extend GIS Busbar at South Humber Bank 400kV Substation and install the GIS interface point for the new bay. | 31/07/2026
Sheilhill Battery Storage | PRO-002149 | CS-07549 | Sheilhill Battery Storage Limited | REVIEW - St Fergus | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-07551 | Sheilhill Battery Storage Limited | REVIEW - St Fergus | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-07550 | Sheilhill Battery Storage Limited | REVIEW - St Fergus | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
|  | CS-07552 | Sheilhill Battery Storage Limited | REVIEW - St Fergus | SHET-RI-187 | St Fergus 132kV Substation- Establish a new 132kV St Fergus double busbar substation at the site of the existing St Fergus 132kV Switching Station. Split the double busbars and establish an open point between them. | 31/10/2033
|  | CS-07553 | Sheilhill Battery Storage Limited | REVIEW - St Fergus | SHET-RI-188 | St Fergus to New Deer 2 132kV Reinforcement – At New Deer 2 400kV Substation, establish a new 132kV busbar at New Deer 2 substation and install 2x240MVA 400/132kV transformers. Construct a new 132kV double circuit overhead line from New Deer 2 to St Fergus substation (Approx. 26 km). | 31/10/2033
Sheirdrim Wind Farm | PRO-001066 | CS-06045 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Sheirdrim 132kV Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 31/10/2029
|  | CS-06042 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Sheirdrim 132kV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2029
|  | CS-06043 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Sheirdrim 132kV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2029
|  | CS-06044 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Sheirdrim 132kV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2029
Shepherds Rig Wind Farm | PRO-000511 | CS-03715 | SETT WIND DEVELOPMENT LIMITED | Shepherds Rig Wind Farm 132kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 30/07/2024
|  | CS-03716 | SETT WIND DEVELOPMENT LIMITED | Shepherds Rig Wind Farm 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 30/07/2024
|  | CS-03717 | SETT WIND DEVELOPMENT LIMITED | Shepherds Rig Wind Farm 132kV Substation | SPT-RI-211 | Construct a new 132kV switching station, named Holm Hill, and install a 132kV OHL circuit between the new site and the tee off points to Shepherds Rig and Lorg wind farms. At an appropriate tee-off point on the New Cumnock to Kendoon 132kV circuit, install the new Holm Hill 132kV Switching Station containing one 132kV circuit breaker with two associated disconnectors. Install ~8km of 132kV wood pole overhead line with High Temperature Low Sag (HTLS) EAGLE conductor (190°C, minimum summer pre-fault rating 295MVA) to the tee point between Shepherd’s Rig and Lorg wind farms. | 30/07/2024
Shewalton Rd Solar Farm | PRO-002178 | CS-07988 | SP Distribution plc | Kilmarnock South GSP | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 25/10/2024
Shipley Road BESS | PRO-002553 | CS-09061 | CSE43 LIMITED | Lovedean 400kV Substation | 102347-204512 | Installation of a Reserve Busbar Section Circuit Breaker (X160) at Bolney 400kV Substation. | 21/10/2031
|  | CS-09060 | CSE43 LIMITED | Lovedean 400kV Substation | 102436-204965 | Replacement, or modification, of existing towers and associated OHL works to facilitate a single Tee-Point connection to a new 400kV substation via the Lovedean - Bolney overhead line circuit. • Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks, and associated infrastructure. • Construction of 400kV busbar to accommodate the OHL Tee-In connection and the Users Generator Bay. • Local works to facilitate the extension of the Melksham Operational Tripping Scheme. | 21/10/2031
|  | CS-09062 | CSE43 LIMITED | Lovedean 400kV Substation | 011642-010177 | Hotwiring of the Bolney – Lovedean – Ninfield circuits to increase their thermal rating. | 21/10/2031
Sinclair Offshore Wind Farm | PRO-003790 | CS-09709 | SINCLAIR OFFSHORE WIND FARM LIMITED | Peterhead 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-09710 | SINCLAIR OFFSHORE WIND FARM LIMITED | Peterhead 400kV Substation | SHET-RI-179 | 0 | 31/10/2033
|  | CS-09711 | SINCLAIR OFFSHORE WIND FARM LIMITED | Peterhead 400kV Substation | SHET-RI-180 | Second Peterhead 400kV Busbar - Construct a second 400kV Substation at Peterhead | 31/10/2033
Sizewell C | PRO-000145 | CS-06046 | Sizewell C Limited | Sizewell 400kV Substation | 20834-4 | Reconductor the two Sizewell – Bramford double circuits | 31/10/2029
|  | CS-06047 | Sizewell C Limited | Sizewell 400kV Substation | 20834-5 | Circuit transfer of 4 Bramford – Sizewell 400kV circuits from the existing Sizewell B GIS substation to the new Sizewell C substation | 31/10/2029
|  | CS-06048 | Sizewell C Limited | Sizewell 400kV Substation | 20834-2 | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 31/10/2029
|  | CS-06049 | Sizewell C Limited | Sizewell 400kV Substation | 20315S | Construct an initial 9 bay 400kV GIS substation at Bramford as a 2 section substation with one bus coupler and two bus sections to be subsequently extended by a further section turning in existing Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 31/10/2029
|  | CS-06050 | Sizewell C Limited | Sizewell 400kV Substation | NGET-RI-20834-1 | Installation of two 400kV 3000MVA reactors in the existing Sizewell 400kV GIS substation site by utilizing and populating the four spare bays on the existing GIS originally identified for future nuclear generator station and unit transformer connections. | 31/10/2029
Sizing John (Rainhill) | PRO-001581 | CS-06942 | SIZING JOHN LIMITED | Rainhill GSP | 101326-202646 | 1.Replace the 4 x 132kV SGT breakers (180, 280, 380, 480) at Rainhill substation | 30/10/2024
|  | CS-06943 | SIZING JOHN LIMITED | Rainhill GSP | 101326-202643 | 1. Establish a 132kV LV banked connection onto SGT1 to accommodate User’s connection 2. Install a 132kV Disconnector to provide isolation from the User’s circuit | 30/10/2024
Slickly Wind Farm | PRO-001517 | CS-06523 | Slickly Wind Farm Limited | Slickly 132/33kV Substation | SHET-RI-028 Thurso to Gills Bay | Gills Bay – Thurso South 132kV Double Circuit - It is proposed to construct a new 132kV GIS double busbar arrangement substation at a suitable location around Gills Bay (west of John O’Groats) and connect in two OHL radial circuits from Thurso south. (SHET-RI-028). | 31/10/2028
|  | CS-06524 | Slickly Wind Farm Limited | Slickly 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/10/2028
|  | CS-06525 | Slickly Wind Farm Limited | Slickly 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2028
|  | CS-06526 | Slickly Wind Farm Limited | Slickly 132/33kV Substation | no Scheme | 0 | 31/10/2028
|  | CS-06527 | Slickly Wind Farm Limited | Slickly 132/33kV Substation | Slickly Wind Farm H1 Works | Installation of a 132 kV line disconnector (113) connected to the TCA 132 kV Circuit Breaker (110) at the Slickly wind farm 132 kV substation. The 132 kV line disconnector (113) will connect to the incoming 7.5 km 132 kV circuit (comprising 0.5 km underground cable and 7 km of Trident wood pole overhead line) from Gills Bay 132 kV switching station. The 132 kV OHL will be connected to Gills Bay 132 kV switching station via a new fully equipped 132 kV double busbar feeder bay, comprising 132 kV line disconnector (703), 132 kV feeder circuit breaker (705) and 132 kV double busbar selection disconnectors (704/706). The 7.5 km 132 kV circuit between Gills Bay and Slickly terminates on an outdoor type 132 kV line disconnector (113) at Slickly wind farm 132 kV substation and a CSE structure/compound at Gills Bay. | 31/10/2028
Smeaton BESS | PRO-002635 | CS-09238 | KONA ASSET 3 LIMITED | Smeaton 400kV | Smeaton BESS H1 | Installing a new 400kV disconnector at Smeaton 400kV substation to enable a tee off connection from the existing busbars. | 23/06/2028
|  | CS-09240 | KONA ASSET 3 LIMITED | Smeaton 400kV | SPT-RI-204 | Wishaw-Smeaton-Torness-Eccles Overload Protection Scheme -An overload protection scheme is proposed to be installed within the Wishaw – Smeaton – Torness – Eccles 275kV and 400kV network in order to protect the system in compliance with Category 2 Intertripping Scheme as defined by the Grid Code. The intertripping scheme will disconnect the generation within the area following system outage conditions as specified in Appendix F of the Bilateral Connection Agreement - | 23/06/2028
|  | CS-09239 | KONA ASSET 3 LIMITED | Smeaton 400kV | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 23/06/2028
Sneddon Law Wind | PRO-000324 | CS-06055 | SNEDDON LAW COMMUNITY WIND COMPANY LTD | Kilmarnock Town 275/33kV Substation | Sneddon Law Item 1 | Installation and commissioning of a protection scheme to interface with the relevant transmission licensee's protection scheme(s) identified in one off works and relay a signal to the user's wind farm substation in order to disconnect the user's wind farm. These works will need to be completed by the host distribution network operator. | 31/03/2023
|  | CS-06056 | SNEDDON LAW COMMUNITY WIND COMPANY LTD | Kilmarnock Town 275/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 31/03/2023
Sofia Offshore Wind Farm | PRO-000404 | CS-06944 | SOFIA OFFSHORE WIND FARM LIMITED | Dogger Bank 220kV Offshores | 031571-031571 | Extend the GIS busbars to the west of Lackenby 400kV substation to Onshore Transmissionprovide the customer’s connection bay. | 01/09/2024
|  | CS-06945 | SOFIA OFFSHORE WIND FARM LIMITED | Dogger Bank 220kV Offshores | 100090-200245 | Drax-Thornton 1 circuit – Uprate existing quad zebra conductors to achieve required rating. | 01/09/2024
|  | CS-06057 | SOFIA OFFSHORE WIND FARM LIMITED | Dogger Bank 220kV Offshores | NGET-RI-31571 | Extend Lackenby 400kV substation to make available a single, skeletal OFTO bay for the relevant Transmission Licensee at the interface point. | 01/09/2024
Somerford | PRO-001631 | CS-06946 | PD813ETY LTD | Minety 400kV Substation | 101488-202944 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays 3. Establish new bus bar, 33kV substation at Minety to be connected via new 400/33kV SGT8B 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 30/06/2025
|  | CS-06947 | PD813ETY LTD | Minety 400kV Substation | 020903-020903 | Uprating of Cowley-Minety 400kV circuit and Cowley-Minety 400kV cables to achieve 1300 MVA pre-fault Summer rating. | 30/06/2025
|  | CS-06948 | PD813ETY LTD | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 1990MVA | 30/06/2025
Southernlink | PRO-000976 | CS-08218 | NATIONAL GRID INTERCONNECTOR HOLDINGS LIMITED | Grain 400kV Substation | 033694-033694 | Construction of the new Grain West 400 kV GIS double busbar substation consisting of feeder bays, a bus coupler bay Section Breaker and a User bay. | 31/10/2029
|  | CS-08221 | NATIONAL GRID INTERCONNECTOR HOLDINGS LIMITED | Grain 400kV Substation | 033694-201373 | Turn in of the Grain to Tilbury 400 kV circuit - Reconductor OHL circuits and reinforce cable circuits to achieve 2350 MVA pre-fault and 3200 post fault rating. | 31/10/2029
|  | CS-08219 | NATIONAL GRID INTERCONNECTOR HOLDINGS LIMITED | Grain 400kV Substation | 101999-204134 | Turn in of the Grain to Kingsnorth 400 kV circuit - Reconductor OHL circuits and reinforce cable circuits to achieve 2350 MVA pre-fault and 3200 post fault rating. | 31/10/2029
|  | CS-08516 | NATIONAL GRID INTERCONNECTOR HOLDINGS LIMITED | Grain 400kV Substation | 100379-201163 | Make provision for the connection of the Users second bay at Grain West 400kV GIS Substation. | 31/10/2029
Southery | PRO-002172 | CS-07774 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 30/10/2031
|  | CS-07775 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 100676-201432 | At Walpole 400 kV Substation: Uprate the disconnector and feeder protection on the future Kings Lynn-Walpole 400 kV circuit to provide a winter post-fault rating of 3680 MVA | 30/10/2031
|  | CS-07777 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 020340-020340 | Reconductor Bramford-Norwich Main-Yaxley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 30/10/2031
|  | CS-07780 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 30/10/2031
|  | CS-07782 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 30/10/2031
|  | CS-07779 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 30/10/2031
|  | CS-07791 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 101294-202560 | At Norwich Main 400kV: Replace circuit breakers X120 and X320 Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 30/10/2031
|  | CS-07794 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 101995-204129 | At Rye House 400kV: Replace circuit breakers X130. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2031
|  | CS-07772 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 101994-204128 | Installation of a new AIS double busbar 400kV substation between Burwell Main 400 kV and Walpole 400 kV with associated two feeder bays, space for a generation bay and a busbar coupler. Provide a single turn in connection of the new substation to the Burwell Main – Walpole OHL circuit 2 | 30/10/2031
|  | CS-07773 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 30/10/2031
|  | CS-07784 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 100952-201899 | Uprate all three downdroppers on the East Claydon - Leighton Buzzard - Sundon circuit to provide a pre-fault summer rating of 2400MVA | 30/10/2031
|  | CS-07792 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 30/10/2031
|  | CS-07786 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 30/10/2031
|  | CS-07788 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 30/10/2031
|  | CS-07789 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 100591-201213 | Reconductor Ratcliffe – Staythorpe 400kV circuit; reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 2780MVA | 30/10/2031
|  | CS-07785 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 30/10/2031
|  | CS-07787 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm2 and 3M curlew 2x490mm2 @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm2 conductor | 30/10/2031
|  | CS-07790 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 30/10/2031
|  | CS-07776 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 101964-204086 | At Walpole 400kV: Replace circuit breakers X110, X130, X305, X510, X310. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2031
|  | CS-07793 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 30/10/2031
|  | CS-07778 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3820 MVA | 30/10/2031
|  | CS-07781 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400 kV with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3100 MVA. | 30/10/2031
|  | CS-07783 | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 30/10/2031
South Esk Solar Farm | PRO-001222 | CS-06058 | Scottish Hydro Electric Power Distribution Plc | Bridge of Dun GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 31/10/2026
|  | CS-06059 | Scottish Hydro Electric Power Distribution Plc | Bridge of Dun GSP | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2026
Southfields | PRO-001632 | CS-06949 | PD503HAN LTD | Minety 400kV Substation | 101488-202940 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new busbar 33kV substation at Minety to be connected via new 400/33kV SGT8A. 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 30/06/2025
|  | CS-06950 | PD503HAN LTD | Minety 400kV Substation | 020903-020903 | Uprating of Cowley-Minety 400kV circuit and Cowley-Minety 400kV cables to achieve 1300 MVA pre-fault Summer rating. | 30/06/2025
|  | CS-06951 | PD503HAN LTD | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 30/06/2025
Southfields Farm | PRO-001852 | CS-07338 | PD300RON Ltd | Minety 400kV Substation | 101488-202945 | 1. Extend Mesh Corner 4 at Minety 400kV substation. 2. Installation of new 150MVA rated 400/33kV SGT including HV and LV bays. 3. Establish new busbar 33kV substation at Minety to be connected via new 400/33kV SGT8A. 4. Installation of an earthing transformer connecting onto the 33kV busbar. | 31/10/2028
|  | CS-07339 | PD300RON Ltd | Minety 400kV Substation | 020903-020903 | Uprating of Cowley-Minety 400kV circuit and Cowley-Minety 400kV cables to achieve 1300 MVA pre-fault Summer rating. | 31/10/2028
|  | CS-07340 | PD300RON Ltd | Minety 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 31/10/2028
South Kyle 2 Wind farm | PRO-001963 | CS-07390 | VATTENFALL WIND POWER LTD | South Kyle 2 132/33kV Substation | SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 25/05/2029
|  | CS-07391 | VATTENFALL WIND POWER LTD | South Kyle 2 132/33kV Substation | SPT-RI-2389 CZ2A Route Tower | 0 | 25/05/2029
|  | CS-07392 | VATTENFALL WIND POWER LTD | South Kyle 2 132/33kV Substation | South Kyle 2 Wind Farm_A1 works | 0 | 25/05/2029
Spalding Energy Expansion | PRO-000249 | CS-06063 | SPALDING ENERGY EXPANSION LIMITED | Spalding North 400kV Substation | NGET-RI-21765-1 | Extend and convert the existing Bicker Fen 400kV substation to a double busbar AIS substation with 4 feeder bays, 2 transformer bays, 1 bus coupler bays and 2 skeleton bus section bays to accommodating the existing 4 circuits and 2 transformers. Build 4 feeder bays, 2 transformer bays and one bus coupler and fully equip these bays. Modify the existing protection scheme to include 4 feeders, 2 transformers and one bus coupler. | 30/10/2030
|  | CS-06062 | SPALDING ENERGY EXPANSION LIMITED | Spalding North 400kV Substation | NGET-RI-21339S | • To provide one generator bay. • To modify existing busbar protection to include the new generation connection. • To install ancillary services monitoring equipment. | 30/10/2030
Spalding PV and BESS Station | PRO-002768 | CS-08579 | ETP UK 1 LTD | Weston Marsh 400kV Substation | 102747-205542 | Extension of main and reverse busbar at Weston Marsh 400kV substation to facilitate connection of users generator bay. | 30/07/2033
|  | CS-08580 | ETP UK 1 LTD | Weston Marsh 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 30/07/2033
|  | CS-08581 | ETP UK 1 LTD | Weston Marsh 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 30/07/2033
Spennymoor | PRO-001138 | CS-05290 | PIVOTED POWER LLP | Spennymoor 400kV Substation | NGET-R1-100248-200687 (INFRA) | 1. Install earthing transformer on 13kV Tertiary connection 2. Install 13kV disconnector connecting tertiary to connection assets for Users connection | 31/10/2028
| PRO-002698 | CS-08416 | NORTHERN POWERGRID (NORTHEAST) PLC | Spennymoor GSP | 101920-203930 | 1. Extend the existing Auto Clock Scheme. 2. Convert MC4 to provide a suitable connection point. 3. Retrofit and install a 400kV line feeder circuit breaker and bay. 4. Substation extension including fence line and cut and fill. 5. P & C modifications. | 08/10/2023
Spennymoor BESS | PRO-002035 | CS-09233 | CSE27 LIMITED | Spennymoor 400kV Substation | 101917-203914 | 1. Install Earthing Transformer on 13kV Tertiary Connection 2. Install 13kV Cable from Tertiary connection to 13kV Disconnector 3. Install 13kV Disconnector at the 13kV side connecting the Tertiary connection to Connection Assets for User’s connection. | 30/07/2032
Spennymoor Greener Grid Park | PRO-002041 | CS-09692 | STATKRAFT UK LTD | Spennymoor 400kV Substation | 101863-203825 | Extend the Busbar MC2 at Spennymoor 400kV to make provision for the User to connect their equipment | 29/10/2027
Speyslaw Solar | PRO-001278 | CS-06067 | SPEYSLAW SOLAR LIMITED | Elgin GSP | SHET-RI-073 | Keith MacDuff 132kV Blackhillock Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kV transmission network by reconfiguring the Macduff transmission circuits away from Keith 132kV substation. | 30/06/2025
|  | CS-06068 | SPEYSLAW SOLAR LIMITED | Elgin GSP | SHET-RI-099 | Beauly – Keith 132kV Reconductoring - Reconductor approximately 108km of the existing 132kV double circuit OHL between Beauly and Keith 132kV substations. This double circuit is to be reconductored with a minimum summer pre-fault rating of 176MVA. | 30/06/2025
|  | CS-06069 | SPEYSLAW SOLAR LIMITED | Elgin GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 30/06/2025
Spiorad Na Mara Offshore Wind Farm | PRO-001642 | CS-04448 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | NPI A H1 Enabling Works | At Dounreay 400kV substation, install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV circuit breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Onshore Transmission Licensee and the User, as OTSDUW User, will be the User’s side of the new 400kV disconnectors at New Dounreay 400kV substation. | 31/10/2030
|  | CS-04449 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2030
|  | CS-04450 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2030
|  | CS-04451 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2030
|  | CS-04452 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2030
|  | CS-04453 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2030
|  | CS-04454 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2030
|  | CS-04455 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-127 | Dounreay – Spittal 400kV Double Circuit OHL - Establish two new 400kV double busbars, one at a new site close to Dounreay and the second at Spittal. Construct approximately 15km of new 400kV double circuit overhead line from the new site close to Dounreay and Spittal. (SHET-RI-127) | 31/10/2030
|  | CS-04456 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2030
|  | CS-04457 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-025d | North East Reinforcement | 31/10/2030
|  | CS-04458 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2030
|  | CS-04459 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2030
|  | CS-04460 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2030
|  | CS-04461 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2030
|  | CS-04462 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2030
|  | CS-04463 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2030
|  | CS-04464 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-142 | Dounreay to Spittal 400kV Cable - Extend the 400kV double busbar at Dounreay 400kV substation to form 4 sections, install a new single 400kV underground cable circuit from Dounreay 400kV substation to Spittal 400kV substation | 31/10/2030
|  | CS-04465 | Northland Power UK Limited | NPI C 220/66KV OFFSHORE SUBSTATION | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2030
Spirebush Renewable Energy Project | PRO-001692 | CS-07434 | Spirebush Ltd | Spirebush 132kV Substation | Spirebush H1 - 132kV AIS feeder bays | Installation of two new 132kV AIS feeder bays at Redshaw 132kV substation | 01/07/2028
|  | CS-07435 | Spirebush Ltd | Spirebush 132kV Substation | Spirebush H1 - 132kV circuits. Redshaw 132kV - Spirebush 132kV Substations | Installation of two new 132kV circuits between Redshaw 132kV and Spirebush 132kV Substations, circuit length approximately 18km. | 01/07/2028
|  | CS-07436 | Spirebush Ltd | Spirebush 132kV Substation | Spirebush H1 - Two 132kV line disconnectors at Spirebush 132kV Substation | Installation of two 132kV line disconnectors at Spirebush 132kV Substation. | 01/07/2028
|  | CS-07437 | Spirebush Ltd | Spirebush 132kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 01/07/2028
|  | CS-07438 | Spirebush Ltd | Spirebush 132kV Substation | SPT-RI-2061 | Redshaw 132kV Substation - Create of a new 132kV substation connecting into the Redshaw 400kV substation to be constructed under SPT-RI-2060. This 132kV substation will establish a collector substation in this area. (SPT-RI-2061) | 01/07/2028
|  | CS-07439 | Spirebush Ltd | Spirebush 132kV Substation | SPT-RI-2139 | Redshaw 400/132kV SGT2 - a new 360MVA 400/132kV supergrid transformer and associated 400kV and 132kV circuit breakers will be installed. This will increase the thermal capacity of Redshaw 132kV substation. | 01/07/2028
Spittal BESS Station | PRO-003618 | CS-09524 | IGP ENERGY STORAGE 5 LIMITED | Spittal 400kV | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 31/10/2033
|  | CS-09526 | IGP ENERGY STORAGE 5 LIMITED | Spittal 400kV | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2033
|  | CS-09523 | IGP ENERGY STORAGE 5 LIMITED | Spittal 400kV | SHET-RI-140 | 1. Thurso South 275kV Substation Redevelopment - Redevelop the existing Thurso South 275kV substation into a new 275kV double busbar arrangement | 31/10/2033
|  | CS-09527 | IGP ENERGY STORAGE 5 LIMITED | Spittal 400kV | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2033
|  | CS-09522 | IGP ENERGY STORAGE 5 LIMITED | Spittal 400kV | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 31/10/2033
|  | CS-09525 | IGP ENERGY STORAGE 5 LIMITED | Spittal 400kV | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 31/10/2033
|  | CS-09520 | IGP ENERGY STORAGE 5 LIMITED | Spittal 400kV | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/10/2033
|  | CS-09521 | IGP ENERGY STORAGE 5 LIMITED | Spittal 400kV | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90 degrees Celsius to increase the continuous current rating of the circuit | 31/10/2033
SPITTAL MAINS BATTERY ENERGY STORAGE | PRO-002523 | CS-08976 | WRE Broomhill Limited | Spittal 275kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2030
|  | CS-08977 | WRE Broomhill Limited | Spittal 275kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2030
|  | CS-08975 | WRE Broomhill Limited | Spittal 275kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 31/10/2030
|  | CS-08974 | WRE Broomhill Limited | Spittal 275kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 31/10/2030
|  | CS-08973 | WRE Broomhill Limited | Spittal 275kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/10/2030
SSE Celtic Sea 1 | PRO-002405 | CS-08570 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to triple Auriacuria 3 x 700mm2 at 90 degrees to achieve a summer pre-fault rating of 3000MVA | 06/12/2036
|  | CS-08571 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 102444-204992 | Infrastructure works for the generation connection of SSE Celtic Sea Offshore wind farm. | 06/12/2036
|  | CS-08564 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 06/12/2036
|  | CS-08569 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101388-202720 | At Taunton 400k substation turn in the three double circuits from Shurton, Alverdiscott and Exeter into the new GIS Taunton substation. | 06/12/2036
|  | CS-08568 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101388-202719 | Reconfigure the Taunton 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 2 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
|  | CS-08565 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
|  | CS-08566 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
|  | CS-08567 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault summer rating of 1650MVA. | 06/12/2036
SSE Ferrybridge BESS | PRO-001614 | CS-05404 | SSE UTILITY SOLUTIONS LIMITED | Ferrybridge B 132kV Substation | 101503-202960 | Surveying, and protection and control works associated with the User’s connection into a spare bay at Ferrybridge B 132kV substation. | 28/06/2024
|  | CS-05405 | SSE UTILITY SOLUTIONS LIMITED | Ferrybridge B 132kV Substation | 101503-202963 | Replacement of circuit breaker 580 at Ferrybridge B 132kV substation with a 40kA unit tested to an appropriate DC time constant. | 28/06/2024
|  | CS-05406 | SSE UTILITY SOLUTIONS LIMITED | Ferrybridge B 132kV Substation | 101509-202974 | Replace the existing Ferrybridge C 275kV substation, new substation to be established as an offline build with phased circuit transfers. | 28/06/2024
|  | CS-05407 | SSE UTILITY SOLUTIONS LIMITED | Ferrybridge B 132kV Substation | 101503-202961 | Installation of a new 240MVA rated 275/132kV SGT connecting to the new Ferrybridge 275kV substation and to Ferrybridge B 132kV substation including associated auto close scheme | 28/06/2024
SSE Fiddlers Ferry Battery Energy Storage | PRO-001762 | CS-05410 | SSE UTILITY SOLUTIONS LIMITED | Fiddlers Ferry 275kV Substation | 101284-202534 | Reconductor the Legacy - Ironbridge and Legacy – Shrewsbury – Ironbridge 400kV circuits with 2x780mm2 conductor. | 30/04/2025
|  | CS-05411 | SSE UTILITY SOLUTIONS LIMITED | Fiddlers Ferry 275kV Substation | 101279-202529 | Increase thermal rating of the Connah’s Quay leg of Connah’s Quay – Trawsfynydd – Legacy Circuits Reconductor the Padiham-Penwortham 1 circuit to achieve a Summer prefault rating of 2110 MVA | 30/04/2025
|  | CS-05412 | SSE UTILITY SOLUTIONS LIMITED | Fiddlers Ferry 275kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/04/2025
|  | CS-05413 | SSE UTILITY SOLUTIONS LIMITED | Fiddlers Ferry 275kV Substation | 101468-202908 | Reconductor the Daines-Macclesfield 1 circuit to achieve a Summer prefault rating of 2360MVA | 30/04/2025
|  | CS-05414 | SSE UTILITY SOLUTIONS LIMITED | Fiddlers Ferry 275kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 30/04/2025
|  | CS-05415 | SSE UTILITY SOLUTIONS LIMITED | Fiddlers Ferry 275kV Substation | 101381-202706 | Establish a new substation at the Tee-point on the Legacy – Trawsfynydd - Connah’s Quay circuits. | 30/04/2025
|  | CS-05416 | SSE UTILITY SOLUTIONS LIMITED | Fiddlers Ferry 275kV Substation | 101466-202906 | Reconductor the Cellarhead – Daines 400kV with 2x760mm2 conductor or equivalent and uprating of the cable section of the circuit | 30/04/2025
|  | CS-05408 | SSE UTILITY SOLUTIONS LIMITED | Fiddlers Ferry 275kV Substation | 101392-202727 | Infrastructure works for the connection of the Fiddlers Ferry Battery Energy Storage at Fiddlers Ferry 275kV substation. | 30/04/2025
|  | CS-05409 | SSE UTILITY SOLUTIONS LIMITED | Fiddlers Ferry 275kV Substation | 032021-032021 | Replace the conductors on the existing double circuit from Cellarhead to Drakelow with higher rated conductors to increase their thermal rating | 30/04/2025
SSE Offshore 1 | PRO-001488 | CS-06762 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 379/66KV OFFSHORE SUBSTATION | SSE Offshore 1 Enabling | Installation of 400kV plant and apparatus at Cousland 400kV Substation which will form the connections to the SSE 1 Offshore 1 Transmission Interface Points, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers. Provision of communications, alarms and indications . | 31/10/2033
|  | CS-06763 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 379/66KV OFFSHORE SUBSTATION | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 31/10/2033
|  | CS-06764 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 379/66KV OFFSHORE SUBSTATION | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 31/10/2033
|  | CS-06765 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 379/66KV OFFSHORE SUBSTATION | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 31/10/2033
|  | CS-06766 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 379/66KV OFFSHORE SUBSTATION | SPT-RI-1791 | Cockenzie to Eccles (ZA route) Uprating. - The project will uprate the 400kV double circuit between Cockenzie 400kV substation and Eccles 400kV substation from twin Totara to triple Totara operating at 90℃. | 31/10/2033
|  | CS-06767 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 379/66KV OFFSHORE SUBSTATION | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 31/10/2033
|  | CS-06768 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 379/66KV OFFSHORE SUBSTATION | SPT-RI-267 | Eccles 400kV Shunt Compensation - In order maintain to post-fault voltages within statutory limits, the installation of voltage control in the east of the network is required. As such, dynamic shunt compensation will be installed at Eccles 400kV substation with associated switchgear. | 31/10/2033
|  | CS-06769 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 379/66KV OFFSHORE SUBSTATION | SPT-RI-1795 | This project will construct a new 400kV double circuit over the boundary from the South East of Scotland and the North West of England | 31/10/2033
|  | CS-06770 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 379/66KV OFFSHORE SUBSTATION | SPT-RI-1796 | Cousland 400kV GIS Substation - A new 400kV double busbar substation, utilising Gas Insulated Switchgear (GIS), will be established south of Cockenzie in the Cousland area in the vicinity of the Torness/Fallago to Smeaton/Wishaw 400kV double circuit (ZS route) and Cockenzie to Eccles 400kV double circuit (ZA Route) crossing. Both the ZA and the ZS routes will be turned into the new substation. | 31/10/2033
|  | CS-06771 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 379/66KV OFFSHORE SUBSTATION | SPT-RI-1873 | Second East Coast HVDC Link - Installation of a 2 GW HVDC subsea link between the East Lothian area in South East Scotland, and the South Humber area in North East England | 31/10/2033
SSE Offshore 2 | PRO-001491 | CS-06749 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SSE Offshore 2 Enabling | Extension of the existing 400kV double busbar and installation of two new 400kV feeder bays at Fetteresso 400kV substation, each completes with 2 x 400kV busbar selection switches, 1 x 400kv metering breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Relevant Transmission Licensee and the User will be the User side of the 400kV feeder circuit breaker/isolators at Fetteresso 400kV substation. | 31/10/2031
|  | CS-06750 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2031
|  | CS-06751 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 31/10/2031
|  | CS-06752 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2031
|  | CS-06753 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2031
|  | CS-06754 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2031
|  | CS-06755 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-025d | North East Reinforcement | 31/10/2031
|  | CS-06756 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2031
|  | CS-06757 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2031
|  | CS-06758 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2031
|  | CS-06759 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2031
|  | CS-06760 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2031
|  | CS-06761 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION | SPT-RI-003 | Denny-Strathaven 400kV Reinforcement - Construct a new 400kV double circuit overhead line from Bon-nybridge to Newarthill and re-configure associated sites to establish a fourth north to south dou-ble circuit Supergrid route through the Scottish central belt. One side of the new overhead line will oper-ate at 400kV, the other at 275kV. This reinforcement will establish Denny-Bonnybridge, Bonnybridge-Wishaw, Wishaw-Strathaven No.2 and Wishaw-Torness 400kV circuits and a Denny-Newarthill-Easterhouse 275kV circuit. (SPT-RI-003) | 31/10/2031
SSE Offshore 3 | PRO-001489 | CS-06634 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2033
|  | CS-06635 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2033
|  | CS-06636 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-136 | Blackhillock 400kV Busbar Extension | 31/10/2033
|  | CS-06637 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-145 | 2GW HVDC Link New Deer 2 to England | 31/10/2033
|  | CS-06622 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SSE Offshore 3 Enabling | At New Deer 400kV substation, extend the existing 400kV double busbar and install two new 400kV feeder bays, each complete with 2 x 400kV busbar selection switches, 1 x 400kV circuit breaker, 1 x 400kV line disconnector and associated protection equipment. The ownership boundary between the Onshore Transmission Licensee and the User will be the User side of the 400kV feeder circuit breaker/isolators at New Deer 400kV substation. | 31/10/2033
|  | CS-06623 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-06624 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-144 | Establish a new 400kV substation close to the proposed New Deer 400kV substation and tie in the proposed 400kV circuits from New Deer to Peterhead | 31/10/2033
|  | CS-06625 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2033
|  | CS-06626 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2033
|  | CS-06627 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2033
|  | CS-06628 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-139 | 2 GW HVDC Link New Deer to England | 31/10/2033
|  | CS-06629 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2033
|  | CS-06630 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-025d | North East Reinforcement | 31/10/2033
|  | CS-06631 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-033 | Second 2GW East Coast HVDC Link Peterhead to England | 31/10/2033
|  | CS-06632 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-137 | Blackhillock- New Deer-Peterhead 400kV OHL | 31/10/2033
|  | CS-06633 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation | SHET-RI-138 | New Deer 400kV Busbar Extension | 31/10/2033
SSE Offshore 4 | PRO-002145 | CS-07686 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-1738 | 1. Teviot to Harker Reinforcements - It is proposed to construct at a location in the vicinity of Teviot wind farm site a double busbar 132kV AIS substation to which two 400/132kV 360MVA interbus supergrid transformers will be connected. A double busbar AIS 400kV substation will also be established at the wind farm site to which the interbusing transformers will be connected and two further bays will be provided to connect a double circuit OHL. From the 400kV substation a double circuit OHL of around 43km built on L8 towers and installed with twin Totara conductors will be constructed to Harker 400kV substation. SPT will build the OHL to SPT/NGET boundary and NGET will complete the construction of the scheme from the boundary to Harker. (SPT-RI-1738) | 31/10/2033
|  | CS-07688 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-1796 | Cousland 400kV GIS Substation - A new 400kV double busbar substation, utilising Gas Insulated Switchgear (GIS), will be established south of Cockenzie in the Cousland area in the vicinity of the Torness/Fallago to Smeaton/Wishaw 400kV double circuit (ZS route) and Cockenzie to Eccles 400kV double circuit (ZA Route) crossing. Both the ZA and the ZS routes will be turned into the new substation. | 31/10/2033
|  | CS-07689 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-1873 | Second East Coast HVDC Link - Installation of a 2 GW HVDC subsea link between the East Lothian area in South East Scotland, and the South Humber area in North East England | 31/10/2033
|  | CS-07691 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-2378 | Teviot 400/132kV substation - Construct a new 400/132kV substation to facilitate the new 400kV OHL connections into the site as well as install two new 400/132kV 360MVA transformers and a 132kV double busbar substation for the Teviot windfarm connection. It is proposed to install Gas Insulated Switchgear (GIS) rated at 5000A. (SPT-RI-2378) | 31/10/2033
|  | CS-07680 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SSE Offshore 4 H1 | 1. Installation of 400kV plant and apparatus at Cousland 400kV Substation which will form the connection to the SSE Offshore 4 Transmission Interface Point, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers. 2. Provision of communications, alarms and indications, as described in Appendix OF and Appendix F of the Bilateral Connection agreement | 31/10/2033
|  | CS-07681 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 31/10/2033
|  | CS-07690 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-2079 | Galashiels North – At an appropriate location around 10km south of Dunlaw Extension substation and in the area between the ZA route and P route establish Galashiels North 400kV substation. The substation will be AIS and running in double bus bar arrangement. Achieve connectivity to the 400kV system by turning one side of the ZA route (COCK4-ECCL4 No.2 circuit) to the new substation. Install two 400kV circuit breakers for the turning of the COCK4-ECCL4 No.2 circuit and install a bus coupler. | 31/10/2033
|  | CS-07682 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-126 | East Coast HVDC Link- East Coast HVDC Link Installation of an approximate 200km, 2GW VSC HVDC link between the Torness area (Branxton 400kV Substation) in South East Scotland, and Hawthorn Pit in North East England. Complete associated AC onshore reinforcement works at both terminals. (SPT-RI-126) | 31/10/2033
|  | CS-07684 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | 31/10/2033
|  | CS-07683 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | 31/10/2033
|  | CS-07685 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-267 | Eccles 400kV Shunt Compensation - In order maintain to post-fault voltages within statutory limits, the installation of voltage control in the east of the network is required. As such, dynamic shunt compensation will be installed at Eccles 400kV substation with associated switchgear. | 31/10/2033
|  | CS-07687 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-1791 | Cockenzie to Eccles (ZA route) Uprating. - The project will uprate the 400kV double circuit between Cockenzie 400kV substation and Eccles 400kV substation from twin Totara to triple Totara operating at 90℃. | 31/10/2033
|  | CS-07692 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV Substation | SPT-RI-2417 | Teviot to Gala North Reinforcements - A new 400kV double circuit OHL using L13 towers and triple Araucaria conductor from Teviot 400kV substation to Gala North 400kV substation which is approximately 57km. (SPT-RI-2417) | 31/10/2033
SSE Spittal Energy Park | PRO-003259 | CS-09876 | SSE DE SOLAR HOLDCO LIMITED | Spittal 400kV | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 31/10/2033
|  | CS-09877 | SSE DE SOLAR HOLDCO LIMITED | Spittal 400kV | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2033
|  | CS-09874 | SSE DE SOLAR HOLDCO LIMITED | Spittal 400kV | SHET-RI-140 | 1. Thurso South 275kV Substation Redevelopment - Redevelop the existing Thurso South 275kV substation into a new 275kV double busbar arrangement | 31/10/2033
|  | CS-09871 | SSE DE SOLAR HOLDCO LIMITED | Spittal 400kV | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2033
|  | CS-09873 | SSE DE SOLAR HOLDCO LIMITED | Spittal 400kV | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 31/10/2033
|  | CS-09875 | SSE DE SOLAR HOLDCO LIMITED | Spittal 400kV | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 31/10/2033
|  | CS-09872 | SSE DE SOLAR HOLDCO LIMITED | Spittal 400kV | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90 degrees Celsius to increase the continuous current rating of the circuit | 31/10/2033
|  | CS-09878 | SSE DE SOLAR HOLDCO LIMITED | Spittal 400kV | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2033
Stallingborough PV & BESS Station | PRO-003021 | CS-08177 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 100944-201881 | Development and submission of DCO for: - Grimsby West substation extension - New 400kV OHL Lincolnshire North section - New 400kV Substation Lincolnshire Coastal Node - New 400kV OHL Lincolnshire South section - New 400kV substation near Weston Marsh | 30/10/2034
|  | CS-08179 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 101393-202729 | Extend Operational Tripping Scheme at South Humber Bank 400kV substation | 30/10/2034
|  | CS-08182 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 100455-201020 | 1. Transpose the Cottam 1 circuit with the West Burton 1 circuit at Keadby 400kV substation. 2. Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby – Thorpe Marsh 400 kV circuit | 30/10/2034
|  | CS-08184 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 30/10/2034
|  | CS-08190 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 100450-201015 | Uprate the Cottam - Keadby 1 and 2 circuits to achieve a post fault winter rating of 3400MVA | 30/10/2034
|  | CS-08192 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 30/10/2034
|  | CS-08183 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 0333496-0333496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 30/10/2034
|  | CS-08185 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 101746-203470 | New network need from North Lincolnshire to Hertfordshire (NOA LRN4). | 30/10/2034
|  | CS-08189 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 30/10/2034
|  | CS-08187 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 101593-101593 | Uprate the Cottam- Staythorpe circuit 1, to provide winter post fault rating of 3300MVA This includes the cable section. | 30/10/2034
|  | CS-08180 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 30/10/2034
|  | CS-08186 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 101553-203094 | The existing A408 Cottam – Staythorpe 1 400kV circuit will be turned in and out of new High Marnham 400kV substation to create a new Cottam – High Marnham & High Marnham – Staythorpe 400kV circuits. Circuits to be reconductored to achieve a minimum winter post fault rating of 3300MVA. | 30/10/2034
|  | CS-08194 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 30/10/2034
|  | CS-08191 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 101248-202488 | Reconductor Sundon-Wymondley 1 and 2 400 kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. Add a new bus coupler and three new bays at Wymondley 400kV substation. | 30/10/2034
|  | CS-08188 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 30/10/2034
|  | CS-08176 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 102167-204374 | Infrastructure works for Carbon Free/ Stallingborough 500MW Solar/BESS connection at Grimsby West 400kV busbar extension. This includes 1 x busbar extension and associated P&C, SCS mods and database change. At the time of the offer, it was assumed there would space within NG operational land for additional bay. | 30/10/2034
|  | CS-08195 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 101807-203697 | New 400kV double circuit from Chesterfield – Ratcliffe-on-Soar | 30/10/2034
|  | CS-08193 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 100468-201037 | Uprate the Cowley - East Claydon and Cowley – Leighton Buzzard - Sundon circuits | 30/10/2034
|  | CS-08181 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 30/10/2034
|  | CS-08178 | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation | 100944-201880 | Modifications to Grimsby West substation for the new Lincolnshire Green 400kV OHL | 30/10/2034
St Asaph SSE | PRO-003816 | CS-08919 | SSE DE SOLAR HOLDCO LIMITED | Bodelwyddan 400kV Substation | 101986-204112 | Infrastructurew works to connect customer via a generator bay at BODE4 substation. This included the creation of a new substation sectiopn including section break (main and reserve) bus couple, a new feeder bay and the transpotition of a cicuit onto the new feeder bay. The circuit will be determined as part of the scheme to turn BODE4 a double turn in substation | 01/11/2037
|  | CS-08918 | SSE DE SOLAR HOLDCO LIMITED | Bodelwyddan 400kV Substation | 102523-205123 | At Bodelwyddan 400 kV substation: 1. Extend the new busbar sections to make accommodate the Users first Bay | 01/11/2037
|  | CS-08920 | SSE DE SOLAR HOLDCO LIMITED | Bodelwyddan 400kV Substation | 101267-202510 | Scope- Circuits between Wylfa and Pentir will need a new or an existing modificed intertrip scheme to monitor all circuits to trip generation for N-3 events. In addition,all circuits between Pentir-Legacy via TRAWS and CONHQ to monitor all circuits as a result of new connections in the area | 01/11/2037
Staythorpe (BESS and PV) | PRO-001615 | CS-04520 | SSE STAYTHORPE POWER LIMITED | Staythorpe 400kV Substation | 101368-202688 | Extend the Busbar at Staythorpe 400kV to make provision for the User to connect their generator bay | 29/05/2026
|  | CS-04521 | SSE STAYTHORPE POWER LIMITED | Staythorpe 400kV Substation | 101265-202507 | Reconductor Grendon - Marston Vale - Sundon 400kV circuits 1 and 2 with 2 x 620mm2 conductors to achieve a summer pre fault rating of 2490 MVA | 29/05/2026
|  | CS-04522 | SSE STAYTHORPE POWER LIMITED | Staythorpe 400kV Substation | 101245-202485 | Reconductoring of the Eaton Socon -Wymondley 2 circuit | 29/05/2026
|  | CS-08902 | SSE STAYTHORPE POWER LIMITED | Staythorpe 400kV Substation | 101912-203908 | Extend the Busbar at Staythorpe 400kV to make provision for the User to connect their generator bay | 29/05/2026
St Dennis Hendra | PRO-001133 | CS-04750 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 31/10/2024
|  | CS-04751 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 31/10/2024
|  | CS-04752 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 31/10/2024
|  | CS-04753 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 31/10/2024
|  | CS-04754 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 31/10/2024
|  | CS-04755 | SAMBAR POWER LIMITED | Indian Queens 400kV Substation | 100748-201539 | Extend substation to facilitate the connection. | 31/10/2024
Stemster Wind Farm | PRO-000926 | CS-06226 | RWE RENEWABLES UK SWINDON LIMITED | Mybster 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 30/09/2026
|  | CS-06227 | RWE RENEWABLES UK SWINDON LIMITED | Mybster 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 30/09/2026
|  | CS-06228 | RWE RENEWABLES UK SWINDON LIMITED | Mybster 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 30/09/2026
Stirches Solar PV | PRO-001892 | CS-07323 | SP Distribution plc | Hawick GSP | SPT-RI-288 Hawick to Galashiels 132kV Reconfiguration | Hawick 132/33kV substation is currently supplied via two 132kV circuits from Gretna 400/132kV substation, with a 132kV circuit to Galashiels normally open at CB 205. With the proposed connection of Faw Side wind farm (250MW) it is proposed to reconfigure Hawick 132kV substation such that Hawick can be supplied from Galashiels and establish the Hawick / Galashiels 132kV circuit No.1 and No.2. Works at Galashiels will be required to terminate the double circuit from Hawick post reconfiguration. At Hawick, it is also proposed to install two new 132kV circuit breakers and a fourth 132kV circuit at Hawick with Poplar conductor:. The existing circuit breakers at Galashiels are of 600A and 800A. It is also proposed to replace the 600A circuit breakers 120 and 620 with a standard 2000A circuit breaker. | 31/12/2026
|  | CS-07324 | SP Distribution plc | Hawick GSP | NGET - 101268-202511 | Rebuild of Harker substation and rationalise to leave a new 400kV and 132kV substations with six 400/132kV 240MVA SGTs. The preferred option is to rebuild on a greenfield plot of land adjacent to Harker. (NGET - 101268-202511) | 31/12/2026
|  | CS-07325 | SP Distribution plc | Hawick GSP | NGET 101268-202520 | Chapelcross – Harker 132kV circuit uprating - Hark – Chap T Route Uprating | 31/12/2026
Stoke Bardolph 400 | PRO-002191 | CS-08068 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 100478-201049 | Reconductor the Drakelow-Willington East 400kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA | 31/10/2030
|  | CS-08063 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 101884-203860 | Reconductor the Enderby legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490MVA | 31/10/2030
|  | CS-08067 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 032021-032021 | Reconductor MILLBROOK-SUNDON 4-1 (MILB4-SUND4-1) & MILLBROOK-SUNDON 4-2 (MILB4-SUND4-2) 400kV circuit to achieve more than 1605MVA pre-fault summer rating. | 31/10/2030
|  | CS-08065 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 101889-203868 | East Claydon legs of ECLA4-ENDE4-PAFB4 cctReconductor the East Claydon legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 2490MVA | 31/10/2030
|  | CS-08062 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x780mm2 conductor to achieve a post-fault winter rating of 3390MVA. | 31/10/2030
|  | CS-08060 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 101880-203857 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4-WILE4-2) to summer pre-fault rating 2490MVA | 31/10/2030
|  | CS-08066 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 31/10/2030
|  | CS-08064 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 101329-202649 | Uprate Enderby – Ratcliffe 400kV circuit 2 to achieve a pre-fault summer rating of 2790MVA | 31/10/2030
|  | CS-08061 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 100590-201212 | Reconductor the exisiting 2x500mm2 conductor on the Ratcliffe –StokeBardolph 400kV circuit with 2x780mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3390MVA. | 31/10/2030
|  | CS-08059 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 102139-204343 | Extension of 400 kV main and reserve busbar of Stoke Bardolph 400 kV substation to accommodate the users bays | 31/10/2030
STOR Field 9 BESS | PRO-002528 | CS-09313 | EKU ENERGY FAUNE PROJECTS (UK) LIMITED | Inverkeithing GSP | SPT-RI-2905 | 0 | 30/07/2029
Stornoway Wind Farm | PRO-000346 | CS-06070 | STORNOWAY WIND FARM LIMITED | Stornoway 132/33kV Substation | SHET-RI-007b | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 31/10/2030
|  | CS-06071 | STORNOWAY WIND FARM LIMITED | Stornoway 132/33kV Substation | SHET-RI-042 | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHET-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly. | 31/10/2030
|  | CS-06072 | STORNOWAY WIND FARM LIMITED | Stornoway 132/33kV Substation | Stornoway Item 1 | The Relevant Transmission Licensee will construct a 5km single circuit 132kV wood pole overhead line from a fully equipped 132kV feeder bay at Arnish 132kV substation to the windfarm site. The new 132kV line will terminate on the Relevant Transmission’s 132kV line isolator at the User’s 132/33kV windfarm substation. | 31/10/2030
Stracathro BESS | PRO-002392 | CS-08408 | OPDE UK LIMITED | Stracathro BESS 275kV Substation | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 30/06/2032
|  | CS-08409 | OPDE UK LIMITED | Stracathro BESS 275kV Substation | SHET-RI-205 | New Brechin 275kV Substation- New 275kV double busbar substation in the Brechin area. The 275kV XT1/XT2 circuits between Kintore and Tealing will turn in/out of this new 275kV substation. (SHET-RI-205) | 30/06/2032
Stranoch Wind Farm | PRO-000127 | CS-06073 | EDF ENERGY RENEWABLES LIMITED | Stranoch Wind 132/33KV Substation | SPT-RI-205 | Installation of approximately 1km of 132kV overhead line between Chirmorie Wind Farm substation and the tee point on the Mark Hill to Stranoch wind farm overhead line, a 132kV isolator at Chirmorie wind farm substation and 132kV substation at Mark Hill and a 132kV switch bay will be installed. From this a 132kV circuit consisting 0.5km of underground cable and 13.5 of 132kV overhead line 300mm UPAS conductor) will be installed to the overhead line tee point connecting the circuits to Chirmorie and Stranoch wind farms. | 29/08/2025
|  | CS-06074 | EDF ENERGY RENEWABLES LIMITED | Stranoch Wind 132/33KV Substation | SPT-RI-206 | At Mark Hill substation a 275kV switchbay will be installed to control a 275/132kV 240MVA transformer (SGT3). This will connect to a 132kV busbar (B Board) provided for the connection of renewable generation. | 29/08/2025
|  | CS-06075 | EDF ENERGY RENEWABLES LIMITED | Stranoch Wind 132/33KV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 29/08/2025
|  | CS-06076 | EDF ENERGY RENEWABLES LIMITED | Stranoch Wind 132/33KV Substation | Stranoch Part 1 Enabling | 1. Installation of approximately 7.5km of 132kV overhead line from the Stranoch Wind Farm site to the Chirmorie Wind Farm tee point. 2. Installation of a 132kV line isolator at Stranoch Wind Farm substation. | 29/08/2025
|  | CS-06077 | EDF ENERGY RENEWABLES LIMITED | Stranoch Wind 132/33KV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 29/08/2025
Strathaven South Wind Farm | PRO-000815 | CS-06078 | SP Distribution plc | Linmill GSP | SPT-RI-178 | Linnmill Grid T1(2) Overload Protection Scheme | 30/10/2020
|  | CS-04146 | SP Distribution plc | Linmill GSP | SPT-RI-180 | Coalburn SGTx Overload Protection Scheme: An overload protection scheme will be installed at Coalburn 400/132kV substation such that if SGT1 or SGT2 is overloaded, a trip signal will be issued to SPD at Linnmill GSP, and/or to SPT generation connected directly to Coalburn 132kV substation, to disconnect the appropriate generators to remove the overload. Following completion of Coalburn SGT3 (SPT-RI-144), this transformer will be added to the overload scheme proposed in this TORI (SPT-RI-180). | 30/10/2020
Strathaven West | PRO-003432 | CS-09654 | Clean Earth Energy Limited | Strathaven GSP | SPT-RI-2520 | Strathaven 275kV Gas Circuit Breaker Replacement | 30/10/2028
Strath Tirry (keep) | PRO-001363 | CS-06433 | Strath Tirry Wind Energy 2021 Ltd | Lairg GSP | SHET-RI-052 - Lairg – Loch Buidhe 132kV Reinforcement | Establish a new 132kV double busbar at Lairg (Dalchork substation) and construct approximately 17km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. | 31/10/2025
|  | CS-06434 | Strath Tirry Wind Energy 2021 Ltd | Lairg GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2025
Strathy South Wind | PRO-000183 | CS-06079 | SSE GENERATION LIMITED | Strathy South 132/33kV Substation | Strathy South | The provision of two 132kV transformer circuit breakers and two 132kV disconnectors on the 132kV side of both 132/33kV transformers at the User’s connection site. The disconnectors will also be coupled to approximately 4.5 km of new 293MVA/132kV single cable per phase underground cable constructed from the site of Strathy South 132/33kV Substation which will be coupled to a 17 km of new 293MVA 132kV single circuit Overhead Line constructed between a sealing end compound in the vicinity of Strathy Wood wind farm substation and Connagill 275/132kV substation (NYG2). The 132kV overhead line will be connected to Connagill 132kV substation via 132kV line disconnector, 132kV feeder circuit breaker and a 132kV busbar disconnector. | 01/12/2025
|  | CS-06080 | SSE GENERATION LIMITED | Strathy South 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 01/12/2025
|  | CS-06081 | SSE GENERATION LIMITED | Strathy South 132/33kV Substation | SHET-RI-106b | Connagil 2nd SGT – At Connagil substation, install a 2nd 275/132kV 120/240MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit. (SHET-RI-106b) | 01/12/2025
|  | CS-06082 | SSE GENERATION LIMITED | Strathy South 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 01/12/2025
|  | CS-06083 | SSE GENERATION LIMITED | Strathy South 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 01/12/2025
Strathy Wood | PRO-000154 | CS-06087 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | SHET-RI-106b | Connagil 2nd SGT – At Connagil substation, install a 2nd 275/132kV 120/240MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit. (SHET-RI-106b) | 01/05/2025
|  | CS-06088 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 01/05/2025
|  | CS-06089 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | Strathy Wood Part 1 | 1. Construct a 132kV wood pole trident line over a distance of 5km between Strathy North 132/33kV substation and the new 132/33kV substation at Strathy Wood. The wood pole line will be coupled off one of the incoming 132kV line circuits at Strathy North 132kV substation, and terminated on a new 132kV transformer disconnector switch at Strathy Wood 132/33kV substation. 2. Provision and installation of a 132kV transformer circuit switcher (115) at Strathy Wood 132/33kV substation, installed on the 132kV side of the 132/33kV transformer unit. | 01/05/2025
|  | CS-06090 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 01/05/2025
|  | CS-06091 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | SHET-RI-032a | Dounreay Spittal 275kV and 132kV OHL Reinforcement – A new 275kV OHL and substation works between Dounreay, Thurso and Spittal Substations. (SHET-RI-032a). | 01/05/2025
|  | CS-06400 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 01/05/2025
|  | CS-06084 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 01/05/2025
|  | CS-06085 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 01/05/2025
|  | CS-06086 | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | SHET-RI-035 | Loch Buidhe 275/132kV Substation – Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kV and Shin-Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275/132kV SGTs. (SHET-RI-035). | 01/05/2025
Sulgrave Solar PV | PRO-001572 | CS-06952 | EDF ENERGY RENEWABLES LIMITED | East Claydon GSP (SEPD) | 100893-201795 | 1. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT1. 2. Commissioning of new transformer with higher impedance at East Claydon 400kV Substation to resolve the fault level issue at the tertiary winding of SGT2. | 30/10/2026
Summerston PV 50MW | PRO-003199 | CS-09821 | Bluestone Energy Ltd | Killermont 132/33kV | SPT-RI-3314 | Windyhill 132kV B Board Version 2 | 30/06/2031
|  | CS-09818 | Bluestone Energy Ltd | Killermont 132/33kV | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 30/06/2031
|  | CS-09819 | Bluestone Energy Ltd | Killermont 132/33kV | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 30/06/2031
|  | CS-09820 | Bluestone Energy Ltd | Killermont 132/33kV | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 30/06/2031
Sundhope Wind Farm | PRO-002767 | CS-08972 | Sundhope Energy Limited | Sundhope 132kV Substation | SPT-RI-2418 | Under this TORI it is proposed to establish a second 132kV board at Teviot substation. This will require the installation of two 400kV GIS bays as well as two 400/132kV 240MVA transformers and their associated 132kV double busbar bays as well as a 132kV bus coupler. All 132kV switchgear is proposed to be Air Insulated Switchgear (AIS). | 30/05/2033
|  | CS-08971 | Sundhope Energy Limited | Sundhope 132kV Substation | SPT-RI-2378 | Teviot 400/132kV substation - Construct a new 400/132kV substation to facilitate the new 400kV OHL connections into the site as well as install two new 400/132kV 360MVA transformers and a 132kV double busbar substation for the Teviot windfarm connection. It is proposed to install Gas Insulated Switchgear (GIS) rated at 5000A. (SPT-RI-2378) | 30/05/2033
|  | CS-08970 | Sundhope Energy Limited | Sundhope 132kV Substation | SPT-RI-1738 | 1. Teviot to Harker Reinforcements - It is proposed to construct at a location in the vicinity of Teviot wind farm site a double busbar 132kV AIS substation to which two 400/132kV 360MVA interbus supergrid transformers will be connected. A double busbar AIS 400kV substation will also be established at the wind farm site to which the interbusing transformers will be connected and two further bays will be provided to connect a double circuit OHL. From the 400kV substation a double circuit OHL of around 43km built on L8 towers and installed with twin Totara conductors will be constructed to Harker 400kV substation. SPT will build the OHL to SPT/NGET boundary and NGET will complete the construction of the scheme from the boundary to Harker. (SPT-RI-1738) | 30/05/2033
Sundon | PRO-000473 | CS-04269 | SUNDON GREEN LIMITED | Sundon GSP | 100902-201813 | Extend Main busbar 1 and Reserve busbar 1 at Sundon 400kV substation Installation of a new 150MVA rated 400/33kV SGT including HV and LV bays Establish a new single busbar 33kV substation at Sundon to be connected via the new 400/33kV SGT | 10/11/2023
| PRO-001132 | CS-06092 | SUNDON BATTERY STORAGE LIMITED | Sundon 400kV Substation | 100306-200734 | 1. Extend Main busbar 1 and Reserve busbar 1 at Sundon 400kV subtation. 2. Installation of a new 150MVA rated 400/33kV SGT including HV and LV bays 3. Establish a new single busbar 33kV substation at Sundon to be connected via the new 400/33kV SGT | 01/05/2024
Sundon BESS | PRO-002039 | CS-09260 | CSE30 LIMITED | Sundon 400kV Substation | 101926-203937 | 1. Extend Sundon 400kV Substation 2. Extend Main 1 and Reserve 1 busbars for the provision of one User Bay | 31/10/2031
|  | CS-09261 | CSE30 LIMITED | Sundon 400kV Substation | 101927-203938 | At Sundon 400kV: Replace circuit breakers X130, X510 and X710. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 31/10/2031
Sundon Pivoted Power | PRO-001123 | CS-05291 | PIVOTED POWER LLP | Sundon 400kV Substation | 100604-201146 | Extend Main busbar 1 and Reserve busbar 1 at Sundon 400kV substation Installation of a new 150MVA rated 400/33kV SGT including HV and LV bays Establish a new single busbar 33kV substation at Sundon to be connected via the new 400/33kV SGT Installation of an earthing transformer connecting onto the 33kV busbar | 31/10/2023
Swaffham PV & BESS | PRO-003754 | CS-08817 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 30/10/2033
|  | CS-08795 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 102380-204827 | Installation of a new AIS double busbar 400kV substation (New Swaffham) between Walpole 400kV and Necton 400kV with associated two feeder bays, 1 Coupler Bay, 1 section bay and users generator bay. Provide a single turn in connection of the new substation to the existing 400kV OHL circuit 2 between Walpole 400kV and Necton 400kV. | 30/10/2033
|  | CS-08798 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100709-201477 | Construct a new 400 kV double circuit between Norwich Main 400 kV substation and Bramford 400kV substation with a summer post-fault capacity of 3000 MVA on each circuit. | 30/10/2033
|  | CS-08801 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100708-201475 | Post completion of BTNO works reconductor Bramford-Pelham-2 400 kV circuits with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA | 30/10/2033
|  | CS-08799 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100881-201773 | Install two 225 Mvar MSCs at Norwich Main 400 kV substation. Extension of Norwich Main 400 kV substation to accommodate the new MSCs. | 30/10/2033
|  | CS-08822 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 30/10/2033
|  | CS-08803 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 30/10/2033
|  | CS-08807 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 033458-033458 | Reconductor the existing circuit between Bramford and Rayleigh Main 400kV with 3 x 700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 30/10/2033
|  | CS-08816 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 101248-202488 | The circuit running from Pelham to Wymondley (PELH4 – WYMO4-1) will also be reconductored with 3 x 700mm2 conductor rating 2790MVA, 75˚C for pre-fault summer rating The circuit running from Pelham to Wymondley (PELH4 – WYMO4-1_a) will also be reconductored with 3 x 700mm2 conductor rating 3160MVA, 90˚C for pre-fault summer rating The circuit running from Sundon to Wymondley (SUND4 – WYMO4-1) will also be reconductored with 3 x 700mm2 conductor rating 3160MVA, 90˚C for pre-fault summer rating | 30/10/2033
|  | CS-08796 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100381-200905 | 1. Extension of the Norwich Main 400kV AIS Substation at Main Busbar (M2) and Reserve Busbar (R2) to accommodate an OFTO bay. 2. Extension of the existing East Anglia operational intertripping scheme to include the connection. | 30/10/2033
|  | CS-08797 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100709-201476 | Extension of the existing Norwich Main 400 kV substation by 2 bays to accommodate a new double circuit Bramford - Norwich Main | 30/10/2033
|  | CS-08825 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100944-201883 | Build a new 400 kV double circuit between Mablethorpe and Weston Marsh Substations | 30/10/2033
|  | CS-08809 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 021742-021742 | 1) The existing double circuits running from Pelham to Rye House (PELH4- RYEH4B-1) and from Rye House to Rye House (RYEG4 – RYEH4B-1) will also be reconductored with Triple Araucaria 3 x 700mm2 conductor rating 3160MVA, 90˚C for pre fault summer rating. 2) The circuit running from Rye House to Waltham Cross (RYEH4- WALX4A-1) will also be reconductored with 2 x 700mm2 conductor rating 2800MVA, 160˚C for pre fault summer rating. 3) The circuit running from (Brimsdown to Hackney (BRIM4C - HACK4-1) and Brimsdown to Waltham Cross (BRIM4D -WALX4-2) will also be reconductored with 2 x 700mm2 conductor rating 1860MVA, 75˚C for pre fault summer rating. | 30/10/2033
|  | CS-08812 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100951-201898 | Uprate West Burton - High Marnham (A403) cable section to provide a postfault winter rating of 3100MVA | 30/10/2033
|  | CS-08814 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100952-201899 | Reconductor EAST CLAYDON-LEIGHTON BUZZARD (ECLA4- LEIB4B-1) 400kV circuit to achieve a minimum rating of 2450MVA summer pre-fault rating | 30/10/2033
|  | CS-08821 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 101975-204100 | 1. At Kings Lynn 400kV: Ensure circuit break X130 to be rated to 63kA with tested X/R ration of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2033
|  | CS-08820 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 101723-203432 | At Yaxley 400kV: Replace circuit breaker X130. Breaker to be rated to 63kA with tested X/R ration of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2033
|  | CS-08802 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 033750-033750 | Uprate the circuit bay Busbar, CT and Circuit Breaker attached to existing A654 circuit (BRFO-PELH) and uprate the circuit bay Busbar, CT, Circuit Breaker, disconnector and main protection system on the newly formed second Bramford – Pelham circuit (currently part of A646 BRFO-BRAI circuit) to achieve a post fault winter rating of 3820MVA | 30/10/2033
|  | CS-08804 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 30/10/2033
|  | CS-08810 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 30/10/2033
|  | CS-08800 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 033461-033461 | Post completion of BTNO works reconductor Bramford-Pelham 1 400kV circuits with 3 x 700mm2 AAAC conductors to achieve a postfault winter rating of 3820 MVA | 30/10/2033
|  | CS-08815 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 101247-202487 | Reconductor LEIGHTON BUZZARD-SUNDON4-1 (LEIB4A-SUND4-1) & LEIGHTON BUZZARD-SUNDON4-2 (LEIB4B-SUND4-2) 400kV circuit to achieve a minimum rating of 2450MVA summer pre-fault rating. | 30/10/2033
|  | CS-08824 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 102231-204467 | At Weston Marsh 400 kV substation install a 2750 MVA 16 Ohm series reactor between M1/R1 and M2/R2 busbars | 30/10/2033
|  | CS-08808 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 020340-020340 | Reconductor the re-configured Bramford – Norwich Main (4YM route) with 3 x 700 mm2 AAAC conductor operating at 75oC. | 30/10/2033
|  | CS-08811 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA | 30/10/2033
|  | CS-08806 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 021847-021847 | Construct a new 400 kV double circuit between the Bamford 400 kV substation and the Twinstead Tee point strung with 3x700mm2 AAAC conductor at 75°C. At Twinstead Tee rearrange the overhead line circuit to form the Bramford-Pelham double circuit and Bramford-Braintree-Bulls Lodge and Bramford-Braintree-Rayleigh Main 400 kV double circuit (BTNO Works). | 30/10/2033
|  | CS-08813 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100590-201212 | Reconductor the existing 2x500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit to achieve more than 1800MVA summer prefault rating. | 30/10/2033
|  | CS-08823 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 30/10/2033
|  | CS-08819 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 101964-204086 | 6. At Walpole 400kV: Replace circuit breakers X130, X110, X305, X310, X510. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 30/10/2033
|  | CS-08826 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 30/10/2033
|  | CS-08818 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 101729-203439 | At Necton 400kV: Replace circuit breakers X130, X230, X160, X170, X330, X370, X120. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. 2029 | 30/10/2033
|  | CS-08805 | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation | 101883-203859 | Uprating of the Coryton South – Rayleigh Main (A68A) 400kV circuit cables to achieve 3002MVA pre-fault summer rating | 30/10/2033
Swansea Greener Grid Park - Connection 1 | PRO-001120 | CS-08926 | Swansea Grid Solutions Limited | Swansea North 400kV Substation | 100774-201567 | Installation of a new disconnector at a tee point on the outgoing Swansea North – Rhigos 400kV circuit | 31/08/2024
|  | CS-08927 | Swansea Grid Solutions Limited | Swansea North 400kV Substation | 101614-203242 | Extension of South Wales Operational Tripping Scheme | 31/08/2024
|  | CS-08928 | Swansea Grid Solutions Limited | Swansea North 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to achieve 1990MVA pre-fault summer rating | 31/08/2024
|  | CS-08929 | Swansea Grid Solutions Limited | Swansea North 400kV Substation | 020903-020903 | Uprating/replacement of the Cowley – Walham and Cowley - Minety 400kV circuits cables sections to achieve 1193MVA or greater prefault Summer rating. | 31/08/2024
Swansea North | PRO-001119 | CS-05221 | PIVOTED POWER LLP | Swansea North 400kV Substation | NGET-Rl-100279-200696(lnfra) | 1. Install earthing transformer on 13kV Tertiary connection 2. Install 13kV disconnector connecting tertiary to connection assets for Users connection | 31/10/2026
Swansea North Green Energy Centre | PRO-001794 | CS-07277 | INNOVA RENEWABLES LIMITED | Swansea North 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Warwick conductor to achieve a Pre-fault Summer rating of 1990MVA | 30/10/2028
|  | CS-07303 | INNOVA RENEWABLES LIMITED | Swansea North 400kV Substation | 101614-203241 | 0 | 30/10/2028
|  | CS-07304 | INNOVA RENEWABLES LIMITED | Swansea North 400kV Substation | 101614-203242 | 0 | 30/10/2028
|  | CS-07305 | INNOVA RENEWABLES LIMITED | Swansea North 400kV Substation | 020903-020903 | Uprating/replacement of the Cowley – Walham and Cowley - Minety 400kV circuits cables sections to achieve 1193MVA or greater prefault Summer rating. | 30/10/2028
Tacher Wind | PRO-002769 | CS-09412 | Clean Earth Energy Limited | Mybster 132/33kV Substation | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/08/2025
|  | CS-09415 | Clean Earth Energy Limited | Mybster 132/33kV Substation | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/08/2025
|  | CS-09411 | Clean Earth Energy Limited | Mybster 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/08/2025
|  | CS-09413 | Clean Earth Energy Limited | Mybster 132/33kV Substation | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 31/08/2025
|  | CS-09414 | Clean Earth Energy Limited | Mybster 132/33kV Substation | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 31/08/2025
|  | CS-09409 | Clean Earth Energy Limited | Mybster 132/33kV Substation | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90 degrees Celsius to increase the continuous current rating of the circuit | 31/08/2025
|  | CS-09410 | Clean Earth Energy Limited | Mybster 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 31/08/2025
|  | CS-09416 | Clean Earth Energy Limited | Mybster 132/33kV Substation | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/08/2025
Tacher Wind (DNO) | PRO-000997 | CS-06249 | Scottish Hydro Electric Power Distribution Plc | Mybster 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/08/2025
|  | CS-06250 | Scottish Hydro Electric Power Distribution Plc | Mybster 132/33kV Substation | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 31/08/2025
|  | CS-06251 | Scottish Hydro Electric Power Distribution Plc | Mybster 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/08/2025
Tangy IV WF | PRO-001408 | CS-06418 | SSE RENEWABLES SERVICES (UK) LIMITED | Tangy IV 132KV Substation | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 31/10/2026
|  | CS-06419 | SSE RENEWABLES SERVICES (UK) LIMITED | Tangy IV 132KV Substation | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 31/10/2026
|  | CS-06420 | SSE RENEWABLES SERVICES (UK) LIMITED | Tangy IV 132KV Substation | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 31/10/2026
|  | CS-06421 | SSE RENEWABLES SERVICES (UK) LIMITED | Tangy IV 132KV Substation | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 31/10/2026
|  | CS-06422 | SSE RENEWABLES SERVICES (UK) LIMITED | Tangy IV 132KV Substation | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 31/10/2026
|  | CS-06415 | SSE RENEWABLES SERVICES (UK) LIMITED | Tangy IV 132KV Substation | Tangy IV Enabling Works | Construction of approximately 21.5 kilometres of 132kV OHL line (17.5km will be wood pole trident line the other 4km will be NEST structures) connecting between Crossaig Substation and Carradale GSP overhead line and the Tangy IV substation. This will include all associated Circuit Breakers and disconnectors required for the T point from the Crossaig-Carradale line. A 132kV circuit breaker and a 132kV disconnector will also be installed at Tangy IV 132/33KV substation | 31/10/2026
|  | CS-06416 | SSE RENEWABLES SERVICES (UK) LIMITED | Tangy IV 132KV Substation | SHET-RI-086 | Craig Murrail Switching Station - It is proposed that a new 132kV switching station will be constructed near the Port Ann tee point (Craig Murrail) cutting into the Crossaig-Inveraray 132kV double circuit. Disconnect Port Ann from tee points on the 132kV OHL and connect Port Ann GSP directly onto the new 132kV double busbars. | 31/10/2026
|  | CS-06417 | SSE RENEWABLES SERVICES (UK) LIMITED | Tangy IV 132KV Substation | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 31/10/2026
Tarbuckle Hill Wind Farm | PRO-003045 | CS-09595 | ENERGIEKONTOR UK LTD | Cairnford GSP | SHET-RI-232 | Cairnford GSP 275kV tee | 31/10/2031
Tarenni | PRO-001641 | CS-04604 | TARENNI ENERGY PARK LIMITED | Rhigos 400kV Substation | 101506-202970 | 1. Eastern side GIS extension of Rhigos 400KV substation double busbars including AIS-GIS conversion module for provision of the User’s generator bay. [NOTE 1] 2. Replace AIS bus coupler bay with new GIS bus coupler to facilitate space for new generator bays within existing substation compound (avoiding development of contaminated land) [NOTE 1] 3. Installation of a new Commercial/Category 2 Operational Tripping Scheme at Rhigos 400kV substation. | 01/10/2028
|  | CS-04605 | TARENNI ENERGY PARK LIMITED | Rhigos 400kV Substation | 100424-200970 | Reconductor the Bramley – Melksham 400kV circuits 1 and 2 to achieve a pre-fault summer rating of 1990MVA | 01/10/2028
|  | CS-04606 | TARENNI ENERGY PARK LIMITED | Rhigos 400kV Substation | 033793-202898 | Replacement of the Walham - Cowley circuit 2.092km cable section to increase summer pre-fault rating from existing 877MVA to future requirement of at least 1341MVA | 01/10/2028
|  | CS-04607 | TARENNI ENERGY PARK LIMITED | Rhigos 400kV Substation | 033769-033769 | Reconductor the Exeter – Hinkley Point – Taunton 400kV circuits to achieve a 3100MVA pre-fault summer rating | 01/10/2028
Tarland Battery Storage System | PRO-000922 | CS-04306 | Tarland Limited | Tarland GSP | Tarland BSS H1 Works | 1. At Tarland 132/33kV GSP substation, remove the existing 30MVA transformers and install two new 90MVA 132/33kV transformers and ancillary items. The transformers will be installed within the existing substation and cabled to the existing 33kV switchboard. | 31/10/2026
|  | CS-04307 | Tarland Limited | Tarland GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 31/10/2026
Taunton | PRO-001073 | CS-05292 | PIVOTED POWER LLP | Taunton 400kV Substation | NGET-RI-30752 | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. | 31/10/2029
|  | CS-05293 | PIVOTED POWER LLP | Taunton 400kV Substation | NGET-RI-31671-2 | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. | 31/10/2029
|  | CS-05294 | PIVOTED POWER LLP | Taunton 400kV Substation | NGETRI-33539 | Hot wiring of the Hinkley Point – Melksham 1 and 2 circuits to increase their thermal rating | 31/10/2029
|  | CS-05295 | PIVOTED POWER LLP | Taunton 400kV Substation | NGET-RI-31885 | Re-conductor the Bramley – Fleet OHL circuits to increase capacity | 31/10/2029
|  | CS-05220 | PIVOTED POWER LLP | Taunton 400kV Substation | NGET-RI-100279-200693(Infra) | 1. Install earthing transformer on 13kV tertiary connection 2. Install 13kV disconnector and associated earthing switches connecting tertiary to connection assets for Users connection 3. Works to allow for the Category 2 Operational Tripping Scheme as described in Appendix F3. | 31/10/2029
Tealing BESS (100MW) | PRO-002436 | CS-08083 | GPC 1039 Ltd | Tealing 132kV Substation | Tealing BESS Line disconnector | A 132kV line disconnector will be installed at the User’s substation. | 31/10/2028
|  | CS-08085 | GPC 1039 Ltd | Tealing 132kV Substation | Tealing BESS - Fibre Optic Comms | Additionally, fibre optic comms will be installed between Tealing 132kV substation and the User’s substation. | 31/10/2028
|  | CS-08081 | GPC 1039 Ltd | Tealing 132kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2028
|  | CS-08082 | GPC 1039 Ltd | Tealing 132kV Substation | Tealing BESS - Compound extension and new switch bay | Extension of the Tealing substation compound to allow the Tealing 132kV busbar to be extended to install a new 132kV double busbar switch bay | 31/10/2028
|  | CS-08080 | GPC 1039 Ltd | Tealing 132kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2028
|  | CS-08084 | GPC 1039 Ltd | Tealing 132kV Substation | Tealing BESS - Underground Cable | Approximately 2.7km of 132kV underground cable will also be required as part of this connection | 31/10/2028
Tealing Energy Park | PRO-003084 | CS-09159 | Banks Renewables Limited | Tealing 400kV Substation | SHET-RI-009 | East Coast Onshore 275kV Reinforcement - Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2 | 31/10/2033
|  | CS-09162 | Banks Renewables Limited | Tealing 400kV Substation | SPT-RI-200 | East Coast Phase 2 400kV Reinforcement – Reconductoring and reprofiling of XL route to move from 275kV to 400kV operation between Kincardine and the SP Transmission/ SHE Transmission border; and installation of 2 x 400/275kV 1000MVA auto-transformers at Kincardine | 31/10/2033
|  | CS-09161 | Banks Renewables Limited | Tealing 400kV Substation | SHET-RI-093 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade | 31/10/2033
|  | CS-09160 | Banks Renewables Limited | Tealing 400kV Substation | SHET-RI-004 | Reconductor the Beauly - Foyers - Blackhillock 275kV double circuit line with larger capacity conductor between Beauly - Knocknagael and between Knocknagael - Blackhillock and Blackhillock - Kintore (XH1/XH2). The substation at Knocknagael is adjacent to the existing Foyers line tee point. | 31/10/2033
Tealing Solar & Storage | PRO-001501 | CS-04301 | ECODEV GROUP LTD | Tealing IDNO 132/33kV GSP | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 31/10/2026
|  | CS-04302 | ECODEV GROUP LTD | Tealing IDNO 132/33kV GSP | SHET-RI-166 | Tealing – Arbroath 132kV Line Works - Overhead line works to bring the 132kV circuit to ground, including any required modifications. Design and installation of one 132kV circuit breaker with two 132kV disconnectors and associated protection and control equipment. | 31/10/2026
|  | CS-04303 | ECODEV GROUP LTD | Tealing IDNO 132/33kV GSP | Tealing IDNO H1 Works | - Design and installation of a joint Relevant Transmission Licensee and Host Distribution Network Operator protection system covering the modification of the existing circuit protection to incorporate the new substation - Construction of a substation building large enough to accommodate all the required apparatus and associated metering, protection, batteries etc. - Design and installation of a 132kV transformer circuit breaker bay, including two 132kV disconnector switches, as well as all associated protection and control equipment to be housed in a space provided by the Contestable works substation. | 31/10/2026
Teindland Wind Farm | PRO-001821 | CS-09832 | TEINDLAND WIND FARM LIMITED | Blackhillock substation | SHET-RI-079 (a & b) | Blackhillock Additional SGTs- Reinforce the transmission network at Blackhillock substation by installing two additional new 275/132kV Supergrid Transformers. The transformers are to be rated at 360MVA. The SGTs will be connected to the existing 275kV AIS double busbar and 132kV GIS double busbar at Blackhillock. Two new 275kV AIS transformer circuit breaker bays and two new GIS transformer circuit breaker bays will also be required (SHET-RI-079 (a & b)). | 28/09/2029
|  | CS-06883 | TEINDLAND WIND FARM LIMITED | Blackhillock substation | Teindland Item 1 | Installation of a new 132kV line disconnector at the Wind Farm substation, connecting a new approximately 15km 132kV circuit comprised of mostly wood pole overhead line but with a short section of 132kV underground cable for entry into Blackhillock substation. This new circuit will be connected to a new 132kV indoor GIS double busbar circuit breaker bay located at Blackhillock substation. The 132kV busbar protection scheme at Blackhillock will also require to be updated | 28/09/2029
|  | CS-06884 | TEINDLAND WIND FARM LIMITED | Blackhillock substation | SHET-RI-079 | Additional 275/132kV SGT’s at Blackhillock - Reinforce the transmission network at Blackhillock substation by installing two additional new 275/132kV Supergrid Transformers. The transformers are to be rated at 360MVA. (SHETL- RI-079) | 28/09/2029
Templeton BESS | PRO-002593 | CS-09776 | Fig Power Limited | Lyndhurst 132/33kV | SHET-RI-183 | New Dundee 132kV Substation – Construction of a new 132kV double busbar substation in Dundee, to replace Dudhope GSP. This busbar will be fed by turning in the current Dudhope/Milton of Craigie 132kV circuits. (SHET-RI-183) | 31/10/2027
|  | CS-09777 | Fig Power Limited | Lyndhurst 132/33kV | SHET-RI-255 Abernethy 400kV Substation | Construct a new 400kV busbar to facilitate the connection of a new 400/33kV GSP at Abernethy. | 31/10/2027
Teviot Wind Farm | PRO-000855 | CS-06682 | TEVIOT WF LIMITED | Teviot Wind Farm Substation | SPT-RI-1738 | 1. Teviot to Harker Reinforcements - It is proposed to construct at a location in the vicinity of Teviot wind farm site a double busbar 132kV AIS substation to which two 400/132kV 360MVA interbus supergrid transformers will be connected. A double busbar AIS 400kV substation will also be established at the wind farm site to which the interbusing transformers will be connected and two further bays will be provided to connect a double circuit OHL. From the 400kV substation a double circuit OHL of around 43km built on L8 towers and installed with twin Totara conductors will be constructed to Harker 400kV substation. SPT will build the OHL to SPT/NGET boundary and NGET will complete the construction of the scheme from the boundary to Harker. (SPT-RI-1738) | 30/05/2033
|  | CS-06683 | TEVIOT WF LIMITED | Teviot Wind Farm Substation | NGET 101074 - 202154 | 2. New OHL reinforcement from Teviot Substation to Harker 400kV substation. (NGET 101074 – 202154) | 30/05/2033
|  | CS-06684 | TEVIOT WF LIMITED | Teviot Wind Farm Substation | NGET 101076 - 202156 | 3. Offline rebuild of Harker 400kV Substation to enable the connection of scheme 101074 – 202154. (NGET 101076 – 202156) | 30/05/2033
THE CLEAN FUTURE | PRO-002019 | CS-07482 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101866-203832 | Extend Killingholme 400kV substation at main busbar 5 side and make provision for the connection of user bay. | 31/05/2033
|  | CS-07483 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 31/05/2033
|  | CS-07488 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 0333496-0333496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 31/05/2033
|  | CS-07484 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100944-201881 | Build a new 400 kV double circuit between the new Grimsby West and Lincolnshire Coastal substations | 31/05/2033
|  | CS-07487 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100455-201020 | 1. Transpose the Cottam 1 circuit with the West Burton 1 circuit at Keadby 400kV substation. 2. Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby – Thorpe Marsh 400 kV circuit | 31/05/2033
|  | CS-07494 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 31/05/2033
|  | CS-07485 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100944-201880 | Rebuild Grimsby West 400kV as a double busbar substation | 31/05/2033
|  | CS-07491 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 31/05/2033
|  | CS-07495 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100450-201015 | Uprate the Cottam - Keadby 1 and 2 circuits to achieve a post fault winter rating of 3300MVA. | 31/05/2033
|  | CS-07486 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100944-201884 | Build a new 400kV Weston Marsh Substation with 10 Bays - 8 Feeder bays, 1 Coupler Bay and 1 Section Breaker Main and Reserve | 31/05/2033
|  | CS-07489 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100944-201911 | Uprate Weston Marsh - Walpole Double Circuit to achieve a post fault summer rating of 3300MVA | 31/05/2033
|  | CS-07490 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101746-203470 | Build South Lincolnshire to Rutland reinforcement (NOA LRNC) | 31/05/2033
|  | CS-07492 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101593-101593 | Uprate the Cottam- Staythorpe circuit 1, to provide winter post fault rating of 3300MVA This includes the cable section. | 31/05/2033
|  | CS-07493 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 31/05/2033
|  | CS-07497 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 031380-031380 | Hotwire the 4x400mm2 sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 31/05/2033
|  | CS-07496 | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation | 100450-201014 | Uprate the Drax – Eggbrough 1 circuit to achieve a post fault summer rating of 2500MVA. | 31/05/2033
Thorney Edge | PRO-002327 | CS-08704 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 100478-201049 | Reconductor the Drakelow-Willington East 400kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA | 30/11/2037
|  | CS-08693 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 100425-200971 | Reconductor Feckenham-Ironbridge 400 kV circuit to achieve a pre fault summer rating of 2490 MVA | 30/11/2037
|  | CS-08698 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 101910-203902 | Uprating of the Feckenham - Walham 400kV circuit to achieve minimum summer pre-fault rating of 2550MVA | 30/11/2037
|  | CS-08705 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 101977-204102 | Cable section uprate of the Bishops Wood-Penn 275kV circuit to match the overhead line summer prefault rating of 925MVA | 30/11/2037
|  | CS-08692 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 100426-200972 | Reconductor Feckenham-Minety 400 kV circuit to achieve a pre fault summer rating of 2610 MVA | 30/11/2037
|  | CS-08699 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 101908-203900 | Uprate the Feckenham to Hams Hall 400Kv circuit to achieve a pre-fault summer rating of 2490 MVA | 30/11/2037
|  | CS-08696 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 101381-202705 | Establish a new 400kV circuit out of North Wales for increased thermal capability. | 30/11/2037
|  | CS-08702 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/11/2037
|  | CS-08701 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 101939-203974 | Reconductor the Drakelow-Rugeley 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA | 30/11/2037
|  | CS-08695 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 101805-203692 | Install power control devices (8ohms) with push and pull capability on the Cellarhead-Drakelow 400kV circuits 1 and 2 | 30/11/2037
|  | CS-08697 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 101905-203903 | New Power Control with Push Pull Capability into Rugeley Drakelow Circuit | 30/11/2037
|  | CS-08694 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 101474-202916 | Reconductor the existing Cellarhead-Drakelow 400 kV circuits 1 and 2 to achieve a pre fault summer rating of 2800 MVA | 30/11/2037
|  | CS-08691 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 102463-205036 | Extend the 400kV substation compound to facilitate the busbar extension for an additional generator bay. | 30/11/2037
|  | CS-08703 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 101909-203901 | Reconductor the Ironbridge-Rugeley 400kV circuit with 2x620mm2 conductor to achieve a pre-fault summer rating of 2490 MVA. | 30/11/2037
|  | CS-08700 | ARLINGTON (GROUP SERVICES) LIMITED | Cellarhead 400kV Substation | 101907-203905 | Reconductor the Drakelow – Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault summer rating of 2490 MVA | 30/11/2037
Thornlemuir Farm | PRO-003600 | CS-08542 | GPC 1119 Ltd | Neilston 132kV Substation | SPT-RI1741 | Neilston SGT Auto Changeover Scheme - An auto changeover scheme is required at Neilston substation to allow the connection of synchronous compensators at Neilston 400kV. The scheme is needed for the management of fault level at Neilston 132kV substation. It is proposed that one of the three supergrids (SGT1, SGT2 or SGT3B) that serve Neilston 132kV substation to be on open standby to reduce the fault infeed to the 132kV substation and for an unplanned outage on another SGT, the one on open standby will need to be returned to service | 30/09/2027
|  | CS-08543 | GPC 1119 Ltd | Neilston 132kV Substation | SPT-RI1968 | Neilston 275kV Uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. ( | 30/09/2027
Thornton | PRO-001647 | CS-06953 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101093-202181 | Establish a new 400kV double circuit route between Creyke Beck 400kV and High Marnham 400kV substation including all associated substation works | 31/10/2031
|  | CS-06954 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 31/10/2031
|  | CS-06955 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 31/10/2031
|  | CS-06956 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101554-203095 | Reconductor the new High Marham - Staythorpe 400 kV circuit with 2x620mm2 GZTACSR conductor | 31/10/2031
|  | CS-06957 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph 400kV circuit with 2x620mm2 GZTACSR conductor | 31/10/2031
|  | CS-06958 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 100821-201659 | Reconductor the Creyke Beck and Keadby legs of the Creyke Beck-Humber Refinery–Keadby 400kV and Creyke Beck -Keadby –Killingholme 400kV circuits with 3x700mm2 conductor | 31/10/2031
|  | CS-06959 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 31/10/2031
|  | CS-06960 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 31/10/2031
|  | CS-06961 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 033754-033755 | Establish a new 400kV double circuit connecting to the Norton – Osbaldwick 400kV double circuit to Poppleton including all associated substation works | 31/10/2031
|  | CS-04697 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101551-203092 | Thornton 400kV substation extend busbars to make provision for connection of Users generator bay | 31/10/2031
|  | CS-04698 | IGP SOLAR 19 LIMITED | Thornton 400kV Substation | 101552-203093 | At Thornton 400kV substation replace circuit breaker X805 with a new 63kA rated circuit breaker with a X/R ratio of at least 24. | 31/10/2031
Thornton Facility | PRO-001484 | CS-09452 | BALWEN LIMITED | Thornton 400kV Substation | 030613-030613 | Uprate the Cottam - Staythorpe (2) circuit to provide a post-fault summer rating of 2800 MVA | 25/10/2024
|  | CS-09447 | BALWEN LIMITED | Thornton 400kV Substation | 101664-203317 | At Keadby 400kV, installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to 8 ohms to the Keadby – Creyke Beck/Killingholme circuit | 25/10/2024
|  | CS-09456 | BALWEN LIMITED | Thornton 400kV Substation | 101576-203163 | Uprate the Osbaldwick leg of the new Norton- Osbaldwick/ Poppleton 400kV circuits to provide a pre-fault summer rating of 1700 MVA | 25/10/2024
|  | CS-09448 | BALWEN LIMITED | Thornton 400kV Substation | 101041-202083 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +8 ohms along the Cottam – West Burton 1 (A413) 400kV circuit | 25/10/2024
|  | CS-09446 | BALWEN LIMITED | Thornton 400kV Substation | 100455-201020 | 1. Transpose the Cottam 1 circuit with the West Burton 1 circuit at Keadby 400kV substation. 2. Installation of a 2750MVA power electronics bases Power flow control device (such as SV) with the capacity of pushing mode capable of injecting up to +20 ohm in the Drax – Keadby – Thorpe Marsh 400 kV circuit | 25/10/2024
|  | CS-09457 | BALWEN LIMITED | Thornton 400kV Substation | 101923-203933 | Uprating of Circuit Breakers at Creyke Beck for a higher X/R ratio on X110, X130, X210, X230, X310 and X410 | 25/10/2024
|  | CS-09445 | BALWEN LIMITED | Thornton 400kV Substation | 101714-203421 | Installation of a power flow control device (such as SV) along the new High Marnham – Staythorpe 400 kV circuit | 25/10/2024
|  | CS-09451 | BALWEN LIMITED | Thornton 400kV Substation | 101386-202715 | Uprate the Lackenby - Thornton 1 and 2 circuits to achieve a pre fault summer rating of 2250MVA | 25/10/2024
|  | CS-09453 | BALWEN LIMITED | Thornton 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a pre-fault summer rating of 2750MVA | 25/10/2024
|  | CS-09441 | BALWEN LIMITED | Thornton 400kV Substation | 100161-200456 | Uprating/Replacement of the CB X120 at Eggborough 400kV substation | 25/10/2024
|  | CS-09443 | BALWEN LIMITED | Thornton 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 25/10/2024
|  | CS-09454 | BALWEN LIMITED | Thornton 400kV Substation | 101703-203406 | Installation of a 3600MVA power electronics bases power flow control device with the capacity of pushing mode capable of injecting up to +4ohms along the Drax-Thornton 1 400kV circuit | 25/10/2024
|  | CS-09455 | BALWEN LIMITED | Thornton 400kV Substation | 033754-033755 | A new 400kV double circuit between Osbaldwick and Poppleton and relevant 275kV upgrades (NOA OPN2) | 25/10/2024
|  | CS-09449 | BALWEN LIMITED | Thornton 400kV Substation | 101663-203316 | Installation of a 3600MVA power electronics bases Power flow control device (such as SV) with the capacity of pulling mode capable of injecting up to -8 ohms along the Bicker Fen – West Burton 1 (A685) 400kV circuit | 25/10/2024
|  | CS-09450 | BALWEN LIMITED | Thornton 400kV Substation | 100449-201014 | Uprate the Drax – Eggborough 1 & 2 circuits to achieve a post-fault summer rating of 2500MVA | 25/10/2024
|  | CS-09440 | BALWEN LIMITED | Thornton 400kV Substation | 100597-201228 | Uprating/Replacement of the CB X405 at Thornton 400kV substation | 25/10/2024
|  | CS-06488 | BALWEN LIMITED | Thornton 400kV Substation | 101191- 202401 | Busbar extensions to provide space for the User’s connection bay | 25/10/2024
|  | CS-06489 | BALWEN LIMITED | Thornton 400kV Substation | 100467-201036 | Reconductor Drax –Thornton double circuit with 3 x 700mm2 at 75°C. Replace the disconnectors and protection on both Thornton circuits at Drax substation to equipment with an equal rating to provide a post-fault winter rating of 3420MVA | 25/10/2024
|  | CS-06490 | BALWEN LIMITED | Thornton 400kV Substation | 100821- 201659 | Reconductor the existing 4x400 mm2 ACSR sections of the Keadby leg of the Creyke Beck – Keadby – Killingholme circuit with 3×700 mm2 AAAC strung for operation at 75ºC | 25/10/2024
|  | CS-06491 | BALWEN LIMITED | Thornton 400kV Substation | 100844-201689 | Reconductor Cottam – Staythorpe 1 circuit with 2x620mm2 conductor and uprate the cable section to 3 cores per phase | 25/10/2024
|  | CS-06492 | BALWEN LIMITED | Thornton 400kV Substation | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 25/10/2024
|  | CS-06493 | BALWEN LIMITED | Thornton 400kV Substation | 033512-033512 | Uprate Keadby – West Burton 1 circuit to provide a post-fault winter rating of 3420MVA | 25/10/2024
|  | CS-06494 | BALWEN LIMITED | Thornton 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 25/10/2024
|  | CS-06495 | BALWEN LIMITED | Thornton 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm2 AAAC sections of the circuits with 2×591mm2 ACCR conductor and the 2x700mm2 AAAC sections with 3x700mm2 AAAC conductor | 25/10/2024
|  | CS-09439 | BALWEN LIMITED | Thornton 400kV Substation | 101191-205618 | Extension to CNI fence, gates and camera system | 25/10/2024
|  | CS-09444 | BALWEN LIMITED | Thornton 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 25/10/2024
|  | CS-09442 | BALWEN LIMITED | Thornton 400kV Substation | 100452-201017 | Uprating/Replacement of the following CB at Drax 400kV substation: X110, X210, X130, X330, X120 and X220 at Drax 400kV substation | 25/10/2024
Thorpe Marsh 1 (Tertiary) | PRO-000470 | CS-06962 | ENSO GREEN HOLDINGS LIMITED | Thorpe Marsh 400kV Substation | 100954-201902 | 1. Install a tertiary cable box or bushings on SGT 9 2. Install a 13kV cable (if required) from tertiary cable box or bushings to earthing transformer 3. Install an earthing transformer 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets | 31/10/2024
Thorpe Marsh Energy Park | PRO-001620 | CS-06963 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 101504-202964 | Facilitate connection of Users generator bay on busbar 5 at Thorpe Marsh 400kV B substation | 30/10/2026
|  | CS-06964 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 30/10/2026
|  | CS-06965 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 101504-202966 | Hotwire the 2x400mm2 sections of the Bredbury – Stalybridge circuit to an operating temperature of 75°C. | 30/10/2026
|  | CS-06966 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 30/10/2026
|  | CS-06967 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 100171-200449 | Reconductoring the 2x400mm2 sections of the Thorpe Marsh – West Melton circuit 1 for operation at 65 degrees provide a post-fault winter rating of 1090MVA | 30/10/2026
|  | CS-06968 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 30/10/2026
|  | CS-06969 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 031380-031380 | Hotwire the 4x400mm2 sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 30/10/2026
|  | CS-06970 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm2 cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm2 cable. | 30/10/2026
|  | CS-06971 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post fault winter rating of 3420MVA | 30/10/2026
|  | CS-06972 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 30/10/2026
|  | CS-06973 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 30/10/2026
|  | CS-06974 | Banks Renewables Limited | Thorpe Marsh 400kV Substation | 101041-202083 | Power Control technology along the Cottam – West Burton 1 (A413) 400kV circuit | 30/10/2026
Thorpe Marsh Green Energy Centre | PRO-001724 | CS-05318 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 100171-200448 | Uprate Thorpe Marsh – West Melton Circuit 1 by replacing the cable section of this circuit to provide a post-fault winter rating of 1090MVA | 30/10/2030
|  | CS-05327 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 100905-201821 | At Keadby replace the disconnector (X1005) on the Drax – Keadby – Thorpe Marsh circuit (A37C) to provide a post fault winter rating of 3275MVA | 30/10/2030
|  | CS-05328 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 031380-031380 | Hotwire the 4x400mm2 sections of the Lackenby – Thornton 1 400kV circuit for operation at 75°C. Reconductor the 2x700 sections with GAP or equivalent conductor. | 30/10/2030
|  | CS-05330 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101358-202678 | Hotwire the 2x400mm2 sections of the conductor on the Bredbury – South Manchester 275kV circuit to an operating temperature of 75 degrees | 30/10/2030
|  | CS-05333 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101571-203146 | At Thorpe Marsh B 400kv Substation: 1) Eastern extension of the 400kV AIS double busbar to a three section arrangement; comprising of 4 circuit feeder bays, 1 transformer bay, 1 bus coupler bay and 2 section breaker bays 2) Install SGT10 400/275kV 1100MVA Interbus transformers. 3) Connect and Commission SGT8 400/66kV 180MVA Transformer. 4) Busbar extension to provide space for Generator bay (User works). Associated OHL and cable works to transfer following circuits to Thorpe Marsh B 400kV substation: 1) Brinsworth 1 400kV circuit. 2) Drax 400kV circuit. 3) Eggborough 400kV circuit. 4) Stalybridge 400kV circuit. 5) West Melton 1 275kV circuit. | 30/10/2030
|  | CS-05334 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 100171-200449 | Reconductoring the 2x400mm2 sections of the Thorpe Marsh – West Melton circuit 1 for operation at 65 degrees provide a post-fault winter rating of 1090MVA | 30/10/2030
|  | CS-05335 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101571-203148 | Offline replacement of Thorpe Marsh 66kV substation | 30/10/2030
|  | CS-05336 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101571-203149 | Establish Yorkshire Operation Tripping Scheme | 30/10/2030
|  | CS-05337 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm2 cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm2 cable. | 30/10/2030
|  | CS-05338 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 30/10/2030
|  | CS-05339 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101510-202975 | On the Bredbury – Stalybridge 275kV circuit reconductor the 2x400mm2 sections of the circuits between towers ZZC40R and ZZC002 and towers ZZC002 and ZZC001 (13,15km total) with 2x570 mm2 strung to an operating temperature of 75°C. The remaining 1.9km section between ZZC46R and ZZC40R which is already 2x570 mm2should be hotwired to an operating temperature of 75°C. Replace the thermally limiting circuit breaker with a new circuit breaker rated at 3150A continuous. | 30/10/2030
|  | CS-05340 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 033513-033513 | Uprate Keadby – West Burton circuit 2 (A39E) to achieve a post-fault winter rating of 3420MVA | 30/10/2030
|  | CS-05341 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101561-203105 | Uprate the cables sections on: 1) Rochdale – Whitegate 2 275kV circuit 2) Kearsley – Whitegate 1 and 2 275kV circuits | 30/10/2030
|  | CS-05342 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 30/10/2030
|  | CS-05343 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101041-202083 | Power Control technology along the Cottam – West Burton 1 (A413) 400kV circuit | 30/10/2030
|  | CS-05344 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101511-202976 | Hotwire the 2x400mm2 section of the Elland – Stalybridge circuit between towers ZP127 and ZP183 (17.86km) to an operating temperature of 75°C | 30/10/2030
|  | CS-05345 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101504-202965 | Uprate the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit to achieve a pre-fault summer rating of 2790MVA | 30/10/2030
|  | CS-05346 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 100451-201016 | Uprate the Gantries (including down-droppers and down-leads) to match the conductor on the High Marnham - West Burton Circuit (A403) to achieve a post fault summer rating of 2420MVA | 30/10/2030
|  | CS-05347 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101482-202929 | Uprate Aldwarke to Brinsworth -Thurcroft cct 1 | 30/10/2030
|  | CS-05348 | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 101359-202679 | Uprate Neepsend - Pitsmoor 275kV cable | 30/10/2030
Three Lochs Hydro | PRO-000716 | CS-04299 | Scottish Hydro Electric Power Distribution Plc | Grudie Bridge GSP | SHET-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 30/06/2024
|  | CS-04300 | Scottish Hydro Electric Power Distribution Plc | Grudie Bridge GSP | SHET-RI-023 | Upgrade section of the Beauly - Grudie Bridge (BFN/BFS) 132kV double circuit line with two circuits of large conductors and increased design capacity. The upgrade conductor will be between the new Corriemoillie 132kV substation (Near Mossford). | 30/06/2024
Thurso BESS | PRO-001967 | CS-08480 | Stainland BESS Limited | Thurso South GSP | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 30/06/2027
|  | CS-08479 | Stainland BESS Limited | Thurso South GSP | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 30/06/2027
|  | CS-08481 | Stainland BESS Limited | Thurso South GSP | no Scheme | 0 | 30/06/2027
Thurso South BESS | PRO-003655 | CS-09573 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-182 | Loch Buidhe to Spittal 2 400kV Reinforcement - Construct a new 85km of 400kV double circuit OHL between Loch Buidhe and Spittal 2 400kV substations | 31/10/2030
|  | CS-09574 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2030
|  | CS-09570 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-128 | Caithness – Peterhead Transmission Reinforcement 2250MW Link- As part of the Caithness-Peterhead Transmis-sion Reinforcement, it is required to construct a 2250MW HVDC link from Spittal to Peterhead. The HVDC link is approximately 145km from Spittal to Peterhead (130km subsea cable). (SHET-RI-128) | 31/10/2030
|  | CS-09575 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2030
|  | CS-09568 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-058 | Beauly to Loch Buidhe (Cambusmore) 275kV OHL Reinforcement - Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: a. Two new Super Grid Transformers to connect Shin 132kV substation b. New double circuit steel lattice tower construction approximately 40km. c. Works at Beauly and Loch Buidhe 275kV substations | 31/10/2030
|  | CS-09569 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-058a | Beauly to Loch Buidhe 275kV OHL Reinforcement - Reprofile the existing 275kV double circuit OHL between Beauly and Loch Buidhe (approximately 67km). The double circuit is to be reprofiled to allow high temperature operation of 90 degrees Celsius to increase the continuous current rating of the circuit | 31/10/2030
|  | CS-09572 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-153 | Spittal 2 275kV Substation - Construct a new 275kV substation ‘Spittal 2’ close to the existing Spittal 275kV substation in Caithness. (SHET-RI-153) | 31/10/2030
|  | CS-09571 | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ | SHET-RI-140 | 1. Thurso South 275kV Substation Redevelopment - Redevelop the existing Thurso South 275kV substation into a new 275kV double busbar arrangement | 31/10/2030
Tillbridge Solar | PRO-001126 | CS-05774 | TILLBRIDGE SOLAR LIMITED | Cottam 400kV Substation | 100842-201687 | Attributable works | 01/10/2027
|  | CS-05119 | TILLBRIDGE SOLAR LIMITED | Cottam 400kV Substation | 100246-200624 | At Keadby 400kV substation: Replace circuit breaker X210. New Circuit Breaker to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break. | 01/10/2027
|  | CS-05122 | TILLBRIDGE SOLAR LIMITED | Cottam 400kV Substation | 100844-201689 | Reconductor Cottam – Staythorpe 1 circuit with 2x620mm2 conductor and uprate the cable section to 3 cores per phase | 01/10/2027
|  | CS-05124 | TILLBRIDGE SOLAR LIMITED | Cottam 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm2 AAAC sections of the circuits with 2×591mm2 ACCR conductor and the 2x700mm2 AAAC sections with 3x700mm2 AAAC conductor | 01/10/2027
Tinnisburn Wind Farm | PRO-003997 | CS-09724 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | SPT-RI-231 | 0 | 30/10/2031
|  | CS-09727 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | Tinnisburn - Circuit breaker bay | At Bloch Collector substation install a new 132kV circuit breaker bay with associated disconnectors. | 30/10/2031
|  | CS-09728 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | Tinnisburn - 132kV circuit | Construct a new 132kV circuit from Bloch Collector SS to Tinnisburn Wind Farm. This circuit should be capable of 96MVA | 30/10/2031
|  | CS-09729 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | Tinnisburn - 132kV line disconnector | At Tinnisburn Wind Farm install a 132kV line disconnector | 30/10/2031
|  | CS-09725 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | SPT-RI-2320 | 0 | 30/10/2031
|  | CS-09726 | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation | SPT-RI-3434 | Wyseby Hill to Bloch Collector SS 132kV Circuit - Given the number of generation applications in this area and the arrangement at Wyseby Hill, it is proposed to establish a new shared collector substation. It is proposed to install a new 400kV double busbar bay and 400/132kV 240MVA transformer at Wyseby Hill 400kV substation planned to be constructed as part of SPT-RI-2320. From here approx. 9km of 132kV circuit shall be constructed to the Bloch collector substation. At Bloch collector substation, install a single 132kV busbar with a 132kV disconnector. | 30/10/2031
Toftinghall Windfarm | PRO-000960 | CS-06204 | SETT WIND DEVELOPMENT LIMITED | Mybster 1 GSP | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/08/2025
|  | CS-06205 | SETT WIND DEVELOPMENT LIMITED | Mybster 1 GSP | SHET-RI-060 | Loch Buidhe/Dounreay 275kV Circuit (DU1) Reconductoring — Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay making it the same specification as the east side. (SHET-RI-060) | 31/08/2025
|  | CS-06206 | SETT WIND DEVELOPMENT LIMITED | Mybster 1 GSP | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 31/08/2025
Tormsdale Windfarm | PRO-001904 | CS-07065 | ARISE AB | Mybster 3 132/33kV Substation | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 30/06/2027
|  | CS-07066 | ARISE AB | Mybster 3 132/33kV Substation | SHET-RI-088 | Loch Buidhe – Dounreay 275kV Reinforcement - Reconductor the existing 275kV double circuit OHL between Loch Buidhe and Dounreay (approximately 87km). The double circuit is to be reconductored with a high temperature conductor, with a summer pre-fault rating of 900MVA. (SHET-RI-088) | 30/06/2027
|  | CS-07067 | ARISE AB | Mybster 3 132/33kV Substation | no Scheme | 0 | 30/06/2027
Tormywheel Extension WF | PRO-002355 | CS-08165 | SP Distribution plc | Bathgate 132/33kV Substation | SPT-RI-1659 | Bathgate to Bonnybridge 132kV No.1 and No.2 cable uprate | 29/10/2026
Torrance Farm Extension 2 | PRO-001835 | CS-05400 | SP Distribution plc | Bathgate (SPD) GSP | SPT-RI-1659 | Bathgate to Bonnybridge 132kV No.1 and No.2 cable uprate | 30/09/2025
Torridge 2 Offshore Wind Farm | PRO-002795 | CS-09156 | UK MAINSTREAM RENEWABLE POWER LIMITED | Alverdiscott 400kV Substation | 102692-205383 | 0 | 06/12/2036
|  | CS-09157 | UK MAINSTREAM RENEWABLE POWER LIMITED | Alverdiscott 400kV Substation | 101064-202137 | At Alverdiscott 400kV substation, install new cables to run between the new 400kV substation building and the current 400/132kV SGT’s. | 06/12/2036
|  | CS-09158 | UK MAINSTREAM RENEWABLE POWER LIMITED | Alverdiscott 400kV Substation | 101064-202136 | Rebuild the current Alverdiscott substation to a double busbar arrangement. To be located adjacent to the current substation (offline build). Reconfigure overhead lines to form a double turn in arrangement. | 06/12/2036
Tottenham | PRO-001060 | CS-06101 | PIVOTED POWER LLP | Tottenham GSP | 100667-201364 | 1. Extension of the existing Tottenham 275kV substation boundary to accommodate the User’s Assets. 2. Install a tertiary cable box or bushings on SGT1. 3. Install 13kV cable from the tertiary cable box or bushings to an earthing transformer (exact route/length to be confirmed in detailed design stage). 4. Install a 13kV earthing transformer. 5. Install a 13kV disconnector for connection to User’s assets | 31/10/2024
|  | CS-06102 | PIVOTED POWER LLP | Tottenham GSP | 100667201365 Connection | Connection | 31/10/2024
|  | CS-06103 | PIVOTED POWER LLP | Tottenham GSP | 100667-201556 One Off | One Off Works | 31/10/2024
Trafford Power | PRO-000276 | CS-06104 | WAINSTONES ENERGY LIMITED | Carrington 400KV Substation | 33285 | Re-conductor the Carrington to Daines 4 circuit (~2km) with 2 x 620mm² GZTACSR gap-type conductor at 170°C. | 30/10/2025
|  | CS-06105 | WAINSTONES ENERGY LIMITED | Carrington 400KV Substation | 21619 - 11 | Associated substation works for the turn-in including the Penwortham and Daines feeder bays and GIB runs to connect the Penwortham - Daines circuit (ZQ route) to the new 400kV substation. | 30/10/2025
|  | CS-06106 | WAINSTONES ENERGY LIMITED | Carrington 400KV Substation | 21619 - 2 | OHL turn in the Penwortham - Daines circuit into existing Carrington substation. | 30/10/2025
|  | CS-06107 | WAINSTONES ENERGY LIMITED | Carrington 400KV Substation | 33285L | Rephasing of the Carrington - Penwortham circuit. | 30/10/2025
|  | CS-06108 | WAINSTONES ENERGY LIMITED | Carrington 400KV Substation | 21619-1 | Extend the 400kV GIS double busbar substation at Carrington. | 30/10/2025
|  | CS-06109 | WAINSTONES ENERGY LIMITED | Carrington 400KV Substation | 21619-1S | Advance civil works at Carrington substation for Wainstones. | 30/10/2025
|  | CS-06110 | WAINSTONES ENERGY LIMITED | Carrington 400KV Substation | 33285O | Build one skeletal GIS bays for connection of the generation. | 30/10/2025
|  | CS-06111 | WAINSTONES ENERGY LIMITED | Carrington 400KV Substation | 33285S | Scheme Description Build and install a Category 1 intertrip to trip the generation for faults which overload the NETS and also two skeletal GIS bays for connection of the generation. Build and install a Category 1 intertrip to trip the generation for faults which overload the NETS and also two skeletal GIS bays for connection of the generation. | 30/10/2025
Troston Wind Farm | PRO-001115 | CS-06119 | TROSTON WINDFARM LIMITED | Troston Wind Farm 132kV Substation | Troston Item 1 | Installation of a new 132kV disconnector at a tee point (Glenshimmeroch Collector Substation) on the New Cumnock / Blackcraig 132kV circuit and installation of approximately 5km of 132kV overhead line (POPLAR). | 31/10/2027
|  | CS-06120 | TROSTON WINDFARM LIMITED | Troston Wind Farm 132kV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 31/10/2027
|  | CS-06121 | TROSTON WINDFARM LIMITED | Troston Wind Farm 132kV Substation | SPT-RI-186 | Kilmarnock South SGT1(2)(6) Overload Protection Scheme | 31/10/2027
|  | CS-06122 | TROSTON WINDFARM LIMITED | Troston Wind Farm 132kV Substation | SPT-RI-274 | Glenshimmeroch Collector Substation - On the New Cumnock / Blackcraig 132kV circuit, installation of a 132kV circuit breaker and associated disconnectors at Glenshimmeroch Collector Substation in South West Scotland. | 31/10/2027
|  | CS-06123 | TROSTON WINDFARM LIMITED | Troston Wind Farm 132kV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 31/10/2027
Tulliallan BESS | PRO-003619 | CS-09541 | IGP ENERGY STORAGE 6 LIMITED | Kincardine 275kV Substation | SPT-RI-2095 | Kincardine North 400kV Substation - The scope of works at Kincardine North 400kV Substation (ref. NOA Code LWUP) is summarised as follows. The new Kincardine North 400kV GIS Substation will initially connect the following circuits: SHE Transmission Alyth No.1 400kV, SHE Transmission Alyth No.2 400kV, Denny North No.1 400kV, Denny North No.2 400kV, Kincardine No.1 400kV, and Kincardine No.2 400kV. The substation will be equipped with two bus section circuit breakers and two bus coupler circuit breakers | 31/10/2031
|  | CS-09543 | IGP ENERGY STORAGE 6 LIMITED | Kincardine 275kV Substation | SPT-RI-2083 | Kincardine North – Wishaw 400kV reinforcement (DWUP)- Establish 400kV infrastructure through the centre of the network following the East Coast 400kV onshore incremental (ECUP) reinforcement, but in advance of the completion of existing Denny to Wishaw 400kV reinforcement (DWNO). The scope of this TORI will be aligned with the ‘DWUP’ option submitted to the 2021/22 Network Options Assessment (NOA) process. It is proposed to reconfigure and update existing 275kV single circuit between the Kincardine and Wishaw to 400kV operation to establish a new Kincardine North – Wishaw 400kV circuit. | 31/10/2031
|  | CS-09542 | IGP ENERGY STORAGE 6 LIMITED | Kincardine 275kV Substation | SPT-RI-2073 | 18. TKUP Kincardine North - Tealing 400kV Uprating | 31/10/2031
Twyn Hywel Cillfynydd | PRO-001497 | CS-04608 | Twyn Hywel Energy Park Ltd | Cilfynydd 400kV Substation | 100424-200970 | Reconductor the Bramley – Melksham 400kV circuits 1 and 2 to achieve a pre-fault summer rating of 1990MVA | 30/06/2025
|  | CS-04609 | Twyn Hywel Energy Park Ltd | Cilfynydd 400kV Substation | 020903-020903 | Uprating of the Cowley - Walham 400kV circuit cables to achieve 1500MVA post-fault summer rating. | 30/06/2025
|  | CS-06505 | Twyn Hywel Energy Park Ltd | Cilfynydd 400kV Substation | 101231-202455 | 1. Double busbar extension of Cilfynydd 400kV substation to provide space for the user’s generator bay. | 30/06/2025
Upper Beoch Windfarm | PRO-004068 | CS-09808 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-1797 | STHA-ELVA 400kV Reinforcement (Non-Secured)– Due to the increased level of generation connecting on to ZV Route it is necessary to thermally uprate the Strathaven to Elvanfoot 400kV OHL circuits (STHA-COAL, COAL-REDS, REDS-ELVA and STHA-REDS, REDS-ELVA). It is proposed to reconductor the double circuit with twin ACCR “Curlew HTLS” conductor operating at 190℃ | 31/10/2033
|  | CS-09807 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 31/10/2033
|  | CS-09810 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-3315 | New Cumnock North to Glenmuckloch 400kV OHL- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new double circuit OHL between (the proposed) New Cumnock North and Glenmuckloch 400kV substation. The scope of works shall consist of 2 stages: Stage 1 – establishment of a new double circuit OHL (L8 with Twin RUBUS conductor is proposed) from New Cumnock North towards Glenmuckloch. One side of the circuit shall be energised in this stage to provide a minimum scope required to enable a connection of New Cumnock BESS. Stage 2 – establishment of a second double busbar GIS switchgear bays at New Cumnock North 400kV substation to connect to the OHL No.1 circuit | 31/10/2033
|  | CS-09809 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-3309 | New Cumnock North 400kV GIS substation- To accommodate new generation connection in the New Cumnock including the South-West Scotland area, it is proposed to establish a new 400kV substation in the vicinity of the existing New Cumnock 275kV substation. This shall be a double busbar GIS ‘New Cumnock North’ 400kV substation. This new substation shall facilitate the development of the NOA WCNC scheme (currently under review) | 31/10/2033
|  | CS-09806 | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation | SPT-RI-231 | 0 | 31/10/2033
Valorous Offshore Wind Farm | PRO-001383 | CS-06302 | BLUE GEM WIND LIMITED | Pembroke 400kV Substation | 101019-202042 | At Pembroke 400kV substation: Extend Main Bar 2 and Reserve Bar 1/2 with GIS for one User bay and a feeder circuit. Transfer the bay of Pembroke - Swansea North 400kV Circuit 3 to the new busbar extension. Install a section circuit breaker on Main Bar 2 into the bay previously populated by the Pembroke - Swansea North 400kV Circuit 3. | 02/04/2029
|  | CS-06303 | BLUE GEM WIND LIMITED | Pembroke 400kV Substation | 100838-201680 | Replacement of feeder circuit breakers X105 and X305 of Pembroke - Swansea North 400 kV Circuits 1 and 3 and modification of feeder protection to allow faster operation times. | 02/04/2029
|  | CS-06304 | BLUE GEM WIND LIMITED | Pembroke 400kV Substation | 101019-202149 | Extension to the Pembroke 400kV Operational Tripping Scheme to include the Valorous Offshore Wind Farm. | 02/04/2029
|  | CS-06305 | BLUE GEM WIND LIMITED | Pembroke 400kV Substation | 100424-200970 | Reconductor the Bramley - Melksham 400kV circuits 1 and 2 to the Gap conductor to achieve a Pre-fault Summer rating of 1990MVA. | 02/04/2029
|  | CS-06306 | BLUE GEM WIND LIMITED | Pembroke 400kV Substation | 033769-033769 | Reconductor the Taunton - Hinkley Point - Exeter 400kV circuits to achieve a 3100MVA post fault winter rating. Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating | 02/04/2029
|  | CS-06307 | BLUE GEM WIND LIMITED | Pembroke 400kV Substation | 020903-020903 | Uprating of the Cowley - Walham 400kV circuit cables to achieve 1500MVA post-fault summer rating. | 02/04/2029
|  | CS-06308 | BLUE GEM WIND LIMITED | Pembroke 400kV Substation | 101050-202108 | At Swansea North 400kV: Turn in Pembroke - Walham 400kV circuit at Swansea North. Transfer to the 400kV GIS compound the circuits Pembroke - Swansea North 400kV Circuit 3 and Swansea North – Cilfynydd 400kV circuit. | 02/04/2029
Vanguard | PRO-000459 | CS-06132 | NORFOLK VANGUARD WEST LIMITED | Necton 400kV Substation | 30648-1 | Establish two new feeder bays at Norwich 400kV substation for the connection of the new double circuit from Bacton. | 01/12/2025
|  | CS-06133 | NORFOLK VANGUARD WEST LIMITED | Necton 400kV Substation | 32339LI | Build a new double circuit from the new Bacton 400kV substation to the existing Norwich 400kV substation. | 01/12/2025
|  | CS-06134 | NORFOLK VANGUARD WEST LIMITED | Necton 400kV Substation | 32339SI | Build 400kV AIS double busbar substation in the Bacton area, including one skeleton generator bay, two feeder bays and a bus coupler and additional works to connect 600MW. | 01/12/2025
Vanguard East | PRO-000580 | CS-04397 | Norfolk Vanguard East Ltd | Necton 400kV Substation | 100926-201852 | At Necton 400kV Substation: Extend the substation by 4 bays; A Main & Reserve Bus Section Bay, One Feeder Bay and one OFTO Bay. Transfer a circuit into the extended busbar section's feeder bay. Extension of the existing East Anglia Operational intertripping scheme. | 20/03/2028
Viking Link Denmark Interconnector | PRO-000288 | CS-06135 | NATIONAL GRID VIKING LINK LIMITED | Bicker Fen 400kV Substation | NGET-RI-33288 | Extend Bicker Fen 400kV AIS double busbar substation with two additional skeleton generator bays. | 30/09/2023
|  | CS-06136 | NATIONAL GRID VIKING LINK LIMITED | Bicker Fen 400kV Substation | NGET-RI-21339L | Convert the existing single turn in arrangement at Spalding North into a double tee arrangement to form two Bicker Fen - Spalding North - Walpole circuits. Reconductoring the 0.65km redwood conductor on the south route of the double tee points (Spalding North - Walpole circuits) with 3 x 700mm² conductor. | 30/09/2023
|  | CS-06137 | NATIONAL GRID VIKING LINK LIMITED | Bicker Fen 400kV Substation | NGET-RI-21765-1 | Extend and convert the existing Bicker Fen 400kV substation to a double busbar AIS substation with 4 feeder bays, 2 transformer bays, 1 bus coupler bays and 2 skeleton bus section bays to accommodating the existing 4 circuits and 2 transformers. Build 4 feeder bays, 2 transformer bays and one bus coupler and fully equip these bays. Modify the existing protection scheme to include 4 feeders, 2 transformers and one bus coupler. | 30/09/2023
Viking Wind Farm | PRO-000338 | CS-04332 | VIKING ENERGY WIND FARM LLP | Kergord GSP | SHET-RI-152 | Shetland ANM Scheme - ANM System on Shetland to manage flows across 600MW HVDC link (established under SHET-RI-053) from Kergord 132kV substation on Shetland to the Scottish mainland at an HVDC convertor station in the vicinity of Noss Head in Caithness. (SHET-RI-152) | 01/07/2024
|  | CS-06138 | VIKING ENERGY WIND FARM LLP | Kergord GSP | SHET-RI-007c | Blackhillock Substation Redevelopment – Redevelop Blackhillock Substation to enable the construction of a new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 360MVA 275/132kV SGTs. Connect the existing 2 x 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. Also construct a new 132kV double busbar at Blackhillock complete with associated circuit feeder bays. (SHET-RI-007c). | 01/07/2024
|  | CS-06139 | VIKING ENERGY WIND FARM LLP | Kergord GSP | SHET-RI-031 | Spittal – Blackhillock HVDC Link — As part of the Caithness/Moray Firth Transmission Reinforcement, it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). The HVDC link is to be 800MW from Spittal to Noss Head and 1200MW from Noss Head to Blackhillock. The HVDC link is required to harvest the renewable generation and reinforce the transmission network in the Caithness Area. The HVDC link is approximately 30km from Spittal to Noss Head and approximately 133km from Noss Head to Blackhillock (113km Subsea). | 01/07/2024
|  | CS-06140 | VIKING ENERGY WIND FARM LLP | Kergord GSP | SHET-RI-053 | Shetland 600MW HVDC Link and Kergord 132kV Substation ‒ Construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Noss Head in Caithness. The HVDC switching station works will be part of SHET-RI-062 and will integrate with the Caithness-Moray Transmission Reinforcement (part of SHET-RI-031). The HVDC link includes a 600MW HVDC converter station and 132kV Substation at Kergord in Shetland. The new 132kV Substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of subsea cable between Shetland and the HVDC switching station in Caithness. (SHET-RI-053) | 01/07/2024
VPI Immingham B OCGT | PRO-000854 | CS-06975 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 101040-202081 | Extend Main and Reserve Busbar 1 at Humber Refinery 400kV substation | 30/09/2024
|  | CS-06976 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100844-201689 | Reconductor the 2x500mm2 Rubus sections of the Cottam – Staythorpe 1 400kV circuit with 2x700mm2 Araucaria. Replace the cable section. Replace the 0.25km cable section at Cottam with a higher rated cable. | 30/09/2024
|  | CS-06977 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100821-201659 | Uprate the Keadby legs of the Creyke Beck - Humber Refinery – Keadby and Creyke Beck - Keadby – Killingholme circuits to achieve a rating of 3420MVA | 30/09/2024
|  | CS-06978 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 033513-033513 | Hotwire the 4x 400mm2 conductor of the Keadby – West Burton 2 400kV circuit to an operating temperature of 75°C. | 30/09/2024
|  | CS-06979 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm2 cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm2 cable. | 30/09/2024
|  | CS-06980 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100450-201015 | Uprate the Cottam – Keadby 2 circuits by reconductoring the 2x500mm2 AAAC sections of the circuits with 2×591mm2 ACCR conductor and the 2x700mm2 AAAC sections with 3x700mm2 AAAC conductor | 30/09/2024
|  | CS-06981 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 101041-202083 | At West Burton Install a power electronics-based power flow control device in the Cottam – West Burton 400kV circuit and replace disconnector and circuit breaker | 30/09/2024
|  | CS-06982 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100455-201020 | At Keadby 400kV substation Install a 2750MVA 16 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 30/09/2024
|  | CS-06983 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 033837-201649 | At Creyke Beck 400kV substation extend Main bar and Reserve bar 1 and Main bar and Reserve bar 2 and install a 2750MVA series reactor | 30/09/2024
|  | CS-06984 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 033496-033496 | 1. At West Burton 400kV substation install a Power electronics-based power flow control device in the Keadby – West Burton 1 circuit. | 30/09/2024
|  | CS-06985 | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation | 100816-201651 | 1. Hotwire the 2x500mm2 Rubus sections of the Cottam – Grendon 400kV circuit for operation at 90°C | 30/09/2024
Wakeleys BESS | PRO-003921 | CS-09098 | EPL NEWCO6 LIMITED | Wakeleys 400kV | 102643-205312 | Construction of a new 400kV AIS double busbar substation (Wakeleys 400kV) between Enderby 400kV – Patford Bridge 400kV substations, comprising of 2 feeder bays and 1 bus coupler bay. | 30/10/2033
|  | CS-09099 | EPL NEWCO6 LIMITED | Wakeleys 400kV | 102643-205313 | Provide a single turn in of the 400kV OHL circuit 1 between Enderby 400kV – Patford Bridge 400kV–East Claydon 400kV substations to the Wakeleys 400kV substation. | 30/10/2033
|  | CS-09101 | EPL NEWCO6 LIMITED | Wakeleys 400kV | 102643-205315 | Works to facilitate the Category 4 Operational Tripping Scheme as described in Appendix F3 of the Bilateral Connection Agreement. | 30/10/2033
|  | CS-09100 | EPL NEWCO6 LIMITED | Wakeleys 400kV | 102643-205314 | Extend Wakeleys 400kV substation main and reserve 1 busbar for the provision of one User bay. | 30/10/2033
Walpole | PRO-001114 | CS-05219 | PIVOTED POWER LLP | Walpole 400kV Substation | 100248 – 200635 | 1. Install a tertiary cable box or bushing on SGT5. 2.Install a 13kV cable (if required) from tertiary cable box or bushing to earthing transformer. 3.Install an earthing transformer. 4.Install 13kV Disconnector connecting the tertiary connection to Connection Assets. | 31/10/2022
Walpole 1 (Tertiary) | PRO-000556 | CS-06986 | WALPOLE GREEN LIMITED | Walpole 400kV Substation | 100572-201217 | 1. Install a tertiary cable box or bushings on SGT 4 at Walpole 400/132kV substation. 2. Install a 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. 5. Install an auto-close scheme on the section breakers at Walpole 132kV substation to allow a solid running arrangement to be automatically established post fault. | 01/05/2023
Walpole 2 (tertiary) | PRO-000505 | CS-06141 | ENSO GREEN HOLDINGS R LIMITED | Walpole 400kV Substation | 100648-201327 | Install earthing transformer on 13kV tertiary connection Install 13kV cable connecting earthing transformer to the disconnecting circuit breaker. Install a 72.5kV, 40kA-rated disconnecting circuit breaker to the connection assets for the User’s connection. Install an auto-close scheme on the section circuit breakers at Walpole 132kV substation, to allow a solid running arrangement to established automatically, post-fault. --- 1. Extension of Walpole 132kV main and reserve bus bar to accommodate user’s generator bay 2. Install an auto-close scheme on the section breakers at Walpole 132kV substation to allow a solid running arrangement to be automatically established post fault. | 31/10/2024
Walpole Grid Services Facility | PRO-003728 | CS-08792 | Conrad (Walpole) Limited | Walpole 400kV Substation | 102332-204492 | Extension to MBB1 adjacent to SGT5 to provide a suitable connection point. Associated Protection & Control. | 30/05/2025
Waltham Cross BESS | PRO-002070 | CS-08658 | ENSO GREEN HOLDINGS LIMITED | Waltham Cross GSP | 102534-205137 | Extend the 400kV substation busbar for an additional bay Database update for generator bay Busbar Protection | 29/09/2028
|  | CS-08657 | ENSO GREEN HOLDINGS LIMITED | Waltham Cross GSP | 101786-203725 | Construction of new Waltham Cross 400kV GIS Substation | 29/09/2028
|  | CS-08659 | ENSO GREEN HOLDINGS LIMITED | Waltham Cross GSP | 021742-021742 | Waltham Cross – Hackney 275kV to 400kV uprating | 29/09/2028
|  | CS-08660 | ENSO GREEN HOLDINGS LIMITED | Waltham Cross GSP | 033305-033305 | Uprate the ELST4A – SUND4 400kV circuit to achieve 1339 MVA pre-fault summer rating and 1676MVA post-fault winter rating | 29/09/2028
|  | CS-08661 | ENSO GREEN HOLDINGS LIMITED | Waltham Cross GSP | 101248-202488 | The circuit running from Pelham to Wymondley (PELH4 – WYMO4-1) will also be reconductored with 3 x 700mm2 conductor rating 2790MVA, 75˚C for pre-fault summer rating The circuit running from Pelham to Wymondley (PELH4 – WYMO4-1_a) will also be reconductored with 3 x 700mm2 conductor rating 3160MVA, 90˚C for pre-fault summer rating The circuit running from Sundon to Wymondley (SUND4 – WYMO4-1) will also be reconductored with 3 x 700mm2 conductor rating 3160MVA, 90˚C for pre-fault summer rating | 29/09/2028
|  | CS-08662 | ENSO GREEN HOLDINGS LIMITED | Waltham Cross GSP | 101786-203721 | At Pelham 400 kV Substation: Install 3000MVA QBs on the (Pelham to Rye House 1&2 circuits (PELH4-1 - RYEH4A and PELH4-2 - RYEH4B circuits) | 29/09/2028
|  | CS-09084 | ENSO GREEN HOLDINGS LIMITED | Waltham Cross GSP | 101916-203913 | 1. Install a tertiary cable box or bushings on the SGT1A 2. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to User Assets. | 29/09/2028
Warley | PRO-001113 | CS-06987 | WARLEY BATTERY STORAGE | Warley 275kV Substation | 100307-200735 | 1. Site extension to facilitate the transmission works. 2.Install a tertiary cable box or bushings on the SGT 4. 3. Install 13kV Cable (if required) from tertiary cable box or bushings to the earthing transformer. 4. Install an earthing transformer. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 30/06/2024
Warley (tertiary) | PRO-000555 | CS-06142 | WARLEY GREEN LIMITED | Warley 275kV Substation | 100654-201335 | Install earthing transformer on 13kV tertiary connection. Install 13kV cable connecting earthing transformer to the disconnecting circuit breaker. Install a 72.5kV, 40kA-rated disconnecting circuit breaker to the connection assets for the User’s connection. | 31/07/2023
Warley 2 | PRO-001848 | CS-07250 | CSE26 LIMITED | Warley 275kV Substation | 101659-203307 | 1. Extend the existing Warley 275kV substation land boundary 2. Design and rebuild existing Warley 275kV four switch mesh corner substation into double bus bar substation to accommodate four overhead line feeder bays, two busbar coupler bays, two busbar section bays and four Supergrid transformer bays | 31/10/2029
Warley Battery Energy Storage | PRO-002321 | CS-08585 | ABBEY PROPERTIES CAMBRIDGESHIRE LIMITED | Warley 275kV Substation | 101659-203313 | Reconductoring the existing 2x400mm2 conductor on the Tilbury- Warley double circuit with 2x500mm2 conductor to achieve a pre- Fault summer rating of 1120MVA | 31/10/2029
|  | CS-08583 | ABBEY PROPERTIES CAMBRIDGESHIRE LIMITED | Warley 275kV Substation | 101659-203307 | 1. Extend the existing Warley 275kV substation land boundary 2. Design and rebuild existing Warley 275kV four switch mesh corner substation into double bus bar substation to accommodate four overhead line feeder bays, two busbar coupler bays, two busbar section bays and four Supergrid transformer bays | 31/10/2029
|  | CS-08584 | ABBEY PROPERTIES CAMBRIDGESHIRE LIMITED | Warley 275kV Substation | 101868-203835 | Provision for accommodating the User’s bay in the rebuilt Warley 275kV double busbar substation | 31/10/2029
|  | CS-08586 | ABBEY PROPERTIES CAMBRIDGESHIRE LIMITED | Warley 275kV Substation | 100884-201776 | Reconductor Rayleigh Main – Tilbury & Coryton South-Tilbury 400 kV circuit to achieve a minimum rating of 3000 MVA summer pre-fault. | 31/10/2029
Waternish Wind Farm Substaion | PRO-002295 | CS-09314 | WIND DEVELOPMENT HOLDINGS LIMITED | Waternish Wind Farm 12KV Substation | Feeder Bay - Waternish WF | Install a new 132kV double busbar feeder bay at Edinbane collector switching station. Construct approximately 13.1km of single circuit 132kV from the Waternish Wind Farm substation to the Edinbane Collector Switching Station. The new 132kV single circuit will comprise of 11.7km single 132kV overhead line with 2x 500m runs of UGC. The end of this line will be coupled to a new underground cable (0.5km approximately) that will connect the new single circuit 132kV overhead line to a new bay on the Edinbane collector switching station 132kV busbars, via the required 132kV switchgear. | 30/04/2034
|  | CS-09315 | WIND DEVELOPMENT HOLDINGS LIMITED | Waternish Wind Farm 12KV Substation | SHET-RI-061 | Construct a new 132kV circuit from Fort Augustus to Ardmore. The circuit is proposed as double circuit steel structure from Fort Augustus to Broadford, Single Circuit Steel Structure from Broadford to Edinbane and single circuit wood pole structure from Edinbane to Ardmore (approximately 160km Fort Augustus 132kV substation to Ardmore 132kV substation). | 30/04/2034
|  | CS-09316 | WIND DEVELOPMENT HOLDINGS LIMITED | Waternish Wind Farm 12KV Substation | SHET-RI-195 | Edinbane to Grudie Bridge 220kV Subsea HVAC Cable Link - Establish a 220kV HVAC circuit over a distance of approximately 117km between the 132kV GIS substation at Edinbane on Skye and a new 132kV Double Busbar substation in the vicinity of Grudie Bridge. The HVAC circuit comprises of approximately 62km of land cable and 55km of subsea cable. Voltage Compensation devices will be installed at both cable ends within the substation compounds at Edinbane and Grudie Bridge. Rebuild approximately 5km of the existing 132kV overhead line circuits between the proposed new Grudie Bridge substation and Corriemoillie substation. | 30/04/2034
Weirs Drove | PRO-001655 | CS-06988 | EAST ANGLIA GRID STORAGE ONE LIMITED | Burwell Main 400kV Substation | 101462-202902 | Following the conversion of Burwell 400kV substation into a double busbar arrangement, extend main busbar 1 and reserve busbar 1 to accommodate the installation of a new 400/132kV 240MVA rated SGT. | 31/10/2028
|  | CS-06989 | EAST ANGLIA GRID STORAGE ONE LIMITED | Burwell Main 400kV Substation | 101462-202901 | 1. Install and commission a new 400kV Supergrid Transformer (SGT) bay at Burwell 400kV substation. 2. Install and commission switchgear at Burwell to include SGT HV and LV circuit breakers and associated bay assets. 3. Install and commission a new 400/132kV 240MVA rated SGT. 4. Install 132kV cabling from the LV side of the SGT to the relevant bay at the User 132kV substation for each SGT circuit. 5. Install HAM (High Accuracy Metering) unit and associated metering equipment in accordance with the Metering Code of Practice. | 31/10/2028
WELBAR ENERGY STORAGE | PRO-001735 | CS-04610 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101355-202675 | Extension of the existing Hams Hall 400kV substation Main and Reserve Busbars to accommodate the User’s bay. | 30/10/2026
|  | CS-06991 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101465-202905 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Walham 400 kV circuit with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2026
|  | CS-06992 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101329-202649 | Hotwire Enderby – Ratcliffe 400kV circuits 1 and 2 to 65 deg. C to achieve a pre-fault summer rating of 2260MVA. | 30/10/2026
|  | CS-06993 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 1820 MVA. | 30/10/2026
|  | CS-06994 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101466-202906 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Daines 1 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2026
|  | CS-06995 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2026
|  | CS-06996 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101468-202908 | Reconductor the existing 2x570mm2 conductor on the Daines-Macclesfield 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2026
|  | CS-06997 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101284-202534 | Reconductor the existing 2x570mm2 conductor on the IronBridge- Legacy 2 and IronBridge Shrewsbury-Legacy 400 kV circuits with 2x570mm2 conductor at 90 deg. C to achieve a pre fault summer rating of 2490 MVA | 30/10/2026
|  | CS-06998 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101278-202528 | Reconductor the Legacy legs of both Connah’s Quay – Legacy – Trawsfynydd 1 and 2 circuits with 3x700mm2 conductor. | 30/10/2026
|  | CS-06999 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 032030-032030 | Replace the existing Quadrature Boosters at Legacy with a new 2750MVA unit. | 30/10/2026
|  | CS-07000 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 101279-202529 | Reconductor the Connahs Quay legs of both Connahs Quay-Legacy-Trawsfynydd 1 and 2 circuits with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2026
|  | CS-06990 | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2026
West Andershaw Wind Farm | PRO-002584 | CS-09544 | WEST ANDERSHAW WIND FARM LIMITED | West Andershaw 132kV Substation | West Andershaw WF H1 Works | Installation of a 132kV line disconnector at West Andershaw 132kV substation | 30/04/2030
|  | CS-09546 | WEST ANDERSHAW WIND FARM LIMITED | West Andershaw 132kV Substation | SPT-RI-3060 | Redshaw 132kV “B” Board - Establish a new 132kV double busbar substation, indicatively named Redshaw 132kV “B” board at the new Redshaw 400/132kV substation. The location of the SPT’s new 400kV substation (which this 132kV double busbar site will connect into) will be connected in the existing ZV Route corridor (STHA-ELVA / COAL-ELVA) as well as facilitate the new double circuit from Glenmuckloch under SPT-RI-236. The 400kV substation at Redshaw is being constructed under SPT-RI-2060. The 132kV double busbar substation to be established here will also require installation of two 400/132kV 360MVA transformers. (SPT-RI3060) | 30/04/2030
|  | CS-09545 | WEST ANDERSHAW WIND FARM LIMITED | West Andershaw 132kV Substation | SPT-RI-2060 | Redshaw 400kV Substation - Creation of a new 400kV substation connecting into ZV Route. This will tie into the Strathaven and Coalburn circuits coming from the north, the two Elvanfoot circuits heading south and the new double circuit coming across from Glenmuckloch under SPT-RI-236. (SPT-RI-2060) | 30/04/2030
West Boldon GSP (DNO) | PRO-002618 | CS-08509 | NORTHERN POWERGRID (NORTHEAST) PLC | West Boldon 275/66kV Substation | 101539-203054 | At West Boldon 275kV substation: Replace the line disconnectors, busbars, busbar disconnectors and associated CT’s with 3150A rated apparatus. (101539-203054) | 15/12/2023
|  | CS-08508 | NORTHERN POWERGRID (NORTHEAST) PLC | West Boldon 275/66kV Substation | 102315-204538 | Replacement of the CB S10 and S20 at West Boldon 275kV substation with 40kA nominal rating breaker. | 15/12/2023
West Burton Solar Project | PRO-000561 | CS-06840 | WEST BURTON SOLAR PROJECT LIMITED | West Burton 400kV Substation | 100681-201437 | 1. At West Burton 400kV, facilitate the installation of 400kV Gas Insulated Switchgear (User Works), adjacent to banking substation 6 (X690) bay. 2. Modification to the busbar protection and substation control system at West Burton 400kV. 3. Replace circuit breaker X210 at West Burton 400kV with a new 63kA rated circuit breaker | 30/11/2028
|  | CS-06841 | WEST BURTON SOLAR PROJECT LIMITED | West Burton 400kV Substation | 100591-201213 | Reconductor Ratcliffe – Staythorpe 400kV circuit; reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 2780MVA | 30/11/2028
|  | CS-06842 | WEST BURTON SOLAR PROJECT LIMITED | West Burton 400kV Substation | 100459-201024 | Reconductor the existing 2 x 500mm2 conductor on the High Marnham – Stoke Bardolph 400kV circuit with 2 x 620mm2 conductor to provide a post-fault summer rating of 2780MVA | 30/11/2028
|  | CS-06843 | WEST BURTON SOLAR PROJECT LIMITED | West Burton 400kV Substation | 100590-201212 | Reconductor the existing 2 x 500mm2 conductor on the Ratcliffe – Stoke Bardolph 400kV circuit with 2 x 620mm2 conductor and uprate the cable section to provide a post fault summer rating of 2780MVA | 30/11/2028
West Grimsby Farm (DNO) | PRO-002619 | CS-08519 | NORTHERN POWERGRID (YORKSHIRE) PLC | Grimsby West GSP | 102718-205492 | 400kV busbar extension to accommodate new SGT bay Busbar and C Modifications SCS modifications. | 31/10/2035
|  | CS-08517 | NORTHERN POWERGRID (YORKSHIRE) PLC | Grimsby West GSP | 100944-201880 | Modifications to Grimsby West substation for the new Lincolnshire Green 400kV OHL | 31/10/2035
|  | CS-08518 | NORTHERN POWERGRID (YORKSHIRE) PLC | Grimsby West GSP | 101669-203323 | Infrastructure works at the Grimsby West 400kV substation for the addition of an SGT transformer to the 132kV substations to enable a customer connection. | 31/10/2035
West Haddon | PRO-003820 | CS-08923 | SSE DE SOLAR HOLDCO LIMITED | West Haddon 400kV Substation | 102603-205227 | 1. Construct a new 400kV double busbar substation. 2. Provide a single turn in of the East Claydon-Partford Bridge- Enderby 400kV circuit 1 for the new substation (Name: West Haddon 400 kV; TBC). | 01/10/2039
West Saval Battery Storage | PRO-003510 | CS-08444 | West Saval Battery Storage Ltd | West Saval Substation 132 kV | SHET-RI-058 - Beauly – Loch Buidhe (Cambusmore) 132 kV | Beauly – Loch Buidhe 400kV OHL Reinforcement - This project is to replace the existing Beauly - Loch Buidhe 132kV double circuit OHL with a higher capacity 400kV double circuit OHL. (SHET-RI-058 | 31/10/2030
|  | CS-08445 | West Saval Battery Storage Ltd | West Saval Substation 132 kV | SHET-RI-194 | Beauly 2 400 kV substation - Construct a new 400kV double busbar at Beauly 2 400kV switching station. The 400kV double busbar is to comprise of one bus section breaker and two bus couplers. Allowance should be made for a total of 14 feeder bays (Include space provision only for a further four fully selectable busbar feeder bays). | 31/10/2030
|  | CS-08446 | West Saval Battery Storage Ltd | West Saval Substation 132 kV | SHET-RI-200 | Loch Buidhe 400/275kV substation - Establish a new 400kV substation adjacent to the existing 275kV Loch Buidhe substation. The new 400kV substation will have a double busbar arrangement complete with bus section, two bus-couplers, two SGT circuit breaker bays and two-line connected circuit breakers bays. Install 2 x 1200MVA, 400/275kV supergrid transformers (SGT1 and SGT2). | 31/10/2030
West Torrisdale | PRO-000944 | CS-06255 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-013 | North Argyll (Dalmally) - Establish a new 275/132 kV Substation (Ardbrecknish) near the existingInveraray/Taynuilt 132 kV line route with two 360 MVA 275/132 kV transformers.Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275 kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 30/04/2027
|  | CS-06256 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-050b | Port Ann - Crossaig Reinforcement - Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 48km of double circuit OHL between Port Ann and Crossaig. The towers will be built for 275kV operation, but initially operated at 132kV. | 30/04/2027
|  | CS-06257 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-050a | Inveraray – Crossaig 132kV Reinforcement - Reinforce the 132kV Transmission network in the Kintyre Peninsula. Rebuild approximately 35km of double circuit OHL between Inveraray and Port Ann. The towers will be built for 275kV operation, but initially operated at 132kV. (SHET-RI-050a) | 30/04/2027
|  | CS-06258 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-107 | North Argyll Inveraray 132kV Reinforcement - Reinforce the double circuit overhead line between North Argyll 275/132kV substation (established as part of SHET-RI-013) and Inveraray 132kV witching station. This reinforced circuit will connect to the double circuit overhead line from Crossaig (rebuilt as part of SHET-RI-050) approximately 2.8km away from Inveraray. The overhead line from Crossaig to North Argyll will now bypass Inveraray switching station. Crossaig substation will be reconfigured to split the onshore Argyll and Kintyre network from the Kintyre-Hunterston subsea cables. | 30/04/2027
|  | CS-06259 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-130a | Craig Murrail – Crossaig 275kV | 30/04/2027
|  | CS-06260 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SHET-RI-130b | Reinforce the network in the Argyll and Kintyre network to enable 275kV operation of the network from Craig Murrail substation to a new double busbar substation to be established at Crossaig. This project will also radialise the Argyll and Kintyre network, with a normally open point established between the existing Crossaig double busbar and the new Crossaig double busbar. | 30/04/2027
|  | CS-06272 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | West Torrisdale Wind Farm H1 works | 1) replace a Carradale GSP existing 2 x 60MVA 132/33kV Transformers with higher rated 2 x 120MVA 132/33kV 2) replace existing 33kV transformer circuit breaker and cabling | 30/04/2027
|  | CS-07393 | ESB ASSET DEVELOPMENT UK LIMITED | Carradale 1 GSP | SPT-RI-028 | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | 30/04/2027
West Weybridge | PRO-001108 | CS-05218 | PIVOTED POWER LLP | West Weybridge 275kV Substation | NGET-R1-100279-200779(Infra) | 1. Install earthing transformer on the 13kV Tertiary connection 2. Install a 13kV motorised switch-disconnector connecting tertiary to connection assets for the User’s connection | 31/10/2027
West Weybridge | PRO-004324 | CS-09870 | EL (WEST WEYBRIDGE) LIMITED | West Weybridge 275kV Substation | 100955-201904 | 1. Install a tertiary cable box or bushings on SGT 2. 2. Install a 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 31/10/2027
West Weybridge (Tertiary) | PRO-000552 | CS-07001 | ENSO GREEN HOLDINGS LIMITED | West Weybridge 275kV Substation | 100955-201904 | 1. Install a tertiary cable box or bushings on SGT 2. 2. Install a 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 31/10/2025
Wether Hill | PRO-001527 | CS-04352 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-2094 | Quantans Hill to Holmhill 132kV Circuit – At the proposed Quantans Hill wind farm site establish a 132kV substation and establish a 132kV busbar to which a 132kV line isolator is connected. Install around 6km of wood pole overhead line with HTLS conductor to connect Quantans Hill substation to Holmhill substation. At Holmhill substation install a 132kV circuit breaker to connect the OHL. | 01/12/2028
|  | CS-04353 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-1507 | Holm Hill 132kV substation - At an appropriate point next to the DE route establish a 132kV substation (Holmhill 132kV substation) by teeing into the proposed future New Cumnock to Glenlee 132kV circuit. The substation will consist of a 132kV busbar to which wind farm circuits will connect to. | 01/12/2028
|  | CS-04354 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 01/12/2028
|  | CS-04355 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 01/12/2028
|  | CS-04356 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 01/12/2028
|  | CS-04357 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 01/12/2028
|  | CS-04358 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 01/12/2028
|  | CS-04359 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation | Wether Hill H1 Works | At Wether Hill substation install one 132kV line isolator. Installation of around 11km of wood pole OHL with Poplar conductor between Wether Hill substation and Quantans Hill substation. At Quantans Hill extend the substation to install 132kV circuit breaker to connect the OHL. | 01/12/2028
White Cairns BESS | PRO-004219 | CS-09403 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | White Cairns BESS - Comms | Additionally, fibre optic comms will be installed between Newmachar 275kV substation and the User's substation. | 31/10/2033
|  | CS-09398 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 31/10/2033
|  | CS-09396 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | SHET-RI-25c | 0 | 31/10/2033
|  | CS-09397 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | SHET-RI-25d | 0 | 31/10/2033
|  | CS-09402 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | White Cairns BESS - Disconnector | A 275kV line disconnector will be installed at the User’s substation | 31/10/2033
|  | CS-09399 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | SHET-RI-215 | New Aberdeen 275kV Substation (Newmachar) – New 275kV double busbar substation in the Aberdeen area. The 275kV circuits between Peterhead/Persley/Kintore (VX2/VP/PX) will connect in/out of this new 275kV substation | 31/10/2033
|  | CS-09393 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2033
|  | CS-09395 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | SHET-RI-25b | 0 | 31/10/2033
|  | CS-09401 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | White Cairns BESS - 275kV Circuit | Approximately 5.2km of 275kV single circuit overhead line and 1km of 275kV underground cable will also be required as part of this new connection | 31/10/2033
|  | CS-09394 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | SHET-RI-25a | 0 | 31/10/2033
|  | CS-09400 | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV | White Cairns BESS - 275kV Switch Bay | Installation of a 275kV double busbar switch bay at a new 275kV substation | 31/10/2033
Whitegate Tertiary Connection | PRO-000512 | CS-07002 | HD144WHI LTD | Whitegate 275kV Substation | 10079-201575 | 1. Install a tertiary cable box or bushings on SGT1B. 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer at the 13kV side 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets | 30/06/2024
Whitehill Battery Storage | PRO-002093 | CS-07547 | Whitehill Battery Storage Ltd | Easterhouse 275kV | 275kV Disconnector - Whitehill Battery | At Easterhouse 275kV substation, installation of one new 275kV disconnector and associated equipment. | 31/10/2026
|  | CS-07548 | Whitehill Battery Storage Ltd | Easterhouse 275kV | SPT-RI-2436 | Easterhouse 275kV fault level mitigation works - To allow a new generation / battery storage connection at Easterhouse 275kV the short circuit rating of Easterhouse 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of all equipment and structures to withstand a fault current of 40kA | 31/10/2026
WHITEHILL BESS | PRO-004639 | CS-09756 | GPC 1210 Ltd | Whitehill BESS 275/132kV Substation | SPT-RI-1968 | Neilston 275kV uprating to 40kA - To allow the connection of the second Synchronous Compensator at Neilston 400kV the short circuit rating of Neilston 275kV need to increase from current design specification of 31.5kA to 40kA. This will include the assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. (SPT-RI-1968) | 01/10/2029
|  | CS-09757 | GPC 1210 Ltd | Whitehill BESS 275/132kV Substation | SPT-RI-2085 | Windyhill – Lambhill – Denny North 400kV reinforcement – Establish 400kV infrastructure on from Denny North following the East Coast 400kV onshore incremental (ECUP) reinforcement, Eastern HVDC link from Peterhead (E4DC/D2/D3) and from Torness (E2DC/D2/D3). The scope of this TORI is, at this time, aligned with the ‘DLUP’ option submitted to the 2020/21 Network Options Assessment (NOA) process. The project will establish a 400kV circuit between Denny North and Windyhill, via Lambhill, on the existing 275kV circuit. | 01/10/2029
|  | CS-09758 | GPC 1210 Ltd | Whitehill BESS 275/132kV Substation | SPT-RI-2791 | 4. Windyhill 275kV Substation Modernisation – The scope of this TORI is reflective of the ongoing modernisation works at Windyhill 275kV substation identified within the RIIO T2 Price Control. These works shall replace the existing 12 bay double busbar AIS substation with a new 15 bay double busbar GIS substation. | 01/10/2029
|  | CS-09755 | GPC 1210 Ltd | Whitehill BESS 275/132kV Substation | SPT-RI-2625 | Windyhill 275kV Fault Level Uprating - To allow additional generation connection in the area, the short circuit rating of Windyhill 275kV is required to ensure specification of 40kA. This will include the survey assessment and uprating where necessary of equipment and structures to withstand a fault current of 40kA. | 01/10/2029
Whitelaw Brae BESS | PRO-003247 | CS-09618 | BUK23 Limited | Whitelaw Brae B 33kV Substation | SPT-RI-3189 | Clyde South to Whitelaw Brae 33kV Works - Following further connection applications in this area it is required to establish a shared 33kV circuit from Clyde South substation to the Whitelaw Brae substation. | 31/07/2026
Whiteleigh Farm | PRO-002385 | CS-08320 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101501-202957 | Reconductor the Hinkley point - Sandford CSE circuit 1 (only ZG section) in order to achieve a summer post fault rating of 2850MVA | 06/12/2036
|  | CS-08312 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101363-202683 | Reconductoring of the Alverdiscott - Indian Queens circuit in order to achieve a post fault Summer rating of 1650MVA. | 06/12/2036
|  | CS-08311 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 102169-204376 | Replacement, or modification, of existing towers and associated OHL works to facilitate a full turn in of the Alverdiscott – Indian Queens 2 overhead line circuit. Works required to establish a new 400kV substation compound, including the installation of substation earth mat, LVAC supplies, substation fencing, groundworks and associated infrastructure. Construction of 400kV Busbar to accommodate the OHL turn-in and the Users Generator Bay. Local works to facilitate the extension of the Operational Tripping Scheme | 06/12/2036
|  | CS-08315 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101387-202717 | Reconfigure the Nursling 400kV substation to a double busbar arrangement, consisting of 6 feeder bays, 3 SGT bays, 2 coupler bays and a section bay. | 06/12/2036
|  | CS-08316 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101387-202718 | At Nursling 400k substation turn in the double circuits from both Lovedean and Mannington, as well as the single circuits from Fawley and Marchwood. | 06/12/2036
|  | CS-08318 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101497-202952 | Reconductor the single circuit between Melksham - Seabank (route 4YX and 2VL) in order to achieve a pre fault summer rating of 2500MVA and post fault summer rating of 3210MVA. | 06/12/2036
|  | CS-08325 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101620-203254 | Reconductoring of the Landulph – Indian Queens 2 circuit to achieve a post-fault Summer rating of 2300MVA. | 06/12/2036
|  | CS-08326 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101499-202954 | Following the double turn in at Alverdiscott 400kV substation, reconductor the circuit between Alverdiscott 400kV and Taunton 400kV to triple Auriacuria 3 x 700mm2 at 90 degrees to achieve a summer pre-fault rating of 3000MVA | 06/12/2036
|  | CS-08313 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 100480-201051 | Uprate the cable section of the Seabank -Whitson section of the three-ended Seabank -Whitson - Cilfynydd circuit to a pre-fault rating of 1800MVA | 06/12/2036
|  | CS-08314 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 033769-033769 | Reconductor the Taunton - Shurton 400kV circuits to achieve a 3100MVA post fault winter rating. | 06/12/2036
|  | CS-08321 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101501-202958 | Reconductor the Hinkley point - Sandford CSE circuit 2 (only ZG section) in order to achieve a summer post fault rating of 2850MVA. | 06/12/2036
|  | CS-08319 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101833-203761 | Uprate the Chickerel - Mannington double circuit (NASP Code: A851 and A830) to summer pre fault rating of 2200MVA. | 06/12/2036
|  | CS-08317 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101498-202953 | Uprate the double circuit between the Exeter - Axminster – Chickerell substations, to achieve at least a post fault summer rating of 2420MVA | 06/12/2036
|  | CS-08322 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101500-202955 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 1 in order to achieve a summer post fault rating of 2850MVA | 06/12/2036
|  | CS-08323 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 101500-202956 | Reconductor the Shurton and Melksham legs of the Shurton - Bridgewater -Melksham circuit 2 in order to achieve a summer post fault rating of 2850MVA | 06/12/2036
|  | CS-08324 | Greenswitch Capital Limited | Pyworthy 400kV Substation | 102057-204227 | A new 400kV network reinforcement between Devon and Hampshire to increase boundary capacity and accommodate power export from the South West Peninsula | 06/12/2036
Whitson | PRO-001061 | CS-05217 | PIVOTED POWER LLP | Whitson 275kV Substation | NGET-RI-100279-200767(Infra) | I. Extension of 33kV busbar and cable to 33kv disconnector to accommodate 33kV generator bay 2. Install 33kV disconnector 3. Replace the Quad Boosters1and 2 at Whitson for larger units 4. Replacement of Whitson SGT5 for a larger rated unit | 31/10/2026
Willington | PRO-000326 | CS-05216 | PIVOTED POWER LLP | Willington East 400kV Substation | 10756-201150 | 1. Make connections on the SGT 6. 2. Condition assessment of 13kV cable and other assets to confirm suitability for reuse. 3. Install earthing transformer on 13kV Tertiary connection. 4. Install 13kV Cable (if required) from 13kV Tertiary connection to the13kV Disconnector. 5. Install a 13kV Disconnector at the 13kV side connecting tertiary to Connection Assets. | 30/06/2026
Willington | PRO-002257 | CS-07528 | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation | 101879-203856 | Uprate the Ratcliffe 400kV to Willington East 400kV circuit #1 (RATS4- WILE4-1) to summer pre-fault rating 1680MVA | 30/10/2029
|  | CS-07535 | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation | 101889-203868 | Reconductor the East Claydon legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 1820MVA | 30/10/2029
|  | CS-07529 | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation | 101880-203857 | Uprate the Ratcliffe 400kV to Willington East 400kV circuit #2 (RATS4- WILE4-2) to summer pre-fault rating 1680MVA | 30/10/2029
|  | CS-07527 | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation | 101878-203855 | Extension of the existing Willington East 400kV substation Main and Reserve Busbars to accommodate the User’s bay. Swap the bays with Coupler bay for ease of connection for Customer | 30/10/2029
|  | CS-07534 | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation | 101884-203860 | Reconductor the Enderby legs of both East Claydon– Enderby – Patford Bridge 1 and 2 circuits to achieve a pre-fault summer rating of 1860MVA | 30/10/2029
|  | CS-07533 | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation | 101329-202649 | Hotwire Enderby – Ratcliffe 400kV circuits 1 and 2 to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 30/10/2029
|  | CS-07536 | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation | 101891-203873 | Uprate the circuit Drakelow 400kV Willington East 400kV to achieve a summer pre-fault rating of 1820MVA | 30/10/2029
|  | CS-07530 | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2029
|  | CS-07531 | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation | 101467-202907 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Hams Hall 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 1820 MVA. | 30/10/2029
|  | CS-07532 | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2029
Willington East 1 (Tertiary) | PRO-000551 | CS-07003 | ENSO GREEN HOLDINGS LIMITED | Willington East 400kV Substation | 100943-201878 | 1. Install a tertiary cable box or bushings on the SGT7. 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV disconnector at the 13kV side connecting tertiary to connection assets. | 30/06/2025
Willington East 2 (Tertiary) | PRO-000548 | CS-07004 | ENSO GREEN HOLDINGS LIMITED | Willington East 400kV Substation | 100945-201885 | 1. Install a tertiary cable box or bushings on the SGT2. 2. Install 13kV cable (if required) from tertiary cable box or bushings to the earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV disconnector at the 13kV side connecting tertiary to connection assets. | 31/10/2025
Willington Energy Park | PRO-001964 | CS-07116 | RNA-ENERGY LTD | Willington 400kV Substation | 101778-203570 | Extension of the existing Willington East 400kV substation main and reserve busbars to accommodate the User’s bay | 30/03/2028
|  | CS-07117 | RNA-ENERGY LTD | Willington 400kV Substation | 100477-201048 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4- WILE4-2) to summer pre-fault rating 1400MVA | 30/03/2028
|  | CS-07118 | RNA-ENERGY LTD | Willington 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/03/2028
|  | CS-07119 | RNA-ENERGY LTD | Willington 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/03/2028
|  | CS-07120 | RNA-ENERGY LTD | Willington 400kV Substation | 101329-202649 | Hotwire Enderby – Ratcliffe 400kV circuits 1 and 2 to 75 deg. C to achieve a pre-fault summer rating of 2500MVA. | 30/03/2028
Willington Green Energy Centre | PRO-001797 | CS-07038 | WILLINGTON GREEN ENERGY LIMITED | Willington 400kV Substation | 101595-203210 | Substation Busbar extension works to facilitate the use of the existing generator bays (for the decommissioned generators) for connection of Willington Green Energy | 30/10/2026
|  | CS-07039 | WILLINGTON GREEN ENERGY LIMITED | Willington 400kV Substation | 100477-201048 | Uprate the Ratcliffe 400kV -to- Willington East 400kV circuit #2 (RATS4- WILE4-2) to summer pre-fault rating 1400MVA | 30/10/2026
|  | CS-07040 | WILLINGTON GREEN ENERGY LIMITED | Willington 400kV Substation | 100426-200972 | Reconductor the existing 2x500mm2 conductor on the Feckenham-Minety 400 kV circuit with 2x620mm2 conductor to achieve a pre fault summer rating of 2490 MVA. | 30/10/2026
|  | CS-07041 | WILLINGTON GREEN ENERGY LIMITED | Willington 400kV Substation | 032021-032021 | Reconductor the existing 2x570mm2 conductor on the Cellarhead-Drakelow 1 and 2 400 kV circuits with 2x620mm2 conductor to achieve a pre-fault Summer rating of 2490 MVA. | 30/10/2026
|  | CS-07042 | WILLINGTON GREEN ENERGY LIMITED | Willington 400kV Substation | 033512-033512 | Uprate Keadby - West burton 1 circuit to provide a post fault winter rating of 3420MVA | 30/10/2026
WindyHill BESS2 Facility | PRO-002032 | CS-07272 | ENERGYGRIDPOWER LTD | Windy Hill Grid 132kV Substation | SPT-RI-148 | Install an auto-close scheme across the three 275/132kV supergrid transformers at WindyHill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. | 30/09/2024
|  | CS-07273 | ENERGYGRIDPOWER LTD | Windy Hill Grid 132kV Substation |  | FALSE | 30/09/2024
WindyHill Energy Storage Facility | PRO-001696 | CS-04503 | ENERGYGRIDPOWER LTD | Windy Hill Grid 132kV Substation | SPT-RI-2148 | WindyHill SGT Auto-close scheme - Installation of an auto-close scheme across the three 275/132kV supergrid transformers at Windyhill 132kV substation. This is because an SGT will need to sit on open standby to maintain the fault level rating on the switchgear. This auto-close scheme shall close back in the open standby transformer following the loss of an in-service unit. It is proposed to run SGT3 on open standby and for the loss/opening of SGT1 (CB1380) or SGT2 (CB1480) an instruction shall be issued to close the SGT3 circuit breaker (CB1080) in order to keep two SGTs in service at all times. The scope of works also makes inclusion for the replacement of the SCADA/HMI system in order to facilitate the installation of this auto-close scheme | 30/07/2024
Windy Standard II (Brockloch Rig) Wind Farm | PRO-000233 | CS-06147 | BROCKLOCH RIG WINDFARM LIMITED | Dun Hill 132/33kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 30/06/2024
|  | CS-06148 | BROCKLOCH RIG WINDFARM LIMITED | Dun Hill 132/33kV Substation | SPT-RI-145 | Construction of Dun Hill 132/33kV Substation including three 33kV circuit breakers, two 132/33kV 90MVA transformers and 33kV switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 30/06/2024
|  | CS-06149 | BROCKLOCH RIG WINDFARM LIMITED | Dun Hill 132/33kV Substation | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 30/06/2024
Windy Standard III Wind Farm | PRO-000359 | CS-05433 | Brockloch Rig III Ltd | Dun Hill 132/33kV Substation | SPT-RI-173 | To enable the connection of generation around the Glenmuckloch area, the 132kV network need to be extended from Glenglass substation to Glenmuckloch. To achieve this it is proposed to build a new 132kV double circuit between Glenglass and Glenmuckloch. The project will mainly entail the extension of the proposed GIS substation at Glenglass to add two new bays to which the 132kV double circuit will connect, then construct around 10km of steel lattice towers to Glenmuckloch and at Glenmuckloch establish a 132kV double busbar collector substation to terminate the OHL double circuit. | 30/06/2024
|  | CS-05434 | Brockloch Rig III Ltd | Dun Hill 132/33kV Substation | SPT-RI-236 | Glenmuckloch to ZV route reinforcements - extends the 400kV network from the ZV route to Glenmuckloch collector substation. It is proposed to establish a new 400kV substation by turning in the ZV route into a new 400kV substation between Elvanfoot and Coalburn. From the new 400kV substation a new 400kV L8 overhead line will be established to a new 400kV substation at Glenmuckloch. Three 400/132kV 360MVA interbusing transformers will connect the 400kV to the 132kV collector substation at Glenmuckloch. | 30/06/2024
|  | CS-05435 | Brockloch Rig III Ltd | Dun Hill 132/33kV Substation | SPT-RI-302 | 8). Glenglass 132kV Substation - To enable the connection of generation in the Glenglass area and extend the 132kV network to Glenmuckloch a new 132kV substation is required in Glenglass. The new substation will be a double busbar 132kV GIS substation with a bus coupler and sized for eight feeder circuits. Also to maximise the network capabilities the 132kV circuits between Glenglass and Blackhill are limited by cables at Blackhill substation. These cables will need to be uprated to match the 132kV Blackhill to Glenglass OHL ratings. | 30/06/2024
|  | CS-06150 | Brockloch Rig III Ltd | Dun Hill 132/33kV Substation | SPT-RI-007 | New Cumnock 275/132kV Substation | 30/06/2024
|  | CS-06151 | Brockloch Rig III Ltd | Dun Hill 132/33kV Substation | SPT-RI-145 | Construction of Dun Hill 132/33kV Substation including three 33kV circuit breakers, two 132/33kV 90MVA transformers and 33kV switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 30/06/2024
|  | CS-06152 | Brockloch Rig III Ltd | Dun Hill 132/33kV Substation | SPT-RI-284 | Generation Export Management Scheme (GEMS) -The Generation Export Management Scheme (GEMS) is a load management system that protects the Relevant Transmission Licensee’s transmission network in south west Scotland against unacceptable overloads on transmission equipment under intact and depleted system conditions. The GEMS system will instruct directly connected and embedded generation to curtail their output to avoid the overloading of any transmission circuits. The order with which these generators are curtailed will be determined by the System Operator (SO) and GEMS system will receive the order list periodically from the SO. (SPTRI-284 | 30/06/2024
|  | CS-06153 | Brockloch Rig III Ltd | Dun Hill 132/33kV Substation | SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV New Cumnock Collector Substation, heading east, to 132kV Dun Hill Substation tee off. These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 30/06/2024
|  | CS-06154 | Brockloch Rig III Ltd | Dun Hill 132/33kV Substation | SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/06/2024
|  | CS-06155 | Brockloch Rig III Ltd | Dun Hill 132/33kV Substation | SPT-RI-143 | Kilmarnock South 275kV and 400kV Substations Uprating - The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. It is proposed to replace the switchgear with 3150Amp/1500MVA rated equipment to provide sufficient capacity for the generation in South West Scotland. Furthermore there are two 400/275kV 1000MVA auto wind transformers at the 400kV substation and to comply with NETS SQSS a third transformer is required to ensure that for N-1 conditions there are no restriction on the generation in South West Scotland. | 30/06/2024
Womblehill BESS Farm | PRO-002197 | CS-07978 | RE Projects Development Limited | Womblehill BESS Farm 132kV | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2029
|  | CS-07979 | RE Projects Development Limited | Womblehill BESS Farm 132kV | SHET-RI-025b & NGET-RI-30204 | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead and Drax | 31/10/2029
|  | CS-07982 | RE Projects Development Limited | Womblehill BESS Farm 132kV | SHET-RI-120 | Craigiebuckler – Tealing/Arbroath Tee 132kV Reconductoring - Reconductor the existing 132kV single circuit overhead line between Craigiebuckler substation and the Arbroath/Tealing Tee point. Both Fiddes GSP and Bridge of Dun GSP are connected to this single circuit. The circuit should be reconductored with a minimum summer pre-fault rating of 150MVA | 31/10/2029
|  | CS-07980 | RE Projects Development Limited | Womblehill BESS Farm 132kV | SHET-RI-025d | North East Reinforcement | 31/10/2029
|  | CS-07981 | RE Projects Development Limited | Womblehill BESS Farm 132kV | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2029
WORSET LANE BESS | PRO-003650 | CS-08578 | HARTFINDER ONE LIMITED | Hartmoor 275kV Substation | 102573-205181 | Hartmoor 275kV substation: extend mesh corner 4 and install a CB/DCB | 28/10/2033
Worset PV & BESS Park | PRO-001055 | CS-06156 | Worcestershire Solar 1 Limited | Hartmoor 275kV Substation | 100788-201592 | Reconfigure the bars around SGT2 and provide a banked 66kV User connection point consisting of a disconnector and cable sealing end at Hartmoor 275/66kV substation | 07/06/2024
Wright Street BESS | PRO-003083 | CS-08555 | P3P PARTNERS LLP | Braehead Park GSP | SPT-RI-243 - Devol Moor-Erskine-Braehead Park Circuit LMS | A Load Management Scheme (LMS) is required to manage connections in the Neilston – Devol Moor 132 kV group to prevent overloads on the Devol Moor-Erskine-Braehead Park Circuit. The overload will be removed by the LMS tripping the appropriate non-firm connections. | 16/07/2025
Wylfa Substation | PRO-000506 | CS-06157 | ENSO GREEN HOLDINGS LIMITED | Wylfa 132kV Substation | 100647-201326 | Provision of existing Skeleton bay to enable User to connect to that bay Substation control modification and bus bar protection | 31/10/2026
Wymondley | PRO-001245 | CS-05215 | PIVOTED POWER LLP | Wymondley 400kV Substation | 100589-201123 | 1. Install a tertiary cable box or bushing on the SGT 1. 2. Install 13kV Cable (if required) from tertiary cable box or bushings to earthing transformer. 3. Install an earthing transformer. 4. Install a 13kV Disconnector at the 13kV side connecting tertiary to User Assets. | 30/06/2025
| PRO-002187 | CS-08019 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 100708- 201475 | Post-completion of BTNO works, reconductor Bramford-Pelham 2 400kV circuits with 3 x700mm2 AAAC conductors to achieve a post-fault winter rating of 3820 MVA. | 31/10/2031
|  | CS-08012 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 030447-030447 | Transfer King’s Lynn B – Walpole 400kV circuit (Necton-Norwich- Walpole 400kV circuit 1) onto Main and Reserve bus section 2 at Walpole 400kV substation | 31/10/2031
|  | CS-08020 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 031867-031867 | New offshore HVDC link between Suffolk and Kent (NOA Code: SCD1) | 31/10/2031
|  | CS-08010 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 102012-204166 | 4. At Rye House 400kV: Replace circuit breakers X130. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 31/10/2031
|  | CS-08007 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 101248-204325 | Add a new bus coupler and three new bays at Wymondley 400kV substation to facilitate the turn-in of the existing Pelham to Sundon 400kV circuit at Wymondley 400kV substation | 31/10/2031
|  | CS-08017 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 021847-021847 | Construct a new 400kV double circuit between the Bramford 400 kV substation and the Twinstead Tee point strung with 3 x 700mm2 AAAC conductor at 75oC. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Pelham double circuit and Bramford – Braintree – Bulls lodge and Bramford – Braintree – Rayleigh Main 400 kV double circuit (BTNO Works). | 31/10/2031
|  | CS-08006 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 102122-204324 | Extend Wymondley 400kV substation main and reserve 2 busbars for the provision of one User bay | 31/10/2031
|  | CS-08008 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 101248- 202488 | Reconductor Sundon-Wymondley 1 and 2 400kV circuits with 3 x 700mm2 AAAC 75oC conductors to achieve a post-fault winter rating of 3820 MVA. Modify the existing circuit (A603) that runs from Pelham to Sundon 400kV. Turn in the circuit at Wymondley 400kV substation between towers 4TA001 and 4TB074 to create two separate circuits that run from Pelham to Wymondley 400kV and from Wymondley to Sundon 400kV. | 31/10/2031
|  | CS-08015 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 101885-203861 | Reconductor MILLBROOK-SUNDON 4-1 (MILB4-SUND4-1) & MILLBROOK-SUNDON 4-2 (MILB4-SUND4-2) 400kV circuit to achieve more than 1605MVA summer pre-fault rating | 31/10/2031
|  | CS-08014 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 100952-201899 | Uprate the East Claydon - Leighton Buzzard – Sundon circuit | 31/10/2031
|  | CS-08009 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 100942-201877 | At Walpole 400kV Substation: Install 2750MVA QBs on the Burwell-Walpole 1 and 2 circuits | 31/10/2031
|  | CS-08011 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 101927-203938 | 5. At Sundon 400kV: Replace circuit breakers X130, X510 and X710. Breakers to be rated to 63kA with tested X/R ratio of at least 28 and a peak withstand of at least 2.7 x RMS break | 31/10/2031
|  | CS-08013 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 021742-021742 | Uprate to 400kV operation two of the existing four Tottenham–Brimsdown–Waltham Cross circuits. They will bypass Tottenham and connect Waltham Cross 400kV directly with Hackney 400kV, using the existing Tottenham 275kV to Hackney 400kV route. Reconductor these circuits with 50/50 mixture of GAP 2x620 mm2 and 3M curlew 2x490 mm2 @ 190˚C conductors. The existing double circuits running from Pelham to Rye House to Waltham Cross will also be reconductored with Triple Araucaria 3 x 700mm2 conductor (at 90˚C). | 31/10/2031
|  | CS-08016 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 100591-201213 | Reconductor the existing 2x500mm2 conductor on the Ratcliffe – Staythorpe 400kV circuit with 2x620mm2 conductor and uprate the cable section to achieve a post-fault winter rating of 3100MVA | 31/10/2031
|  | CS-08018 | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 033461- 033461 | Post-completion of BTNO works, reconductor Bramford-Pelham 1 400kV circuits with 3 x700mm2 AAAC conductors to achieve a post-fault winter rating of 3100 MVA | 31/10/2031
Wymondley Solar Farm | PRO-001105 | CS-05296 | AGR SOLAR 4 LIMITED | Wymondley 400kV Substation | 100895-201796 | 1. Installation of tertiary cable box on the 13kV side of SGT1 at the Connection Site. 2. Installation of 13kV cable at the Connection Site. 3. Installation of earthing transformer at the Connection Site. 4. Installation of 13kV Disconnector at the Connection Site. | 30/06/2024
Wyseby Hill Energy Farm | PRO-001884 | CS-07332 | WYSEBYHILL ENERGY FARM LIMITED | Wyseby Hill Energy Farm 400kV Substation | SPT-RI-231 | 0 | 31/10/2031
|  | CS-07333 | WYSEBYHILL ENERGY FARM LIMITED | Wyseby Hill Energy Farm 400kV Substation | SPT-RI-2320 | 0 | 31/10/2031
|  | CS-07334 | WYSEBYHILL ENERGY FARM LIMITED | Wyseby Hill Energy Farm 400kV Substation | NGET-101268-202511 | 0 | 31/10/2031
|  | CS-07335 | WYSEBYHILL ENERGY FARM LIMITED | Wyseby Hill Energy Farm 400kV Substation | NGET -101268-202520 | 0 | 31/10/2031
Zenobe Blackhillock 300 MW | PRO-001624 | CS-06647 | ZENOBE BLACKHILLOCK LIMITED | Blackhillock 275kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 01/02/2024
|  | CS-06648 | ZENOBE BLACKHILLOCK LIMITED | Blackhillock 275kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 01/02/2024
|  | CS-06649 | ZENOBE BLACKHILLOCK LIMITED | Blackhillock 275kV Substation | SHET-RI-025d | North East Reinforcement | 01/02/2024
|  | CS-06650 | ZENOBE BLACKHILLOCK LIMITED | Blackhillock 275kV Substation | SHET-RI-093 and SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement – Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Establish a new 400kV double busbar at Kintore to enable this upgrade. | 01/02/2024
Zenobe Coalburn Battery Storage | PRO-001780 | CS-07442 | ZENOBE ENERGY LIMITED | Coalburn 400kV Substation | SPT-RI-2058 | Coalburn North 400kV Substation - construction of a new 400kV substation, indicatively called Coalburn North, to connect into the Strathaven-Elvanfoot 400kV circuit. Construction of a new 400kV double busbar substation with a bus coupler circuit breaker, two feeder bays to connect onto the Strathaven-Elvanfoot 400kV circuit. | 30/06/2026
Zenobe Kilmarnock South | PRO-001687 | CS-04488 | Zenobe Kilmarnock South Limited | Kilmarnock South GSP | SPT-RI-1854 | At Kilmarnock South 400kV GIS substation install a bus coupler to run the substation in double busbar arrangements. (SPT-RI-1854. Protection and control modifications as required. Associated civil works. Miscellaneous and minor works | 25/10/2024
Zenobe New Deer Battery Storage | PRO-001778 | CS-06805 | ZENOBE ENERGY LIMITED | New Deer 400kV Substation | SHET-RI-009 and SPT-RI-004 | East Coast Onshore 275kV Upgrade: Re-profile the existing Kintore-Tealing-Kincardine 275kV circuits and the existing Tealing-Westfield-Longannet 275kV circuits for operation at 65˚C. Establish new busbar at Alyth, to be built at 400kV but initially operate at 275kV, with reactive support. Install 275 kV Phase shifting transformers in each of the Kintore – Tealing circuits, XT1/XT2. Increasing the maximum operating temperature of the Longannet - Mossmorran - Westfield - Tealing 275kV overhead line routes to 65oC, and replacing the associated 275kV cable sections at Longannet to match the increased overhead line rating. Terminate the existing Windyhill-Lambhill-Longannet 275kV circuit in Denny North 275kV Substation, creating Windyhill-Lambhill-Denny North and Denny North Longannet No.2 275kV circuits. | 31/10/2029
|  | CS-06806 | ZENOBE ENERGY LIMITED | New Deer 400kV Substation | SHET-RI-025a | Reinsulate the existing VX1/VH overhead line for 400kV operation between the new 400kV Peterhead Substation and the new 400kV substation at Rothienorman. | 31/10/2029
|  | CS-06807 | ZENOBE ENERGY LIMITED | New Deer 400kV Substation | SHET-RI-025d | North East Reinforcement | 31/10/2029
|  | CS-06808 | ZENOBE ENERGY LIMITED | New Deer 400kV Substation | SHET-RI-025b | Eastern Subsea HVDC Link – Install a 2GW HVDC link between Peterhead (SHE-Transmission) and Drax (NGET). | 31/10/2029
|  | CS-06809 | ZENOBE ENERGY LIMITED | New Deer 400kV Substation | SHET-RI-025c | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | 31/10/2029
|  | CS-06810 | ZENOBE ENERGY LIMITED | New Deer 400kV Substation | SHET-RI-026 | Install two 1000MVA 275kV Quadrature Boosters at Blackhillock, on the existing 275kV circuits (AH1/HO2) to Knocknagael. | 31/10/2029
|  | CS-06811 | ZENOBE ENERGY LIMITED | New Deer 400kV Substation | SHET-RI-093 & SPT-RI-200 | East Coast Phase 2 – 400kV Reinforcement - Upgrade the existing Blackhillock / Rothienorman / Kintore / Alyth / Kincardine east coast 275kV circuits to 400kV operation. Also a new 400kV double busbar at Kintore will be developed to enable this upgrade. This upgrade also interfaces at Blackhillock 400kV Substation and with Scottish Power Transmission (SPT) at Kincardine substation. SPT will be responsible for all the 400kV OHL upgrade and substation works beyond the SHE Transmission/SPT Boundary (Boundary 4) | 31/10/2029
|  | CS-06812 | ZENOBE ENERGY LIMITED | New Deer 400kV Substation | SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/10/2029
Zenobe Norton | PRO-001691 | CS-07005 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 101333-202653 | Establish a new 400kV substation, provisionally referred to as Norton East 400kV, to the East of the existing Norton 400kV substation. Connect the new substation to the transmission system via a turn in of the existing Norton – Saltholme 400kV circuit to form a new Norton – Norton East 400kV and Norton East – Saltholme 400kV circuit | 31/10/2031
|  | CS-07006 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 101331-202651 | Busbar extension at Norton East 400kV to provide space for the User’s generator bay | 31/10/2031
|  | CS-07007 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 100455-201020 | At Keadby 400kV substation: Install a 2750MVA 32 Ohm impedance reactor in the Drax – Keadby – Thorpe Marsh circuit. Transpose the Cottam 1 circuit with the West Burton 1 circuit. | 31/10/2031
|  | CS-07008 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 101554-203095 | Uprate the new High Marham - Staythorpe 400 kV circuit to achieve a post-fault winter rating of 3100MVA | 31/10/2031
|  | CS-07009 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 101093-202181 | Establish a new 400kV double circuit route between Creyke Beck 400kV and High Marnham 400kV substation including all associated substation works | 31/10/2031
|  | CS-07010 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 033496-033496 | At Keadby 400kV Substation: Install a 2750MVA 16 Ohm series reactor in the Keadby – West Burton 1 circuit. | 31/10/2031
|  | CS-07011 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 101553-203094 | At High Marnham 400kV substation turn in the Cottam – Staythorpe 400kV circuit to create a new Cottam – High Marnham 400kV and High Marnham – Staythorpe 400kV circuit | 31/10/2031
|  | CS-07012 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 101554-203095 | Reconductor the new High Marham - Staythorpe 400 kV circuit with 2x620mm2 GZTACSR conductor | 31/10/2031
|  | CS-07013 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 101504-202965 | Reconductor the Drax leg and Thorpe Marsh leg of the Drax – Keadby – Thorpe Marsh 400kV circuit with 3x700mm2 strung for operation at 75°C. At Keadby 400kV substation, replace the X1005 feeder bay for Drax – Keadby – Thorpe Marsh circuit. | 31/10/2031
|  | CS-07014 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 100818-201654 | Establish a new 400kV double circuit route between Creyke Beck 400kV substation and High Marnham 400kV substation, including all associated substation works | 31/10/2031
|  | CS-07015 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph 400kV circuit with 2x620mm2 GZTACSR conductor | 31/10/2031
|  | CS-07016 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 100821-201659 | 1. Reconductor the Creyke Beck and Keadby legs of the Creyke Beck - Humber Refinery – Keadby 400kV and Creyke Beck -Keadby – Killingholme 400kV circuits with 3x700mm2 conductor | 31/10/2031
|  | CS-07017 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 033754-033755 | Establish a new 400kV double circuit connecting to the Norton – Osbaldwick 400kV double circuit to Poppleton including all associated substation works | 31/10/2031
|  | CS-07018 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 100459-201024 | Reconductor the existing 2x500mm2 conductor on the High Marnham – Stoke Bardolph circuit with 2x620mm2 conductor to achieve a post-fault winter rating of 3100MVA. | 31/10/2031
|  | CS-07019 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 020640-020640/101576-203163 | 1. Uprate the Norton - Osbaldwick 1 and 2 400kV circuits | 31/10/2031
|  | CS-07020 | ZENOBE ENERGY LIMITED | Norton 400kV Substation | 100449-201014 | At Drax, replace the existing 2 cores per phase 1600mm2 cable on the Drax – Eggborough 1 circuit with a 2 cores per 2500mm2 cable. | 31/10/2031