## Welcome
DRC Welcome Page
This tool provides a list of essential data fields required to be submitted by parties seeking connection to the GB transmission network at the application stage, in order to ensure technical competency of the application. In addition, further data fields are listed which, whilst not mandatory at application stage, are useful for the designer to ensure optimal network planning is undertaken. This tool does not list the complete set of data a customer is required to provide following acceptance of an offer and on an annual basis thereafter.
Please follow the instructions below. In case of doubt please refer to the FAQ section below.
Step 1. Click one the button below based on your connection type. Step 2. Confirm if you are carrying out OTSDUW works Step 3. (Only for Synchronous Machine based connections) Confirm if your connection will have either Station or Unit transformer arrangement. Step 4. Fill required data for your connection in column E of the displayed worksheets. If you have more than one generator unit please use other colums on the right of column E.
Frequently Asked Questions
How do I decide what type of connection I have? If you power station uses synchronous machine (Typically CCGT, OCGT, Nuclear, Biomass, Pump storage, CHP, Oil, Diesel, coal etc.) please click synchronous machine button for DRC submission. If you are connecting GB transmission network with any other transmission network, please click interconnector button for DRC Submission. If you have generation which is connected through a DC to AC converter or having power park modules (typically intermittent renewable generators such as wind farms, PV.), please click Power Park Module/ DC Converter Based Generators button for DRC submission. If you are connecting battery storage, please click the Battery Storage button and complete both tabs which are openned. If your connection includes only demand connection and no generation, please click Demand button for DRC submission. What is OTSDUW ? OTSDUW is Offshore Transmission System Development User Works. This is an arrangement where offshore generator plans to carry out certain aspects of the design, consenting, construction, installation and/or commissioning of the transmission assets prior to the transfer of those assets to a Relevant Transmission Licensee under an Offshore Tender Process. This arrangement is only for offshore network development and does not apply to Onshore connections. What is the difference between Station Transformer and Unit Transformer? In order to supply power station auxiliaries power is drawn form the network. Unit transformer connects to a Generator Unit’s terminals and supplied power to auxiliaries. Typical voltage ratios are 23/11 kV and 15/6.6 kV. Station transformers are not directly connected to generator terminals. They might be connected to the lower voltage transmission network or distribution network supplying power station auxiliaries. Do I need to include all the data declared essential at the application stage? All the data declare essential at the application stage are the minimum data required for carrying out technical assessment for the connection. Hence, all the data listed as essential at the application stage has to be provided. In case of unavailability of some of the data, assumptions can be made. User will have to agree if real value is different from the assumed value and has a material impact on the design. User will have to apply for modification of the application. This could affect delivery programme and connection date. Why are you asking more data than data only essential at the application stage? It is voluntary for the User to provide data in addition to data essential at the application stage. However, we recommend User to provide more data if they are available. Additional declared data not essential at the application stage help us design efficiently. It could result in possible earlier connection or lower securities in some cases.
Interconnector
Power Park Module/ DC Converter Based Generators
Synchronous Machine
Demand
Battery Storage

## INTERCONNECTOR (hidden)
DRC INFORMATION FOR INTERCONNECTORS | ESSENTIAL AT THE APPLICATION STAGE ? | DATA TYPE | PLEASE PROVIDE YOUR DATA HERE
SCHEDULE 1
Power Station Name | Yes | SPD
DC CONVERTER STATION DEMANDS
The maximum Demand that could occur during import. MW | No
The maximum Demand that could occur during export. MW | No
The maximum Demand that could occur during import. Mvar | No
The maximum Demand that could occur during export. Mvar | No
The minimum Demand that could occur during import. MW | No
The minimum Demand that could occur during export. MW | No
The minimum Demand that could occur during import. Mvar | No
The minimum Demand that could occur during export. Mvar | No
DC CONVERTER
Point of connection to the NGET Transmission System (or the Total System if Embedded) of the DC Converter Station configuration in terms of geographical and electrical location and system voltage | Yes | SPD
If the busbars at the Connection Point are normally run in separate sections identify the section to which the DC Converter Station configuration is connected | No | SPD
Number of poles, i.e. number of DC Converters | Yes | SPD+
Pole arrangement (e.g. monopole or bipole) | Yes | SPD+
Details of each viable operating configuration | Yes | SPD+
Remote ac connection arrangement | Yes | SPD
DC Converter Type (e.g. current or Voltage source) | Yes | SPD
Rated MVA (PC.A.3.3.1) | Yes | SPD+
Rated MW import per pole [PC.A.3.3.1] | Yes | SPD+
Rated MW export per pole [PC.A.3.3.1] | Yes | SPD+
Registered Capacity | Yes | SPD
Registered Import Capacity | Yes | SPD
Minimum Import Capacity | Yes | SPD
Minimum Generation | Yes | SPD
Import MW available in excess of Registered Import Capacity. | Yes | SPD
Time duration for which MW in excess of Registered Import Capacity is available | Yes | SPD
Export MW available in excess of Registered Capacity. | Yes | SPD
Time duration for which MW in excess of Registered Capacity is available | Yes | SPD
DC CONVERTER TRANSFORMER
Rated MVA (PC.A.3.3.1 & PC.A.5.3.2) | No | DPD2
Voltage Ratio (PC.A.5.3.2) | No | DPD2
Positive sequence reactance: (PC.A.5.3.2) | No | DPD2
Max tap | No | DPD2
Min tap | No | DPD2
Nominal tap | No | DPD2
Positive sequence resistance: (PC.A.5.3.2) | No | DPD2
Max tap | No | DPD2
Min tap | No | DPD2
Nominal tap | No | DPD2
Zero phase sequence reactance (PC.A.5.3.2) | No | DPD2
Tap change range (PC.A.5.3.2) | No | DPD2
Tap change step size (PC.A.5.3.2) | No | DPD2
Tap changer type: on-load or off-circuit (PC.A.5.3.2) | No | DPD2
DC NETWORK
Rated DC voltage per pole | No | DPD2
Rated DC current per pole | No | DPD2
Nominal loading rate MW Export | Yes (if connection can impact stability) | DPD1
Maximum (emergency) loading rate MW Export | Yes (if connection can impact stability) | DPD1
Nominal loading rate MW Import | Yes (if connection can impact stability) | DPD1
Maximum (emergency) loading rate MW Import | Yes (if connection can impact stability) | DPD1
SCHEDULE 2
OUTPUT CAPABILITY
Registered Capacity on a station and unit basis (on a station and module basis in the case of a CCGT Module or Power Park Module at a Large Power Station) | Yes | SPD
Minimum Generation (on a module basis in the case of a CCGT Module or Power Park Module at a Large Power Station) | Yes | SPD
MW available from Generating Units or Power Park Modules in excess of Registered Capacity | Yes | SPD
SCHEDULE 5
USERS SYSTEM LAYOUT (PC.A.2.2)
A Single Line Diagram showing all or part of the User’s System is required. This diagram shall include:- | Yes | SPD
(a) all parts of the User’s System, whether existing or proposed, operating at Supergrid Voltage, and in Scotland and Offshore, also all parts of the User System operating at 132kV, | Yes | SPD
(b) all parts of the User’s System operating at a voltage of 50kV, and in Scotland and Offshore greater than 30kV, or higher which can interconnect Connection Points, or split bus-bars at a single Connection Point, | Yes | SPD
(C) all parts of the User’s System between Embedded Medium Power Stations or Large Power Stations or Offshore Transmission Systems connected to the User’s Sub transmission System and the relevant Connection Point or Interface Point, | Yes | SPD
(d) all parts of the User’s System at a Transmission Site. | Yes | SPD
The Single Line Diagram may also include additional details of the User’s Sub transmission System, and the transformers connecting the User’s Sub transmission System to a lower voltage. With NGET’s agreement, it may also include details of the User’s System at a voltage below the voltage of the Sub transmission System. | Yes | SPD
This Single Line Diagram shall depict the arrangement(s) of all of the existing and proposed load current carrying Apparatus relating to both existing and proposed Connection Points, showing electrical circuitry (ie. overhead lines, underground cables, power transformers and similar equipment), operating voltages. In addition, for equipment operating at a Supergrid Voltage, and in Scotland and Offshore also at 132kV, circuit breakers and phasing arrangements shall be shown. | Yes | SPD
REACTIVE COMPENSATION (PC.A.2.4)
For independently switched reactive compensation equipment not owned by a Transmission Licensee connected to the User's System at 132kV and above, and also in Scotland and Offshore, connected at 33kV and above, other than power factor correction equipment associated with a customers Plant or Apparatus | Yes | SPD
Type of equipment (eg. fixed or variable) | Yes | SPD
Capacitive rating; or | Yes | SPD
Inductive rating; or | Yes | SPD
Operating range | Yes | SPD
Details of automatic control logic to enable operating characteristics to be determined | Yes | SPD
Point of connection to User's System (electrical location and system voltage) | Yes | SPD
SUBSTATION INFRASTRUCTURE (PC.A.2.2.6(b))
For the infrastructure associated with any User’s equipment at a Substation owned by a Transmission Licensee or operated or managed by NGET:- | No | SPD
Rated 3-phase rms short-circuit withstand current | No | SPD
Rated 1-phase rms short-circuit withstand current | No | SPD
Rated Duration of short-circuit withstand | No | SPD
Rated rms continuous current | No | SPD
LUMPED SUSCEPTANCES (PC.A.2.3)
Equivalent Lumped Susceptance required for all parts of the User’s Sub transmission System which are not included in the Single Line Diagram. | Yes | SPD
Equivalent lumped shunt susceptance at nominal Frequency. | Yes | SPD
CIRCUIT PARAMETERS (PC.A.2.2.4)
Years Valid | No | SPD
Node 1 | Yes | SPD
Node 2 | Yes | SPD
Rated Voltage kV | Yes | SPD
Operating Voltage | Yes | SPD
Positive Phase Sequence % on 100 MVA R | Yes | SPD
Positive Phase Sequence % on 100 MVA X | Yes | SPD
Positive Phase Sequence % on 100 MVA B | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA R | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA X | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA B | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA R | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA X | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA B | Yes | SPD
TRANSFORMER DATA (PC.A.2.2.5)
Year Valid | No | SPD
Name of Node or Connection Point | Yes | SPD
Transformer Identity | Yes | SPD
Rating MVA | Yes | SPD
Voltage Ratio | Yes | SPD
Positive Phase Sequence Reactance % on Rating | Yes | SPD
Positive Phase Sequence Resistance % on Rating | Yes | SPD
Zero Sequence Reactance % on Rating | Yes | SPD
Winding Arrangement | Yes | SPD
Tap Changer range +%to-% | Yes | SPD
Tap Changer step size % | Yes | SPD
Tap Changer type (On / Off) | Yes | SPD
Earthing details (Direct/Resistance/Reactance) | Yes | SPD
SWITCHGEAR DATA
Years Valid | No | SPD
Connection Point | Yes (if existing connection) | SPD
Switchgear Identity | Yes (if existing connection) | SPD
Rated Voltage kV rms | Yes (if existing connection) | SPD
Operating Voltage kV rms | Yes (if existing connection) | SPD
Rated short-circuit breaking current 3 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit breaking current 1 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit peak making current 3 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit peak making current 1 Phase kA rms | Yes (if existing connection) | SPD
Rated rms continuous current (A) | Yes (if existing connection) | SPD
DC time constant at testing of asymmetrical breaking ability(s) | Yes (if existing connection) | SPD
SCHEDULE 13
SHORT CIRCUIT INFEED TO THE NATIONAL ELECTRICITY TRANSMISSION SYSTEM FROM USERS SYSTEM AT A CONNECTION POINT
Name of node or Connection Point | Yes | SPD
Symmetrical three phase short-circuit current infeed - at instant of fault kA | Yes | SPD
Symmetrical three phase short-circuit current infeed - after subtransient fault current contribution has substantially decayed kA | Yes | SPD
Zero sequence source impedances as seen from the Point of Connection or node on the Single Line Diagram (as appropriate) consistent with the maximum infeed above: - Resistance % on 100 MVA | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Zero sequence source impedances as seen from the Point of Connection or node on the Single Line Diagram (as appropriate) consistent with the maximum infeed above: - Reactance % on 100 MVA | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Positive sequence X/R ratio at instance of fault | Yes | SPD
Pre-Fault voltage magnitude at which the maximum fault currents were calculated p.u. | Yes | SPD
Negative sequence impedances of User’s System as seen from the Point of Connection or node on the Single Line Diagram (as appropriate). - Resistance % on 100 MVA | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Negative sequence impedances of User’s System as seen from the Point of Connection or node on the Single Line Diagram (as appropriate). - Reactance % on 100 MVA | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Show Essential at Application
Show All

## Power Park Module (hidden)
DRC INFORMATION FOR POWER PARK MODULE / DC CONVERTER BASED GENERATORS | ESSENTIAL AT THE APPLICATION STAGE ? | DATA TYPE
SCHEDULE 1
POWER STATION NAME: | Yes | SPD
GENERATING STATION DEMANDS | No
The maximum Demand that could occur. MW | No | DPD1
The maximum Demand that could occur. Mvar | No | DPD1
POWER PARK MODULE
Point of connection to the National Electricity Transmission System (or the Total System if embedded) of the Generating Unit (other than a CCGT Unit) or the CCGT Module, as the case may be in terms of geographical and electrical location and system voltage (PC.A.3.4.1) | Yes | SPD
If the busbars at the Connection Point are normally run in separate sections identify the section to which the Generating Unit (other than a CCGT Unit) or CCGT Module, as the case may be is connected (PC.A.3.1.5) | No | SPD
Type of Unit (steam, Gas Turbine Combined Cycle Gas Turbine Unit, tidal, wind, etc.) (PC.A.3.2.2 (h)) | Yes | SPD
Number & Type of Power Park Units within each Power Park Module (PC.A.3.2.2(k)) or Number & Type of Offshore Power Park Units within each Offshore Power Park String and the number of Offshore Power Park | Yes | SPD
Power Park Module Data Rated MVA (PC.A.3.3.1(a)) | Yes | SPD+
Power Park Unit Data Rated MVA (PC.A.3.3.1(e)) | Yes | SPD+
Power Park Module Rated MW (PC.A.3.3.1) | Yes | SPD+
Power Park Unit Data Rated MW (PC.A.3.3.1(e)) | Yes | SPD+
Power Park Unit Data Rated terminal voltage (PC.A.3.3.1(e)) | Yes | SPD+
Output Usable (On a monthly basis) (PC.A.3.2.2(b)) | No | SPD
Equivalent inertia constant of the first mass (e.g. wind turbine rotor and blades) at minimum speed (PC.A.5.4.2(b)) MW secs/MVA | No | SPD+
Equivalent inertia constant of the first mass (e.g. wind turbine rotor and blades) at synchronous speed (PC.A.5.4.2(b)) MW secs/MVA | No | SPD+
Equivalent inertia constant of the first mass (e.g. wind turbine rotor and blades) at rated speed (PC.A.5.4.2(b)) MW secs/MVA | No | SPD+
Equivalent inertia constant of the second mass (e.g. generator rotor) at minimum speed (PC.A.5.4.2(b)) MW secs/MVA | No | SPD+
Equivalent inertia constant of the second mass (e.g. generator rotor) at synchronous speed (PC.A.5.4.2(b)) MW secs/MVA | No | SPD+
Equivalent inertia constant of the second mass (e.g. generator rotor) at rated speed (PC.A.5.4.2(b)) MW secs/MVA | No | SPD+
Equivalent shaft stiffness between the two masses (PC.A.5.4.2(b)) Nm/ electrical radian | No | SPD+
Minimum generator rotor speed (Doubly Fed Induction Generators) (PC.A.3.3.1(e)) RPM | No | SPD+
Maximum generator rotor speed (Doubly Fed Induction Generators) (PC.A.3.3.1(e)) RPM | No | SPD+
IMPEDANCES | No
Stator Resistance (PC.A.5.4.2(b)) | No | SPD+
Stator Reactance (PC.A.3.3.1(e)) | No | SPD+
Magnetising Reactance (PC.A.3.3.1(e)) | No | SPD+
Rotor Resistance (at starting). (PC.A.5.4.2(b)) | No | DPD2
Rotor Resistance (at rated running) (PC.A.3.3.1(e)) | No | SPD+
Rotor Reactance (at starting). (PC.A.5.4.2(b)) | No | DPD2
Rotor Reactance (at rated running) (PC.A.3.3.1(e)) | No | SPD+
SCHEDULE 2
OUTPUT CAPABILITY
Registered Capacity on a station and unit basis (on a station and module basis in the case of a CCGT Module or Power Park Module at a Large Power Station) | Yes | SPD
Minimum Generation (on a module basis in the case of a CCGT Module or Power Park Module at a Large Power Station) | Yes | SPD
MW available from Generating Units or Power Park Modules in excess of Registered Capacity | Yes | SPD
SCHEDULE 5
USERS SYSTEM LAYOUT (PC.A.2.2)
A Single Line Diagram showing all or part of the User’s System is required. This diagram shall include:- | Yes | SPD
(a) all parts of the User’s System, whether existing or proposed, operating at Supergrid Voltage, and in Scotland and Offshore, also all parts of the User System operating at 132kV, | Yes | SPD
(b) all parts of the User’s System operating at a voltage of 50kV, and in Scotland and Offshore greater than 30kV, or higher which can interconnect Connection Points, or split bus-bars at a single Connection Point, | Yes | SPD
(C) all parts of the User’s System between Embedded Medium Power Stations or Large Power Stations or Offshore Transmission Systems connected to the User’s Sub transmission System and the relevant Connection Point or Interface Point, | Yes | SPD
(d) all parts of the User’s System at a Transmission Site. | Yes | SPD
The Single Line Diagram may also include additional details of the User’s Sub transmission System, and the transformers connecting the User’s Sub transmission System to a lower voltage. With NGET’s agreement, it may also include details of the User’s System at a voltage below the voltage of the Sub transmission System. | Yes | SPD
This Single Line Diagram shall depict the arrangement(s) of all of the existing and proposed load current carrying Apparatus relating to both existing and proposed Connection Points, showing electrical circuitry (ie. overhead lines, underground cables, power transformers and similar equipment), operating voltages. In addition, for equipment operating at a Supergrid Voltage, and in Scotland and Offshore also at 132kV, circuit breakers and phasing arrangements shall be shown. | Yes | SPD
REACTIVE COMPENSATION (PC.A.2.4)
For independently switched reactive compensation equipment not owned by a Transmission Licensee connected to the User's System at 132kV and above, and also in Scotland and Offshore, connected at 33kV and above, other than power factor correction equipment associated with a customers Plant or Apparatus | Yes | SPD
Type of equipment (eg. fixed or variable) | Yes | SPD
Capacitive rating; or | Yes | SPD
Inductive rating; or | Yes | SPD
Operating range | Yes | SPD
Details of automatic control logic to enable operating characteristics to be determined | Yes | SPD
Point of connection to User's System (electrical location and system voltage) | Yes | SPD
SUBSTATION INFRASTRUCTURE (PC.A.2.2.6(b)) | No
For the infrastructure associated with any User’s equipment at a Substation owned by a Transmission Licensee or operated or managed by NGET:- | No | SPD
Rated 3-phase rms short-circuit withstand current | No | SPD
Rated 1-phase rms short-circuit withstand current | No | SPD
Rated Duration of short-circuit withstand | No | SPD
Rated rms continuous current | No | SPD
LUMPED SUSCEPTANCES (PC.A.2.3)
Equivalent Lumped Susceptance required for all parts of the User’s Sub transmission System which are not included in the Single Line Diagram. | Yes | SPD
Equivalent lumped shunt susceptance at nominal Frequency. | Yes | SPD
CIRCUIT PARAMETERS (PC.A.2.2.4)
Years Valid | No | SPD
Node 1 | Yes | SPD
Node 2 | Yes | SPD
Rated Voltage kV | Yes | SPD
Operating Voltage | Yes | SPD
Positive Phase Sequence % on 100 MVA R | Yes | SPD
Positive Phase Sequence % on 100 MVA X | Yes | SPD
Positive Phase Sequence % on 100 MVA B | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA R | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA X | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA B | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA R | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA X | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA B | Yes | SPD
Transformer Data (PC.A.2.2.5)
Years Valid | No | SPD
Name of Node or Connection Point | Yes | SPD
Transformer Identity | Yes | SPD
Rating MVA | Yes | SPD
Voltage Ratio | Yes | SPD
Positive Phase Sequence Reactance % on Rating | Yes | SPD
Positive Phase Sequence Resistance % on Rating | Yes | SPD
Zero Sequence Reactance % on Rating | Yes | SPD
Winding Arrangement | Yes | SPD
Tap Changer range +%to-% | Yes | SPD
Tap Changer step size % | Yes | SPD
Tap Changer type (ON/OFF) | Yes | SPD
Earthing details (Direct/Resistance/Reactance) | Yes | SPD
SWITCHGEAR DATA
Years Valid | No | SPD
Connection Point | Yes (if existing connection) | SPD
Switchgear Identity | Yes (if existing connection) | SPD
Rated Voltage kV rms | Yes (if existing connection) | SPD
Operating Voltage kV rms | Yes (if existing connection) | SPD
Rated short-circuit breaking current 3 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit breaking current 1 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit peak making current 3 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit peak making current 1 Phase kA rms | Yes (if existing connection) | SPD
Rated rms continuous current (A) | Yes (if existing connection) | SPD
DC time constant at testing of asymmetrical breaking ability(s) | Yes (if existing connection) | SPD
SCHEDULE 13
SHORT CIRCUIT INFEED TO THE NATIONAL ELECTRICITY TRANSMISSION SYSTEM FROM USERS SYSTEM AT A CONNECTION POINT
Name of node or Connection Point | Yes | SPD
Symmetrical three phase short-circuit current infeed - at instant of fault kA | Yes | SPD
Symmetrical three phase short-circuit current infeed - after subtransient fault current contribution has substantially decayed kA | Yes | SPD
Zero sequence source impedances as seen from the Point of Connection or node on the Single Line Diagram (as appropriate) consistent with the maximum infeed above: - Resistance % on 100 MVA | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Zero sequence source impedances as seen from the Point of Connection or node on the Single Line Diagram (as appropriate) consistent with the maximum infeed above: - Reactance % on 100 MVA | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Positive sequence X/R ratio at instance of fault | Yes | SPD
Pre-Fault voltage magnitude at which the maximum fault currents were calculated p.u. | Yes | SPD
Negative sequence impedances of User’s System as seen from the Point of Connection or node on the Single Line Diagram (as appropriate). - Resistance % on 100 MVA | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Negative sequence impedances of User’s System as seen from the Point of Connection or node on the Single Line Diagram (as appropriate). - Reactance % on 100 MVA | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Show Essential at Application
Show All

## Synchronous Machine (hidden)
| ESSENTIAL AT THE APPLICATION STAGE ? | DATA TYPE | Please provide your Data here
SCHEDULE 1
POWER STATION NAME: | Yes
GENERATING STATION DEMANDS | No
The maximum Demand that could occur. MW | No | DPD1
The maximum Demand that could occur. Mvar | No | DPD1
INDIVIDUAL GENERATING UNI(OR AS THE CASE MAY BE, CCGT MODULE) DATA
Point of connection to the National Electricity Transmission System (or the Total System if embedded) of the Generating Unit (other than a CCGT Unit) or the CCGT Module, as the case may be in terms of geographical and electrical location and system voltage (PC.A.3.4.1) | Yes | SPD
If the busbars at the Connection Point are normally run in separate sections identify the section to which the Generating Unit (other than a CCGT Unit) or CCGT Module, as the case may be is connected (PC.A.3.1.5) | No | SPD
Type of Unit (PC.A.3.2.2 (h)) | Yes | SPD
A list of the CCGT Units within a CCGT Module, identifying each CCGT Unit, and the CCGT Module of which it forms part, unambiguously. In the case of a Range CCGT Module, details of the possible configurations should also be submitted. (PC.A.3.2.2 (g)) | Yes | SPD
Rated MVA (PC.A.3.3.1) | Yes | SPD+
Rated MW (PC.A.3.3.1) | Yes | SPD+
Rated terminal voltage (PC.A.5.3.2.(a) & PC.A.5.4.2 (b)) | Yes | DPD1
Performance Chart at Onshore Synchronous Generating Unit stator terminals (PC.A.3.2.2(f)(i)) | Yes | SPD
Performance Chart of the Offshore Synchronous Generating Unit at the Offshore Grid Entry Point (PC.A.3.2.2(f)(ii)) | Yes | SPD
Output Usable (on a monthly basis) (PC.A.3.2.2(b)) | No | SPD
Turbo-Generator inertia constant (for synchronous machines) (PC.A.5.3.2(a)) | Yes | SPD+
Short circuit ratio (synchronous machines) (PC.A.5.3.2(a)) | Yes | SPD+
IMPEDANCES
Direct axis synchronous reactance (PC.A.5.3.2(a)) (Unsaturated) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
Direct axis transient reactance (PC.A.3.3.1(a)& PC.A.5.3.2(a) | Yes | SPD+
Direct axis sub-transient reactance (PC.A.5.3.2(a)) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
Quad axis synch reactance (PC.A.5.3.2(a)) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
Quad axis sub-transient reactance (PC.A.5.3.2(a)) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
Stator leakage reactance (PC.A.5.3.2(a)) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
Armature winding direct current resistance. (PC.A.5.3.2(a)) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
TIME CONSTANTS (Short-circuit and Unsaturated)
Direct axis transient time constant (PC.A.5.3.2(a)) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
Direct axis sub-transient time constant (PC.A.5.3.2(a)) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
Quadrature axis sub-transient time constant (PC.A.5.3.2(a)) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
Stator time constant (PC.A.5.3.2(a)) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
GENERATING UNIT STEP-UP TRANSFORMER
Rated MVA (PC.A.3.3.1 & PC.A.5.3.2) | Yes | SPD+
Voltage Ratio (PC.A.5.3.2) | Yes | DPD1
Positive sequence reactance: (PC.A.5.3.2) | Yes | SPD+
Max tap | Yes | SPD+
Min tap | Yes | SPD+
Nominal tap | Yes | SPD+
Positive sequence resistance: (PC.A.5.3.2) | Yes | DPD1
Max tap | Yes | DPD1
Min tap | Yes | DPD1
Nominal tap | Yes | DPD1
Zero phase sequence reactance (PC.A.5.3.2) | Yes | DPD2
Tap change range (PC.A.5.3.2) | Yes | DPD2
Tap change step size (PC.A.5.3.2) | Yes | DPD2
Tap changer type: on-load or off-circuit (PC.A.5.3.2) | Yes | DPD2
EXCITATION
Detail of Excitation system (PC.A.5.3.2c) | Yes | DPD1 (essential at the application stage/ If not provided subject to assumption. This can lead to uncertainty on build programme)
SCHEDULE 2
OUTPUT CAPABILITY
Registered Capacity on a station and unit basis (on a station and module basis in the case of a CCGT Module or Power Park Module at a Large Power Station) | Yes | SPD
Minimum Generation (on a module basis in the case of a CCGT Module or Power Park Module at a Large Power Station) | Yes | SPD
MW available from Generating Units or Power Park Modules in excess of Registered Capacity | Yes | SPD
EXPECTED RUNNING REGIME
Is Power Station normally available for full output 24 hours per day, 7 days per week? If No please provide details of unavailability below. | No | SPD
SCHEDULE 5
USERS SYSTEM LAYOUT (PC.A.2.2)
A Single Line Diagram showing all or part of the User’s System is required. This diagram shall include:- | Yes | SPD
(a) all parts of the User’s System, whether existing or proposed, operating at Supergrid Voltage, and in Scotland and Offshore, also all parts of the User System operating at 132kV,
(b) all parts of the User’s System operating at a voltage of 50kV, and in Scotland and Offshore greater than 30kV, or higher which can interconnect Connection Points, or split bus-bars at a single Connection Point,
(C) all parts of the User’s System between Embedded Medium Power Stations or Large Power Stations or Offshore Transmission Systems connected to the User’s Sub transmission System and the relevant Connection Point or Interface Point,
(d) all parts of the User’s System at a Transmission Site.
The Single Line Diagram may also include additional details of the User’s Sub transmission System, and the transformers connecting the User’s Sub transmission System to a lower voltage. With NGET’s agreement, it may also include details of the User’s System at a voltage below the voltage of the Sub transmission System.
This Single Line Diagram shall depict the arrangement(s) of all of the existing and proposed load current carrying Apparatus relating to both existing and proposed Connection Points, showing electrical circuitry (ie. overhead lines, underground cables, power transformers and similar equipment), operating voltages. In addition, for equipment operating at a Supergrid Voltage, and in Scotland and Offshore also at 132kV, circuit breakers and phasing arrangements shall be shown.
REACTIVE COMPENSATION (PC.A.2.4)
For independently switched reactive compensation equipment not owned by a Transmission Licensee connected to the User's System at 132kV and above, and also in Scotland and Offshore, connected at 33kV and above, other than power factor correction equipment associated with a customers Plant or Apparatus | Yes | SPD
Type of equipment (eg. fixed or variable) | Yes | SPD
Capacitive rating; or | Yes | SPD
Inductive rating; or | Yes | SPD
Operating range | Yes | SPD
Details of automatic control logic to enable operating characteristics to be determined | Yes | SPD
Point of connection to User's System (electrical location and system voltage) | Yes | SPD
SUBSTATION INFRASTRUCTURE (PC.A.2.2.6(b))
For the infrastructure associated with any User’s equipment at a Substation owned by a Transmission Licensee or operated or managed by NGET:- | No | SPD
Rated 3-phase rms short-circuit withstand current | No | SPD
Rated 1-phase rms short-circuit withstand current | No | SPD
Rated Duration of short-circuit withstand | No | SPD
Rated rms continuous current | No | SPD
LUMPED SUSCEPTANCES (PC.A.2.3)
Equivalent Lumped Susceptance required for all parts of the User’s Sub transmission System which are not included in the Single Line Diagram. | Yes | SPD
Equivalent lumped shunt susceptance at nominal Frequency. | Yes | SPD
CIRCUIT PARAMETERS (PC.A.2.2.4)
Years Valid | No | SPD
Node 1 | Yes | SPD
Node 2 | Yes | SPD
Rated Voltage kV | Yes | SPD
Operating Voltage | Yes | SPD
Positive Phase Sequence % on 100 MVA R | Yes | SPD
Positive Phase Sequence % on 100 MVA X | Yes | SPD
Positive Phase Sequence % on 100 MVA B | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA R | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA X | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA B | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA R | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA X | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA B | Yes | SPD
TRANSFORMER DATA (PC.A.2.2.5)
Year Valid | No | SPD
Name of Node or Connection Point | Yes | SPD
Transformer Identity | Yes | SPD
Rating MVA | Yes | SPD
Voltage Ratio | Yes | SPD
Positive Phase Sequence Reactance % on Rating | Yes | SPD
Positive Phase Sequence Resistance % on Rating | Yes | SPD
Zero Sequence Reactance % on Rating | Yes | SPD
Winding Arrangement | Yes | SPD
Tap Changer range +%to-% | Yes | SPD
Tap Changer step size % | Yes | SPD
Tap Changer type (On / Off) | Yes | SPD
Earthing details (Direct/Resistance/Reactance) | Yes | SPD
SWITCHGEAR DATA (PC.A.2.2.6(a))
Years Valid | No | SPD
Connection Point | Yes (if existing connection) | SPD
Switchgear Identity | Yes (if existing connection) | SPD
Rated Voltage kV rms | Yes (if existing connection) | SPD
Operating Voltage kV rms | Yes (if existing connection) | SPD
Rated short-circuit breaking current 3 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit breaking current 1 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit peak making current 3 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit peak making current 1 Phase kA rms | Yes (if existing connection) | SPD
Rated rms continuous current (A) | Yes (if existing connection) | SPD
DC time constant at testing of asymmetrical breaking ability(s) | Yes (if existing connection) | SPD
SCHEDULE 14
FAULT INFEEDS VIA STATION TRANSFORMERS | If design includes Station Transformers
Name of Power Station | Yes | SPD
Number of Station Transformer | Yes | SPD
Symmetrical three phase short-circuit current infeed for a fault at the Connection Point - at instant of fault | Yes | SPD
Symmetrical three phase short-circuit current infeed for a fault at the Connection Point after subtransient fault current contribution has substantially decayed | Yes | SPD
Positive sequence X/R ratio At instance of fault | Yes | SPD
Subtransient time constant (if significantly different from 40ms) | Yes | SPD
Pre-fault voltage (if different from 1.0 p.u.) at fault point. (The pre-fault voltage provided it represents the voltage within the range 0.95 to 1.05 that gives the highest fault current) | Yes | SPD
Zero sequence source Impedances as seen from the Point of Connection Consistent with the maximum Infeed above: - Resistance % on 100 MVA | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Zero sequence source Impedances as seen from the Point of Connection Consistent with the maximum Infeed above: - - Reactance % on 100 MVA | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
FAULT INFEEDS VIA UNIT TRANSFORMERS | If design includes Unit Transformers
Name of Power Station | Yes | SPD
Number of Unit Transformer | Yes | SPD
Symmetrical three phase short- circuit current infeed through the Unit Transformers(s) for a fault at the Generating Unit terminals - at instant of fault | Yes | SPD
Symmetrical three phase short- circuit current infeed through the Unit Transformers(s) for a fault at the Generating Unit terminals - after subtransient fault current contribution has substantially decayed | Yes | SPD
Positive sequence X/R ratio At instance of fault | Yes | SPD
Subtransient time constant (if significantly different from 40ms) | Yes | SPD
Pre-fault voltage (if different from 1.0 p.u.) at fault point (The pre-fault voltage provided it represents the voltage within the range 0.95 to 1.05 that gives the highest fault current) | Yes | SPD
Zero sequence source Impedances as seen from the Point of Connection Consistent with the maximum Infeed above: - Resistance % on 100 | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Zero sequence source Impedances as seen from the Point of Connection Consistent with the maximum Infeed above: - - Reactance % on 100 | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Show Only the details Essential at the Application Stage
Show All

## Demand (hidden)
DRC INFORMATION FOR DEMAND | ESSENTIAL AT THE APPLICATION STAGE ? | DATA TYPE
SCHEDULE 5
USERS SYSTEM LAYOUT (PC.A.2.2)
A Single Line Diagram showing all or part of the User’s System is required. This diagram shall include:- | Yes | SPD
(a) all parts of the User’s System, whether existing or proposed, operating at Supergrid Voltage, and in Scotland and Offshore, also all parts of the User System operating at 132kV, | Yes | SPD
(b) all parts of the User’s System operating at a voltage of 50kV, and in Scotland and Offshore greater than 30kV, or higher which can interconnect Connection Points, or split bus-bars at a single Connection Point, | Yes | SPD
(C) all parts of the User’s System between Embedded Medium Power Stations or Large Power Stations or Offshore Transmission Systems connected to the User’s Sub transmission System and the relevant Connection Point or Interface Point, | Yes | SPD
(d) all parts of the User’s System at a Transmission Site. | Yes | SPD
The Single Line Diagram may also include additional details of the User’s Sub transmission System, and the transformers connecting the User’s Sub transmission System to a lower voltage. With NGET’s agreement, it may also include details of the User’s System at a voltage below the voltage of the Sub transmission System. | Yes | SPD
This Single Line Diagram shall depict the arrangement(s) of all of the existing and proposed load current carrying Apparatus relating to both existing and proposed Connection Points, showing electrical circuitry (ie. overhead lines, underground cables, power transformers and similar equipment), operating voltages. In addition, for equipment operating at a Supergrid Voltage, and in Scotland and Offshore also at 132kV, circuit breakers and phasing arrangements shall be shown. | Yes | SPD
REACTIVE COMPENSATION (PC.A.2.4)
For independently switched reactive compensation equipment not owned by a Transmission Licensee connected to the User's System at 132kV and above, and also in Scotland and Offshore, connected at 33kV and above, other than power factor correction equipment associated with a customers Plant or Apparatus | Yes | SPD
Type of equipment (eg. fixed or variable) | Yes | SPD
Capacitive rating; or | Yes | SPD
Inductive rating; or | Yes | SPD
Operating range | Yes | SPD
Details of automatic control logic to enable operating characteristics to be determined | Yes | SPD
Point of connection to User's System (electrical location and system voltage) | Yes | SPD
SUBSTATION INFRASTRUCTURE (PC.A.2.2.6(b))
For the infrastructure associated with any User’s equipment at a Substation owned by a Transmission Licensee or operated or managed by NGET:- | No | SPD
Rated 3-phase rms short-circuit withstand current | No | SPD
Rated 1-phase rms short-circuit withstand current | No | SPD
Rated Duration of short-circuit withstand | No | SPD
Rated rms continuous current | No | SPD
LUMPED SUSCEPTANCES (PC.A.2.3)
Equivalent Lumped Susceptance required for all parts of the User’s Sub transmission System which are not included in the Single Line Diagram. | Yes | SPD
Equivalent lumped shunt susceptance at nominal Frequency. | Yes | SPD
CIRCUIT PARAMETERS (PC.A.2.2.4)
Rated Voltage kV | Yes | SPD
Operating Voltage | Yes | SPD
Positive Phase Sequence % on 100 MVA R | Yes | SPD
Positive Phase Sequence % on 100 MVA X | Yes | SPD
Positive Phase Sequence % on 100 MVA B | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA R | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA X | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA B | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA R | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA X | Yes | SPD
Zero Phase Sequence (mutual) % on 100 MVA B | Yes | SPD
Transformer Data (PC.A.2.2.5)
Rating MVA | Yes | SPD
Voltage Ratio | Yes | SPD
Positive Phase Sequence Reactance % on Rating | Yes | SPD
Positive Phase Sequence Resistance % on Rating | Yes | SPD
Zero Sequence Reactance % on Rating | Yes | SPD
Winding Arrangement | Yes | SPD
Tap Changer range +%to-% | Yes | SPD
Tap Changer step size % | Yes | SPD
Tap Changer type | Yes | SPD
Earthing details | Yes | SPD
Connection Point | Yes | SPD
Rated Voltage kV rms | Yes (if existing connection) | SPD
Operating Voltage kV rms | Yes (if existing connection) | SPD
Rated short-circuit breaking current 3 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit breaking current 1 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit peak making current 3 Phase kA rms | Yes (if existing connection) | SPD
Rated short-circuit peak making current 1 Phase kA rms | Yes (if existing connection) | SPD
Rated rms continuous current (A) | Yes (if existing connection) | SPD
DC time constant at testing of asymmetrical breaking ability(s) | Yes (if existing connection) | SPD
SCHEDULE 13
SHORT CIRCUIT INFEED TO THE NATIONAL ELECTRICITY TRANSMISSION SYSTEM FROM USERS SYSTEM AT A CONNECTION POINT
Name of node or Connection Point | Yes | SPD
Symmetrical three phase short-circuit current infeed - at instant of fault | Yes | SPD
Symmetrical three phase short-circuit current infeed - after subtransient fault current contribution has substantially decayed | Yes | SPD
Zero sequence source impedances as seen from the Point of Connection or node on the Single Line Diagram (as appropriate) consistent with the maximum infeed above: - Resistance % on 100 | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Zero sequence source impedances as seen from the Point of Connection or node on the Single Line Diagram (as appropriate) consistent with the maximum infeed above: - Reactance % on 100 | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Positive sequence X/R ratio at instance of fault | Yes | SPD
Pre-Fault voltage magnitude at which the maximum fault currents were calculated | Yes | SPD
Negative sequence impedances of User’s System as seen from the Point of Connection or node on the Single Line Diagram (as appropriate). - Resistance % on 100 | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Negative sequence impedances of User’s System as seen from the Point of Connection or node on the Single Line Diagram (as appropriate). - Reactance % on 100 | If no data is given, it will be assumed that they are equal to the positive sequence values. | SPD
Show Essential at Application
Show All

## Offshore Data (hidden)
DRC INFORMATION FOR THE OFFSHORE NETWORK | ESSENTIAL AT THE APPLICATION STAGE ? | DATA TYPE | Please provide your Data here
OFFSHORE TRANSMISSION SYSTEM LAYOUT (PC.A.2.2.1, PC.A.2.2.2 and P.C.A.2.2.3)
A Single Line Diagram showing connectivity of all of the Offshore Transmission System including all Plant and Apparatus between the Interface Point and all Connection Points is required. | Yes | SPD
This Single Line Diagram shall depict the arrangement(s) of all of the existing and proposed load current carrying Apparatus relating to both existing and proposed Interface Points and Connection Points, showing electrical circuitry (ie. overhead lines, underground cables (including subsea cables), power transformers and similar equipment), operating voltages, circuit breakers and phasing arrangements | Yes | SPD
Operational Diagrams of all substations within the OTSDUW Plant and Apparatus | Yes | SPD
SUBSTATION INFRASTRUCTURE (PC.A.2.2.6)
For the infrastructure associated with any OTSDUW Plant and Apparatus
Rated 3-phase rms short-circuit withstand current | Yes | SPD
Rated 1-phase rms short-circuit withstand current | Yes | SPD
Rated Duration of short-circuit withstand | Yes | SPD
Rated rms continuous current | Yes | SPD
LUMPED SUSCEPTANCES (PC.A.2.3)
Equivalent Lumped Susceptance required for all parts of the User’s Subtransmission System (including OTSDUW Plant and Apparatus) which are not included in the Single Line Diagram.
This should not include:
(a) Independently switched reactive compensation equipment identified above.
(b) Any susceptance of the OTSDUW Plant and Apparatus inherent in the Demand (Reactive Power).
Equivalent lumped shunt susceptance at nominal Frequency. % on 100 MVA | Yes | SPD
BRANCH DATA (PC.A.2.2.4)
Node 1 | Yes | SPD
Node 2 | Yes | SPD
Rated Voltage (kV) | Yes | SPD
Operating Voltage (kV) | Yes | SPD
Circuit Identity | Yes | SPD
Positive Phase Sequence % on 100 MVA R | Yes | SPD
Positive Phase Sequence % on 100 MVA X | Yes | SPD
Positive Phase Sequence % on 100 MVA B | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA R | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA X | Yes | SPD
Zero Phase Sequence (self) % on 100 MVA B | Yes | SPD
Maximum Continuous Winter Rating | Yes | SPD
Maximum Continuous Summer Rating | Yes | SPD
Maximum Continuous Spring/Autumn Rating | Yes | SPD
Length | Yes | SPD
2 WINDING TRANSFORMER DATA (PC.A.2.2.5)
HV Node | Yes | SPD
HV (kV) | Yes | SPD
LV Node | Yes | SPD
LV (kV) | Yes | SPD
Rating MVA | Yes | SPD
Transformer Identity | Yes | SPD
Positive Phase Sequence Reactance % on Rating With Min. Tap | Yes | SPD
Positive Phase Sequence Reactance % on Rating With Min. Tap | Yes | SPD
Positive Phase Sequence Reactance % on Rating With Normal Tap | Yes | SPD
Positive Phase Sequence Resistance % on Rating With Min. Tap | Yes | SPD
Positive Phase Sequence Resistance % on Rating With Min. Tap | Yes | SPD
Positive Phase Sequence Resistance % on Rating With Normal Tap | Yes | SPD
Zero Sequence Reactance % on Rating | Yes | SPD
Winding Arrangement | Yes | SPD
Tap Changer range +%to-% | Yes | SPD
Tap Changer step size % | Yes | SPD
Tap Changer type (ON/OFF) | Yes | SPD
Earthing details (Direct/Resistance/Reactance) | Yes | SPD
Earthing Impedance Method | Yes | SPD
AUTO TRANSFORMER DATA 3-WINDING (PC.A.2.2.5)
HV Node | Yes | SPD
HV (kV) | Yes | SPD
LV Node | Yes | SPD
LV (kV) | Yes | SPD
Rating MVA | Yes | SPD
Transformer Identity | Yes | SPD
Positive Phase Sequence Reactance % on Rating With Min. Tap | Yes | SPD
Positive Phase Sequence Reactance % on Rating With Min. Tap | Yes | SPD
Positive Phase Sequence Reactance % on Rating With Normal Tap | Yes | SPD
Positive Phase Sequence Resistance % on Rating With Min. Tap | Yes | SPD
Positive Phase Sequence Resistance % on Rating With Min. Tap | Yes | SPD
Positive Phase Sequence Resistance % on Rating With Normal Tap | Yes | SPD
Zero Sequence Reactance % on Rating | Yes | SPD
Winding Arrangement | Yes | SPD
Tap Changer range +%to-% | Yes | SPD
Tap Changer step size % | Yes | SPD
Tap Changer type (ON/OFF) | Yes | SPD
Earthing details (Direct/Resistance/Reactance) | Yes | SPD
Earthing Impedance Method | Yes | SPD
SWITCHGEAR DATA (PC.A.2.2.6(a))
Location | Yes | SPD
Switchgear Identity | Yes | SPD
Rated Voltage kV rms | Yes | SPD
Operating Voltage kV rms | Yes | SPD
Make | Yes (if existing connection) | SPD
Model | Yes (if existing connection) | SPD
Type | Yes (if existing connection) | SPD
Year Commissioned | Yes (if existing connection) | SPD
Assumed Circuit Breaker Operating Time (ms) | Yes (if existing connection) | SPD
Assumed Minimum Protection & Trip Relay Operating Time (mS) | Yes (if existing connection) | SPD
Assumed Total Operating Time (mS) | Yes (if existing connection) | SPD
Continuous Rating (A) | Yes | SPD
Fault Rating (RMS Symmetrical) (3 phase) (MVA) | Yes | SPD
Fault Break Rating (RMS Symmetrical) (3 phase) (kA) | Yes | SPD
Fault Break Rating (Peak Asymmetrical) (3 phase) (kA) | Yes | SPD
Fault Make Rating (Peak Asymmetrical) (3 phase) (kA) | Yes | SPD
Fault Rating (RMS Symmetrical) (1 phase) (MVA) | Yes | SPD
Fault Break Rating (RMS Symmetrical) (1 phase) (kA) | Yes | SPD
Fault Break Rating (Peak Asymmetrical) (1 phase) (kA) | Yes | SPD
Fault Make Rating (Peak Asymmetrical) (1 phase) (kA) | Yes | SPD
DC time constant at testing of asymmetrical breaking ability (s) | Yes | SPD
REACTIVE COMPENSATION EQUIPMENT (PC.A.2.4(e))
Item Name | Yes | SPD
Node | Yes | SPD
Rated Voltage (kV) | Yes | SPD
Device No. | Yes | SPD
Rating (MVAr) | Yes | SPD
P Loss (kW) | Yes (if existing connection) | SPD
Tap range | Yes | SPD
Connection Arrangement (Manually/Automatically Switched) | Yes | SPD
REACTIVE COMPENSATION (SVC Modelling Data (PC.A.2.4.1(e)(iii)))
HV Node | Yes | SPD
LV Node | Yes | SPD
Control Node | Yes | SPD
Nominal Voltage (kV) | Yes | SPD
Target Voltage (kV) | Yes | SPD
Max MVAr at HV | Yes | SPD
Min MVAr at HV | Yes | SPD
Slope % | Yes | SPD
Voltage Dependant Q Limit | Yes | SPD
Normal Running Mode | Yes | SPD
R1 PPS_R | Yes | SPD
X1 PPS_X | Yes | SPD
R0 ZPS_R | Yes | SPD
X0 ZPS_X | Yes | SPD
Transf.Winding Type | Yes | SPD
Connection (Direct/Tertiary) | Yes | SPD
FAULT INFEED DATA TO BE SUBMITTED BY OTSDUW PLANT AND APPARATUS PROVIDING A FAULT INFEED (INCLUDING OTSDUW DC CONVERTERS) (PC.A.2.5.5)
Name of OTSDUW Plant and Apparatus | Yes | SPD
OTSDUW DC Converter type (ie voltage or current source) | Yes | SPD
A submission shall be provided for the contribution of each OTSDUW Plant and Apparatus to the positive, negative and zero sequence components of the short circuit current at the Interface Point and each Connection Point for | Yes | SPD
(i) a solid symmetrical three phase short circuit | Yes | SPD
(ii) a solid single phase to earth short circuit | Yes | SPD
(iii) a solid phase to phase short circuit | Yes | SPD
(iv) a solid two phase to earth short circuit | Yes | SPD
If protective controls are used and active for the above conditions, a submission shall be provided in the limiting case where the protective control is not active. This case may require application of a non-solid fault, resulting in a retained voltage at the fault point. | Yes | SPD
Positive sequence X/R ratio of the equivalent at time of fault at the Interface Point and each Connection Point | Yes | SPD
Positive sequence X/R ratio of the equivalent at time of fault at the Interface Point and each Connection Point | Yes | SPD
Pre-fault voltage (if different from 1.0 p.u.) at fault point (The pre-fault voltage provided above should represent the voltage within the range 0.95 to 1.05 that gives the highest fault current) | Yes | SPD
OTSDUW DC CONVERTER TECHNICAL DATA
OTSDUW DC Converter Name | Yes | SPD
Number of poles, i.e. number of OTSDUW DC Converters | Yes | SPD
Pole arrangement (e.g. monopole or bipole) | Yes | SPD
Return path arrangement | Yes | SPD
Details of each viable operating configuration | Yes | SPD
OTSDUW DC Converter Type (e.g. current or Voltage source) | Yes | SPD
If the busbars at the Interface Point or Connection Point are normally run in separate sections identify the section to which the OTSDUW DC Converter configuration is connected | Yes | SPD
Rated MW import per pole (PC.A.3.3.1) | Yes | SPD
Rated MW export per pole (PC.A.3.3.1) | Yes | SPD
Active Power Transfer Capability (PC.A.3.2.2) MW | Yes | SPD
Interface Point Capacity Mvar | Yes | SPD
OTSDUW DC CONVERTER TRANSFORMER (PC.A.5.4.3.1) | No | DPD II
Rated MVA | No | DPD II
Winding arrangement | No | DPD II
Nominal primary voltage | No | DPD II
Nominal secondary (converter-side) voltage(s) | No | DPD II
Positive sequence reactance with Maximum tap % on MVA | No | DPD II
Positive sequence reactance with Nominal tap % on MVA | No | DPD II
Positive sequence reactance with Minimum tap % on MVA | No | DPD II
Positive sequence resistance with Maximum tap % on MVA | No | DPD II
Positive sequence resistance with Nominal tap % on MVA | No | DPD II
Positive sequence resistance with Minimum tap % on MVA | No | DPD II
Zero phase sequence reactance % on MVA | No | DPD II
Tap Changer range +%to-% | No | DPD II
Number of steps | No | DPD II
OTSDUW DC CONVERTER NETWORK DATA (PC.A.5.4.3.1 (c)) | No
Rated DC voltage per pole kV | No | DPD II
Rated DC current per pole A | No | DPD II
Details of the OTSDUW DC Network described in diagram form including resistance, inductance and capacitance of all DC cables and/or DC lines. Details of any line reactors (including line reactor resistance), line capacitors, DC filters, earthing electrodes and other conductors that form part of the OTSDUW DC Network should be shown. | No | DPD II
Show Only the details Essential at the Application Stage
Show All