## SAOM+LFCBOM
Approach to compliance for methodologies to be produced under SOGL articles 118 and 119
Texts from the Synchronous Area Operational Methodology Document
SOGL Article | requires | Root to Compliance | Art 6 / 10 - NRA approval and consultation | SAOM article number | Methodology Text | GB code | Code version | Section reference
118a | the dimensioning rules for FCR in accordance with Article 153; | COMPLIANT/MAPPING EXISTS | Y | SAOM Article 1 | 1. The GB ESO may use one or more services to meet the Frequency Containment Reserve (FCR) dimensioning requirements set forth in SOGL Article 153. 2. The NETS SQSS and Grid Code specify the standards which are used to dimension the GB services used to meet GB Frequency Containment Reserve (FCR) dimensioning requirements. a. The NETS SQSS specifies the requirement to limit the loss of power infeed risk. b. The Grid Code specifies the reserve holding requirement and identifies the specific losses to be covered by the ESO in order to meet the NETS SQSS and SOGL frequency quality standards. c. The NETS SQSS terminology for infeed loss risk is equivalent to the SOGL defined term for the Reference Incident. 3. The ESO shall determine the Frequency Containment Reserve capacity required for the GB synchronous area at least daily and refine this according to changes in system conditions, through to real time. 4. Market parties will be made aware of the FCR capacity that the ESO has determined through publications on the internet in accordance with SOGL Article 187. | Grid Code | Issue 5, revision 22 | BC1.5.4
[6 empty] | Grid Code | Issue 5, revision 22 | BC1.5.4 b
118b | additional properties of FCR in accordance with Article 154(2); | NOT IN CODES | Y | SAOM Article 2 | 1. All technical properties for GB services, that make up the provision of Frequency Containment Reserves, are specific to those services and no common additional properties are defined here. Individual technical requirements for GB services are published on the ESO’s website and used as part of the prequalification process for those GB services.
118c | The frequency quality defining parameters and the frequency quality target parameters | COMPLIANT/MAPPING EXISTS | Y | SAOM Article 3 | 1. The Frequency Quality Defining Parameters and the Frequency Quality Target Parameters shall remain unaltered from those defined in SOGL Annex III, table 1 and table 2 as follows:- a. Table 1 Frequency quality defining parameters of the GB synchronous area are i standard frequency range ± 200 mHz ii maximum instantaneous frequency deviation 800 mHz iii maximum steady-state frequency deviation 500 mHz iv time to recover frequency 1 minute v frequency recovery range ± 500 mHz vi time to restore frequency 15 minutes vii frequency restoration range not used ± 200 mHz viii alert state trigger time 10 minutes b. Table 2 Frequency quality target parameters of the GB synchronous areas i maximum number of minutes outside the standard frequency range 15,000 2. The ESO shall endeavour to comply with the values for the parameters above and shall verify the fulfilment of the frequency target parameters at least annually. | Grid Code | Issue 5, revision 22 | CC.6.1.2
[6 empty] | NETS SQSS | v2.3 | Section 11 - Unacceptable Frequency Conditions
118m | For the GB synchronous areas, measures to ensure the recovery of energy reservoirs | COMPLIANT/MAPPING EXISTS | Y | SAOM Article 4 | 1. The ESO shall ensure that loss of a providing unit does not endanger operational security by ensuring that the largest connected unit is excluded from those selected when satisfying the need for FCR capacity requirement defined within the FCR dimensioning process. 2. When an FCR providing unit or group trips or can no longer provide an FCR service, the ESO will reallocate the FCR provision to a different FCR unit or FCR Group utilizing operational and commercial information made available by FCR providers. 3. The declared availability of FCR providing units and groups is managed by the FCR providers which reflect the requirement to recover energy reservoirs. Effectively this means that the ESO takes into account the depletion of these reservoirs when procuring FCR. 4. When operating the Frequency Containment Process (FCP) the ESO takes into account depletion of these reservoirs to minimise risk in real time where applicable. | Grid Code | Issue 5, revision 22 | CC.A.3.1
[6 empty] | Grid Code | Issue 5, revision 22 | CC.A.3.5
118y | For the GB synchronous areas, the methodology to determine the minimum provision of reserve capacity on FCR | NOT IN CODES | Y | SOAM Article 5 | 1. The ESO makes sure there is sufficient FCR capacity in GB to meet the dimensioning rules in Article 2. 2. The minimum amount of FCR capacity provided from within GB is determined as follows: The ESO looks at the overall requirements for FCR as defined by the dimensioning rules as stipulated in paragraph 1, and subtracts the maximum amount of FCR exchange and sharing that could be accommodated from other synchronous areas, as per paragraph 3, to establish the minimum provision of reserve capacity of FCR that must be provided within the GB synchronous area. 3. The ESO determines the limits on the amount of FCR exchange and sharing that could be accommodated from other synchronous areas by considering the following: a. Whether sharing of FCR can be accommodated by the ESO under expected system conditions whilst complying with NETS SQSS; b. The ability to transfer FCR between synchronous areas; c. To consider any loss of provision of FCR during a reference incident as defined by SOGL Article 153 (2)(b)(ii); d. Seek minimum cost solution of meeting GB FCR and therein the sharing of FCR, that could be possible subject to meeting points a-c; e. The risk of the probability and impact of FCR short falls that could arise due to exchange and sharing. 4. Market parties will be made aware of the FCR capacity that the ESO has determined through publications on the internet in accordance with SOGL Article 187. The amounts of FCR shared or exchanged with other Synchronous Areas will be published on the ENTSO-E market transparency platform website in accordance with SOGL Article 190.
118z | The methodology to determine limits on the amount of exchange of FRR between synchronous areas and the methodology to determine limits on the amount of sharing of FRR between synchronous areas | NOT IN CODES | Y | SOAM Article 6 | 1. The ESO determines the maximum amount of FRR sharing and exchange that could be accommodated from other synchronous areas by considering the following: a. Whether sharing or exchange of FRR can be accommodated by the ESO under expected system conditions whilst complying with NETS SQSS; b. The ability to transfer FRR between synchronous areas; c. To consider any loss of provision of FRR during a reference incident as defined by SOGL Article 157 (2)(d); d. Seek minimum cost solution of meeting GB FRR and therein the sharing or exchange of FRR, that could be possible subject to meeting points a-c. e. The risk of the probability and impact of FRR short falls that could arise due to sharing. 2. Market parties will be made aware of the FRR capacity that the ESO has determined through publications on the ENTSO-E market transparency platform website in accordance with SOGL Article 188. The amounts of FRR shared or exchanged with other Synchronous Areas will be published on the internet in accordance with SOGL Article 190.
118aa | The methodology to determine limits on the amount of exchange of Replacement Reserves between synchronous areas and the methodology to determine limits on the amount of sharing of Replacement Reserves between synchronous areas | NOT IN CODES | Y | SOAM Article 7 | 1. The ESO determines the maximum amount of RR sharing and exchange that could be accommodated from other synchronous areas by considering the following: a. Whether sharing or exchange of RR can be accommodated by the ESO under expected system conditions whilst complying with NETS SQSS; b. The ability to transfer RR between synchronous areas; c. To consider any loss of provision of RR during a reference incident as defined by SOGL Article 160(3)(c); d. Seek minimum cost solution of meeting GB RR and therein the sharing or exchange of FRR, that could be possible subject to meeting points a-c. e. The risk of the probability and impact of RR short falls that could arise due to sharing or exchange. 2. Market parties will be made aware of the RR capacity that the ESO has determined through publications on the ENTSO-E market transparency platform website in accordance with SOGL Article 189. The amounts of RR shared or exchanged with other Synchronous Areas will be published on the internet in accordance with SOGL Article 190.
118e | The methodology to assess the risk and the evolution of the risk of exhaustion of FCR of the synchronous area | COMPLIANT/MAPPING EXISTS | N | SAOM Article 8 | 1. The ESO determines the maximum amount of RR sharing and exchange that could be accommodated from other synchronous areas by considering the following: a. Whether sharing or exchange of RR can be accommodated by the ESO under expected system conditions whilst complying with NETS SQSS; b. The ability to transfer RR between synchronous areas; c. To consider any loss of provision of RR during a reference incident as defined by SOGL Article 160(3)(c); d. Seek minimum cost solution of meeting GB RR and therein the sharing or exchange of FRR, that could be possible subject to meeting points a-c. e. The risk of the probability and impact of RR short falls that could arise due to sharing or exchange. 2. Market parties will be made aware of the RR capacity that the ESO has determined through publications on the ENTSO-E market transparency platform website in accordance with SOGL Article 189. The amounts of RR shared or exchanged with other Synchronous Areas will be published on the internet in accordance with SOGL Article 190. | Grid Code | Issue 5, revision 22 | CC.6.3.7
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.12
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.13
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.14
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.1
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.3
[6 empty] | Grid Code | Issue 5, revision 22 | ECC.6.3.3
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.4(a)
118f | The synchronous area monitor | NON-REG PUBLICATION | N | SOAM Article 9 | 1. The ESO is the Synchronous Area Monitor for the GB Synchronous Area and will fulfil the frequency reporting and monitoring functions set forth in SOGL Article 133.
118i | The LFC structure; | NON-REG PUBLICATION | N | SOAM Article 10 | 1. In accordance with Article 139 of the SOGL all TSOs of the Synchronous Area GB hereby define: a. the Process Responsibility Structure; and b. the Process Activation Structure. 2. The GB Process Responsibility Structure is defined as follows a. The current Process Responsibility Structure per Article 141 of the SOGL is defined in the methodology for the determination of LFC blocks in GB. b. The operation of Load-Frequency Control processes is based on operational areas, where every area has their own responsibilities in the LFC structure. The overall body is the Synchronous Area in which frequency and phase are the same for the whole area. The Synchronous Area GB consists of a single LFC Block, this LFC Block consists of a single LFC Area. The LFC Area itself consists of a single Monitoring Area, which also consist of a single Scheduling Areas. c. Each of these operational areas has their own obligations: A Scheduling Area is responsible for the scheduling process in that area. A Monitoring Area has in addition to the scheduling the obligation to calculate and measure the active power interchange in real-time in that area. A LFC Area has the additional obligation to fulfil the Frequency Restoration Quality Target Parameters by using the Frequency Restoration Process. A LFC Block is additionally responsible for the dimensioning of Frequency Restoration Reserves (FRR) and Replacement Reserves (RR). The Synchronous Area has the obligation to fulfil the Frequency Quality Target Parameters by using the Frequency Containment Process (FCP). Within GB all these obligations and processes fall to the single electricity system operator. d. The GB Synchronous Area is demarcated by the point at which power is converted from AC into DC for transfer by HVDC interconnectors. 3. There are no virtual tie-lines utilised within the GB. a. All generation modules and demand facilities are directly connected to the GB electricity system and not via virtual tie-lines; in so-much as there is only a single LFC-Area in GB. No modules outside of the GB area are controlled via this mechanism. 4. In accordance with SOGL Article 140 (1) the mandatory processes are: a. the Frequency Containment Process (FCP); b. the Frequency Restoration Process (FRP), which is a 100% manual Frequency Restoration Process 5. In accordance with SOGL Article 140 (2) the optional processes are: a. the Reserve Replacement Process (RRP); b. the Cross-Border FRR Activation Processes, c. the Cross-Border RR Activation Process d. the Time Control Process 6. The following processes types defined in SOGL are not currently part of the GB Process Activation Process: a. the Imbalance Netting Process; b. automatic Frequency Restoration Process (aFRP) as defined in Article 145 (1). 7. The Process Activation Structure of the Synchronous Area GB is implemented in the single GB LFC Area according to the control process in a. The control error, i.e. input, of the FCP is the frequency deviation; b. The manual Frequency Restoration Process (mFRP) and Reserve Replacement Process (RRP) are the mechanisms used to activate mFRR and RR by the TSO. Activations are based on observed or expected imbalances. mFRR and RR is activated in order to return FCR providers to their resting state; 8. The Frequency Containment Process (FCP) in the LFC Area GB shall be implemented according to SOGL Article 142. 9. The Frequency Restoration Process (FRP) in the LFC Area GB shall be organised and operated by the ESO in order to bring the GB, Frequency Restoration Control Error (Δf) within the GB frequency recovery range within the GB time to restore frequency, in accordance with SOGL Article 143. The GB FRP is 100% manual. The manual Frequency Restoration Process shall be operated through instructions for manual FRR activation in accordance with SOGL Article 145(5). 10. The Reserve Replacement Process (RRP) in the LFC Area GB shall be organised and operated by the ESO to progressively restore the activated FCR and FRR, in accordance with SOGL Article 144(1)(c). 11. GB does not operate an aFRP and therefore no properties for a Frequency Restoration Controller are defined.
118j | The methodology to reduce the electrical time deviation; | NON-REG PUBLICATION | N | SOAM Article 11 | Within the GB synchronous area, the ESO controls the electrical system time as specified in the Grid Code
118l | Operational procedures in case of exhausted FCR | COMPLIANT/MAPPING EXISTS | N | SAOM Article 12 | 1. Ensuring sufficient FCR capacity is available to ESO under commercial arrangements: a. In order to ensure that the sufficient FCR capacity is made available in all timescales to the ESO, the Grid Code defines obligations for certain grid users to i. have the capability to provide FCR services to the ESO, and ii. a requirement to make those FCR services commercially available to the ESO. b. Those reserve services that are critical to ensuring sufficient FCR capacity offering in GB are defined in Grid Code. 2. Procedures performed in control timescales where FCR provision from FCR providers is eroded below the dimensioning requirement: a. The approach to managing active FCR provision by the ESO is such that every endeavour is taken to ensure that requirements and risks relating to FCR exhaustion are managed on a continuous basis. This should ensure that a point of critically reduced or exhausted FCR holding is never reached. Where operational conditions arise that result in depletion of FCR capability, the ESO will: i. Reduce the size of the reference incident so it can be secured with the available FCR. ii. Call on ancillary service provision and put additional units in response mode iii. Call upon emergency restoration of transmission equipment on outage or arm inter-tripping generation to relieve any generation that has been in a transmission congestion iv. If points i to iii above are insufficient or unachievable the ESO will issue the appropriate National Electricity Transmission System Warning and actions as defined in the Grid Code. | Grid Code | Issue 5, revision 22 | BC3.4.3
118n | Operational procedures to reduce the system frequency deviation to restore the system state to normal state and to limit the risk of entering into the emergency state; | COMPLIANT/MAPPING EXISTS | N | SAOM Article 13 | 1. When the GB electricity system is in an Alert State, due to frequency deviation or depletion of reserves, the ESO will issue the appropriate National Electricity Transmission System Warning and actions as defined in the Grid Code to ensure that system needs and available reserve resources match. | Grid Code | Issue 5, revision 22 | CC.A.3
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.7
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.12
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.13
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.14
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.1
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.7(f)
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.4(e)
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.4(f)
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.4(a)
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.2; CC.6.3.3; ECC.6.3.3
[6 empty] | Grid Code | Issue 5, revision 22 | OC6.5; OC6.7.1
[6 empty] | Grid Code | Issue 5, revision 22 | OC7.4.8, BC2.9
118o | The roles and responsibilities of the TSOs implementing an imbalance netting process, a cross-border FRR activation process or a cross-border RR activation process | COMPLIANT/MAPPING EXISTS | N | SAOM Article 14 | 1. No Imbalance Netting Process is in place within GB or between GB and other LFC Blocks of other Synchronous Areas. 2. FRR activation processes used by the ESO are defined in interconnector operator protocols and agreed with the ESO in GB, TSOs that operate an Interconnector, the connecting TSOs and where relevant affected TSOs. 3. RR activation processes used by the ESO are defined in interconnector operator protocols and agreed with the ESO in GB, TSOs that operate an Interconnector, the connecting TSOs and where relevant affected TSOs. | Grid Code | Issue 5, revision 22 | OC6.5; OC6.7.1
[6 empty] | Grid Code | Issue 5, revision 22 | OC7.4.8, BC2.9
118p | Requirements concerning the availability, reliability and redundancy of the technical infrastructure | NON-REG PUBLICATION | N | SOAM Article 15 | 1. All BM participants must ensure that appropriate electronic data communication facilities are in place to permit the submission of data as required by the Grid Code and Relevant Electrical Standards. Requirements for non-BM participants shall be defined by Bilateral agreements. National Grid shall maintain compliance standards as detailed in internal Business Requirements Documents. 2. The minimum requirements for the availability, reliability and redundancy of the technical infrastructure shall be in line with the CNI Architecture Principles. The quality standards shall be in accordance with the GE Standards XA. Availability and redundancy of communication infrastructure shall be in accordance with the National Grid Technical Specification NG TS 3.24.20. Finally, all communication protocols must comply with standard protocols ICCP-1996, IEC101 and GI-74.
118q | Common rules for the operation in normal state and alert state and the control actions required | COMPLIANT/MAPPING EXISTS | N | SAOM Article 16 | 1. Common rules for normal state as defined by SOGL Article 14 are the general nature of Load, Frequency Control. The SAOM Article 14 defines the general control structures used in a normal state. 2. Common rules for the alert state as defined by SOGL Article 18 are as per SAOM Article 17 | Grid Code | Issue 5, revision 22 | CC.6.5
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.5.3; CC.6.5.8; CC.6.5.9
118u | The roles and responsibilities of the reserve connecting TSO, the reserve receiving TSO and the affected TSO for the exchange of reserves between synchronous areas, and of the control capability providing TSO, the control capability receiving TSO and the affected TSO for the sharing of reserves between synchronous areas | NON-REG PUBLICATION | N | SOAM Article 17 | 1. Within the GB Synchronous Area, for any reserve exchanged or reserves shared with other areas, the ESO will be the reserve connecting TSO. The ESO will be the TSO which instructs the provision of reserves within GB borders and also agrees to their transfer to another region via HVDC. Where the ESO is requesting reserves from another area the ESO expects the other area to instruct the necessary reserves, if the other area can accommodate the request given its real time and expected system conditions, to enable provision of that service. Insomuch, the ESO will fulfil the roles specified in the Article title and as defined in SOGL Article 3.
118w | The methodology to determine limits on the amount of sharing of FCR between synchronous areas | NON-REG PUBLICATION | N | SOAM Article 18 | 1. The ESO looks at the overall requirements for FCR as defined by the dimensioning rules and subtracts the maximum amount of FCR sharing that could be accommodated from other synchronous areas, as determined below, to establish the minimum provision of reserve capacity of FCR in the GB synchronous area. 2. Limits on the sharing of FCR between the GB synchronous area and other synchronous areas are determined in the following manner: a. Whether sharing of FCR can be accommodated by the ESO under expected system conditions whilst complying with NETS SQSS; b. The ability to transfer FCR between synchronous areas; c. To consider any loss of provision of FCR during a reference incident as defined by SOGL Article 153 (2)(b)(ii); d. Seek minimum cost solution of meeting GB FCR and therein the exchange of FCR that could be possible subject to meeting points a-c; e. The risk of the probability and impact of FCR short falls that could arise due to sharing.
ARTICLE 119 Texts from the LFC Block Opeational Methodology Document
119c | Ramping restrictions for active power output | NOT IN CODES | Y | LFCBOM Article 1 | 1. Rules for ramping restrictions on the active power output of each HVDC interconnector between a LFC Block of another synchronous area and the GB LFC block, in accordance with SOGL Article 137(3): a. The ESO, and the connecting TSOs supervising a LFC block of an HVDC interconnector shall have the right to determine common ramping restrictions in the form of ramping periods and/or maximum ramping rates and shall enter into agreement with the TSOs responsible for operating the interconnector, to determine the processes and mechanisms by which these restrictions will be put in place. These ramping restrictions shall not apply to imbalance netting, frequency coupling, cross-border activation of FRR or cross-border activation of RR. These ramping restrictions shall not apply to any service aimed at maintaining or returning one of the connected electricity systems to a normal system state. The common restriction shall also take into account the restrictions set in the GB synchronous area operational agreement in accordance with SOGL Article 137(1), if applicable; b. The ramping restrictions for each interconnector shall be applied in a non-discriminatory manner. The ESO shall ensure alignment of ramping restrictions between all HVDC interconnectors linking the same two synchronous areas, taking into account the technical capabilities of each HVDC interconnector; c. A summary of the ramping-restrictions to be applied to HVDC interconnectors connecting to the GB LFC Block, shall be published by the ESO on its website at least one week before the rules are enforced, in accordance with the obligations in SOGL Article 8; d. The ESO, in order to prevent the GB LFC block from entering into an emergency state, may restrict equitably the ramp rates of GB interconnectors between GB and the same connecting synchronous areas, in coordination with the affected national TSOs and affected interconnector operators according to the terms referred to paragraph (a) of this Article; e. Within 30 calendar days of an incident which restricted one or more of the HVDC interconnectors, under the process referred to in paragraph (d), the ESO shall prepare a report containing an explanation of the rationale, implementation and impact of this action and submit it to the relevant regulatory authority in accordance with Article 37 of Directive 2009/72/EC and neighbouring TSOs, and also make the report available to all significantly affected system users.
119c | Ramping restrictions for active power output on generation modules and demand units connecting with the area of the GB LFC Block | COMPLIANT/MAPPING EXISTS | Y | LFCBOM Article 2 | 1. Rules regarding power generation modules and demand units connected to the electricity system within the GB LFC Block: a. Active restrictions on ramping restrictions on GB generation modules and demand units will apply where specified in the Grid Code. | Grid Code | Issue 5, revision 22 | BC1A.1.1
119h | The FRR dimensioning rules | COMPLIANT/MAPPING EXISTS | Y | LFCBOM Article 3 | 1. The GB ESO may use one or more services to meet the Frequency Restoration Reserve dimensioning requirements. 2. The NETS SQSS and Grid Code specify the standards which are used to dimension the GB services used to meet GB Frequency Restoration Reserve (FRR) dimensioning requirements: a. FRR dimensioning is met 100% by manual FRR in GB; b. The NETS SQSS specifies the requirement to limit the loss of power infeed risk. The NETS SQSS terminology for infeed loss risk is equivalent to the SOGL defined term for the dimensioning incident; c. The Grid Code specifies the reserve holding requirement and identifies the specific losses to be covered by the ESO in order to meet the NETS SQSS and SOGL frequency quality standards. In somuch the ESO ensures that i. there is sufficient positive and negative reserve capacity on FRR, 1. in procurement timescales where FRR services are tendered; and 2. monitoring and adjusting these to changes in system requirements and service availability through to real-time; ii. the capacity will meet positive and negative LFC block imbalances, 99% of the time based on statistical analysis of historical imbalance data from previous years; iii. when conducting FRR sharing or exchange the risk of non-delivery will be factored into dimensioning and the ESOs continuous processes for reserve management; 3. Market parties will be made aware of the FRR capacity that the ESO has determined through publications on the internet in accordance with SOGL Article 188. | NETS SQSS | v2.3 | Section 2.5
[6 empty] | NETS SQSS | v2.3 | Section 2.6
[6 empty] | Grid Code | Issue 5, revision 22 | BC1.5.4
[6 empty] | Grid Code | Issue 5, revision 22 | BC1.5.4(b)
119r | Measures to reduce the Frequency Restoration Control Error (FRCE) by requiring changes in the active power production or consumption of power generating modules and demand units | NOT IN CODES | Y | LFCBOM Article 4 | 1. Measures to reduce Frequency Restoration Control Error (FRCE) in GB are defined in the GB Grid Code. This includes: a. Measures to ensure sufficient positive and negative reserve capacity through market notices and warnings and emergency instructions b. Measures to correct the frequency through use of emergency instructions 2. The ESO may enter into agreements, where necessary, with specific parties to supplement these measures in accordance with its license to operate the system. | Grid Code | Issue 5, revision 22 | BC1.5.4 and OC7.4.8
[6 empty] | Grid Code | Issue 5, revision 22 | BC2.9 and OC6.5
119b | LFC block monitor | NON-REG PUBLICATION | N | LFCBOM Article 5 | 1. The ESO performs the role of the LFC block monitor in GB.
119g | Operational procedures in case of exhausted FRR and RR | NON-REG PUBLICATION | N | LFCBOM Article 6 | 1. Ensuring sufficient FRR capacity is available to ESO under commercial arrangements: a. In order to ensure that the sufficient FRR capacity is made available in all timescales to the ESO, the Grid Code defines obligations for certain grid users to i. have the capability to provide FRR services to the ESO, and ii. a requirement to make those FRR services commercially available to the ESO. b. Those FRR services that are critical to ensuring sufficient FRR capacity offering in GB are defined in Grid Code. 2. Procedures performed in control timescales where FRR or RR provision from reserve providers is eroded below the dimensioning requirement: a. The approach to Frequency Restoration Reserve and Replacement Reserve management by the ESO is such that every endeavour is taken to ensure that requirements and risks are managed continuously and that a point of critically reduced or no FRR or RR is ever reached. Where operational conditions arise resulting in depletion of FRR or RR capability, the GB electricity system operator will: i. Put additional units in response mode; ii. Call on enhanced ancillary service provision; iii. Call upon emergency restoration of transmission equipment on outage or arm inter-tripping generation to relieve any generation that has been in a transmission congestion zone; iv. Or in more extreme circumstance disconnect load or generation to realign requirements with available provision.
119g | The RR dimensioning rules defined | NON-REG PUBLICATION | N | LFCBOM Article 7 | 1. The GB ESO may use one or more services to meet the Reserve Replacement dimensioning requirements. 2. The NETS SQSS and Grid Code specify the standards which are used to dimension the GB services used to meet GB Restoration Reserve (RR) dimensioning requirements: a. The NETS SQSS specifies the requirement to limit the loss of power infeed risk. The NETS SQSS terminology for infeed loss risk is equivalent to the SOGL defined term for the dimensioning incident. b. The Grid Code specifies the reserve holding requirement and identifies the specific losses to be covered by the ESO in order to meet the NETS SQSS and SOGL frequency quality standards. In so much the ESO ensures that i. there are sufficient positive and negative reserve capacity on RR, 1. in procurement timescales where RR services are tendered; and 2. monitoring and adjusting these to changes in system requirements and service availability through to real-time. ii. the capacity will meet positive and negative LFC block imbalances, 99% of the time based on statistical analysis of historical imbalance data from previous years; iii. the RR capacity is sufficient to maintain frequency quality inside the FRCE quality targets from SOGL Article 128(5) & (6) and Annex IV, table. iv. when conducting RR sharing or exchange the risk of non-delivery will be factored into dimensioning and also the ESOs continuous process for reserve management, considering the potential impact on FRCE quality targets. v. when conducting RR sharing the ESO will ensure that the reduction in positive or negative capacity on RR does not exceed the remaining reserve capacity of RR of the GB LFC Block. 3. Market parties will be made aware of the RR capacity that the ESO has determined through publications on the internet in accordance with SOGL Article 189. | Grid Code | Issue 5, revision 22 | CC.6.3.7
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.12
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.13
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.14
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.1
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.3
[6 empty] | Grid Code | Issue 5, revision 22 | ECC.6.3.3
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.4(a)
[6 empty] | Grid Code | Issue 5, revision 22 | CC.6.3.7(f)
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.4(e)
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.4(f)
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.4(a)
[6 empty] | Grid Code | Issue 5, revision 22 | BC3.5.2; CC.6.3.3; ECC.6.3.3
[6 empty] | Grid Code | Issue 5, revision 22 | OC6.5; OC6.7.1
[6 empty] | Grid Code | Issue 5, revision 22 | OC7.4.8, BC2.9
119k | The escalation procedure and, if applicable, the escalation procedure | NON-REG PUBLICATION | N | LFCBOM Article 8 | 1. Within the GB LFC Block if it is anticipated that there will not be sufficient Frequency Restoration Reserves or Replacement Reserves capacity, and there is sufficient time, a market warning is to be issued in accordance with requirements of the Grid Code. 2. Other European TSOs outside of GB will be informed of a change in System State via the ENTSO-E Emergency Awareness System. | NETS SQSS | v2.3 | Section 2.5
[6 empty] | NETS SQSS | v2.3 | Section 2.6
[6 empty] | Grid Code | Issue 5, revision 22 | BC1.5.4
[6 empty] | Grid Code | Issue 5, revision 22 | BC1.5.4(b)
119l | The FRR availability requirements, the requirements on the control quality and the RR availability requirements and the requirements on the control quality | NON-REG PUBLICATION | N | LFCBOM Article 9 | 1. In the GB LFC Block, the Reserve categories of Frequency Restoration Reserves and Replacement is comprised of multiple reserve services. 2. In the GB LFC Block, the ESO define the necessary Frequency Restoration Reserve and Replacement Reserve availability requirements and control quality requirements within the technical requirements of each reserve service and the associated contracts. 3. The ESO ensures that the needs of the Frequency Restoration Process and Reserve Replacement Process are met by the particular capacities of services it has selected. | Grid Code | Issue 5, revision 22 | OC6.5; OC6.7.1
[6 empty] | Grid Code | Issue 5, revision 22 | OC7.4.8, BC2.9
119o | Roles and the responsibilities of the control capability providing TSO, the control capability receiving TSO and of the affected TSO for the sharing of FRR and RR between synchronous areas | NON-REG PUBLICATION | N | LFCBOM Article 10 | 1. For any exchange or sharing of reserves undertaken between GB with the LFC Blocks of Other synchronous areas via HVDC interconnectors, the ESO will be the only counter-party to TSOs providing or receiving services in those other synchronous areas. Insomuch, 2. Specific arrangements for the activation of reserves across HVDC interconnectors will require the ESO to be: a. the control capability providing TSO when it is activating reserves to be provided to another TSO under a reserve sharing agreement; b. the control capability receiving TSO when it is receiving reserves under a reserve sharing agreement; c. the affected TSO when reserve power required by one TSO is required by another TSO and it traverses GB under a reserve sharing agreement. | BSC | BSC/V15.0 | Section K-3, section 3.1.1
[6 empty] | Grid Code | Issue 5, revision 22 | BC1.4