## Notes
Subject | Notes
System inertia: method of calculation | H=(f*∆P)/(2*RoCoF) H is system inertia; f is the starting frequency; ∆P is the system imbalance; RoCoF is the rate of change of frequency; Note that smaller losses will have less accurate system inertia calculations
RoCoF: method of calculation | RoCoF=(f_500ms-f_0ms)/500ms RoCoF is calculated using 500ms sliding window. RoCoF is the rate of change of frequency; f is the frequency; Note that smaller losses will have less accurate ROCOF calculations
Voltage Dip | Transient Voltage Dip with loss % and duration measured at the local substation
'Immediately before the Significant Event' | The starting frequency indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.
'Immediately after the Significant Event' | The maximum frequency deviation indicated in the Frequency Event Report, for frequency excursions. Where there is no Frequency Event Report, NGESO will use its best judgement.

## Report
|  |  |  | (i) the time(s) in hh.mm.ss of the Significant Event and any potentially related occurrences; | (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available; | (iii) the Frequency record (in table and graphical format) at <=1 second intervals for 1 minute before and 1 minute after the Significant Event; | (iv) the Frequency (to 2 decimal places) immediately before the Significant Event; | (v) the Frequency (to 2 decimal places) immediately after the Significant Event; | (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms; | (vii) where known, the MW of all individual losses or trips related to the Significant Event; |  | (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event; | (ix) the location of any reported Transmission fault on the network diagram and geographically; | (x) the extent of any voltage dip associated with the Significant Event; | (xi) an estimate of system inertia in MWs at the time of the Significant Event along with how it has been calculated; and | (xii) any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and
Event Ref | Event Name | Notes | Date (Local) | Time (Local) | Loss of Embedded Power Station | Frequency Record | Pre-Event Frequency | Post-Event Frequency | RoCoF over 500ms | Individual Loss | Total loss | Demand loss of Users/DNOs related to event | Location of transmission fault | Voltage Dip | System Inertia | Additional data
Event Date-Number | Text | Text | DD/MM/YYYY | hh:mm:ss | MW | Text | Hz | Hz | Hz/s | Text+MW | MW | Text+MW | Text | % | GWs | Text
Event 20191203-1 | Trip of SPLN-1 |  | 2019-12-03 | 20:00 | N/A | Refer to tab 'Event 20191203-1' | 50.06 | 49.688 | -0.068 | 862 | -862 | N/A | N/A | N/A | 317.2921
Event 20191209-1 | Trip of ROCK-1 and EECL-1 |  | 2019-12-09 | 16:07 | N/A | Refer to tab 'Event 20191209-1' | 49.858 | 49.69 | -0.035 | ROCK-1 175, EECL-1 369 | -544 | N/A | N/A | N/A | 387.4679
Event 20191212-1 | Trip of CNQPS-4 |  | 2019-12-12 | 6:02 | N/A | Refer to tab 'Event 20191212-1' | 49.925 | 49.837 | -0.029 | 350 | -350 | N/A | N/A | N/A | 301.2716
Event 20191216-1 | IFA ramp up | Coincident with sudden demand drop | 2019-12-16 | 6:52 | N/A | Refer to tab 'Event 20191216-1' | 50 | 50.316 | 0.005 | N/A | N/A | N/A | N/A | N/A | N/A
Event 20191217-1 | Trip of IFA Bipole 2 |  | 2019-12-17 | 10:53 | N/A | Refer to tab 'Event 20191217-1' | 50.095 | 49.705 | -0.065 | 900 | -900 | N/A | N/A | N/A | 346.8115
Event 20191221-1 | Loss of SPLN-1 | GT tripped | 2019-12-21 | 22:12 | N/A | Refer to tab 'Event 20191221-1' | 50.011 | 49.859 | -0.032 | 507 | -507 | N/A | N/A | N/A | 396.1809
Event 20191222-1 | Trip of IFA Bipole 2 |  | 2019-12-22 | 18:02 | N/A | Refer to tab 'Event 20191222-1' | 50.055 | 49.689 | -0.082 | 995 | -995 | N/A | N/A | N/A | 303.6873
Event 20191226-1 | Trip of IFA |  | 2019-12-26 | 7:42 | N/A | Refer to tab 'Event 20191226-1' | 50.05 | 49.908 | -0.051 | 400 | -400 | N/A | N/A | N/A | 196.2745

## Event 20191203-1
In UTC
Date | Time | Freq
2019-12-03 | 19:59 | 49.995
2019-12-03 | 19:59 | 49.99
2019-12-03 | 19:59 | 49.985
2019-12-03 | 19:59 | 49.982
2019-12-03 | 19:59 | 49.976
2019-12-03 | 19:59 | 49.974
2019-12-03 | 19:59 | 49.969
2019-12-03 | 19:59 | 49.968
2019-12-03 | 19:59 | 49.964
2019-12-03 | 19:59 | 49.963
2019-12-03 | 19:59 | 49.961
2019-12-03 | 19:59 | 49.964
2019-12-03 | 19:59 | 49.965
2019-12-03 | 19:59 | 49.968
2019-12-03 | 19:59 | 49.969
2019-12-03 | 19:59 | 49.97
2019-12-03 | 19:59 | 49.969
2019-12-03 | 19:59 | 49.971
2019-12-03 | 19:59 | 49.97
2019-12-03 | 19:59 | 49.972
2019-12-03 | 19:59 | 49.971
2019-12-03 | 19:59 | 49.971
2019-12-03 | 19:59 | 49.971
2019-12-03 | 19:59 | 49.97
2019-12-03 | 19:59 | 49.969
2019-12-03 | 19:59 | 49.968
2019-12-03 | 19:59 | 49.969
2019-12-03 | 19:59 | 49.968
2019-12-03 | 19:59 | 49.967
2019-12-03 | 19:59 | 49.963
2019-12-03 | 20:00 | 49.963
2019-12-03 | 20:00 | 49.961
2019-12-03 | 20:00 | 49.958
2019-12-03 | 20:00 | 49.956
2019-12-03 | 20:00 | 49.956
2019-12-03 | 20:00 | 49.955
2019-12-03 | 20:00 | 49.955
2019-12-03 | 20:00 | 49.956
2019-12-03 | 20:00 | 49.956
2019-12-03 | 20:00 | 49.957
2019-12-03 | 20:00 | 49.958
2019-12-03 | 20:00 | 49.957
2019-12-03 | 20:00 | 49.958
2019-12-03 | 20:00 | 49.959
2019-12-03 | 20:00 | 49.961
2019-12-03 | 20:00 | 49.963
2019-12-03 | 20:00 | 49.967
2019-12-03 | 20:00 | 49.969
2019-12-03 | 20:00 | 49.97
2019-12-03 | 20:00 | 49.972
2019-12-03 | 20:00 | 49.972
2019-12-03 | 20:00 | 49.971
2019-12-03 | 20:00 | 49.97
2019-12-03 | 20:00 | 49.971
2019-12-03 | 20:00 | 49.967
2019-12-03 | 20:00 | 49.967
2019-12-03 | 20:00 | 49.962
2019-12-03 | 20:00 | 49.961
2019-12-03 | 20:00 | 49.959
2019-12-03 | 20:00 | 49.96
2019-12-03 | 20:00 | 49.957
2019-12-03 | 20:00 | 49.956
2019-12-03 | 20:00 | 49.955
2019-12-03 | 20:00 | 49.954
2019-12-03 | 20:00 | 49.957
2019-12-03 | 20:00 | 49.96
2019-12-03 | 20:00 | 49.963
2019-12-03 | 20:00 | 49.968
2019-12-03 | 20:00 | 49.972
2019-12-03 | 20:00 | 49.977
2019-12-03 | 20:00 | 49.981
2019-12-03 | 20:00 | 49.985
2019-12-03 | 20:00 | 49.991
2019-12-03 | 20:00 | 49.995
2019-12-03 | 20:00 | 50
2019-12-03 | 20:00 | 50.006
2019-12-03 | 20:00 | 50.009
2019-12-03 | 20:00 | 50.014
2019-12-03 | 20:00 | 50.018
2019-12-03 | 20:00 | 50.022
2019-12-03 | 20:00 | 50.023
2019-12-03 | 20:00 | 50.026
2019-12-03 | 20:00 | 50.028
2019-12-03 | 20:00 | 50.029
2019-12-03 | 20:00 | 50.028
2019-12-03 | 20:00 | 50.027
2019-12-03 | 20:00 | 50.026
2019-12-03 | 20:00 | 50.026
2019-12-03 | 20:00 | 50.026
2019-12-03 | 20:00 | 50.024
2019-12-03 | 20:00 | 50.016
2019-12-03 | 20:01 | 49.964
2019-12-03 | 20:01 | 49.907
2019-12-03 | 20:01 | 49.859
2019-12-03 | 20:01 | 49.821
2019-12-03 | 20:01 | 49.787
2019-12-03 | 20:01 | 49.76
2019-12-03 | 20:01 | 49.738
2019-12-03 | 20:01 | 49.721
2019-12-03 | 20:01 | 49.707
2019-12-03 | 20:01 | 49.699
2019-12-03 | 20:01 | 49.693
2019-12-03 | 20:01 | 49.691
2019-12-03 | 20:01 | 49.69
2019-12-03 | 20:01 | 49.693
2019-12-03 | 20:01 | 49.695
2019-12-03 | 20:01 | 49.697
2019-12-03 | 20:01 | 49.702
2019-12-03 | 20:01 | 49.706
2019-12-03 | 20:01 | 49.709
2019-12-03 | 20:01 | 49.711
2019-12-03 | 20:01 | 49.713
2019-12-03 | 20:01 | 49.716
2019-12-03 | 20:01 | 49.717
2019-12-03 | 20:01 | 49.719
2019-12-03 | 20:01 | 49.719
2019-12-03 | 20:01 | 49.719
2019-12-03 | 20:01 | 49.717
2019-12-03 | 20:01 | 49.718
2019-12-03 | 20:01 | 49.717
2019-12-03 | 20:01 | 49.717
2019-12-03 | 20:01 | 49.715
2019-12-03 | 20:01 | 49.715
2019-12-03 | 20:01 | 49.713
2019-12-03 | 20:01 | 49.711
2019-12-03 | 20:01 | 49.708
2019-12-03 | 20:01 | 49.705
2019-12-03 | 20:01 | 49.703
2019-12-03 | 20:01 | 49.702
2019-12-03 | 20:01 | 49.7
2019-12-03 | 20:01 | 49.702
2019-12-03 | 20:01 | 49.702
2019-12-03 | 20:01 | 49.702
2019-12-03 | 20:01 | 49.7
2019-12-03 | 20:01 | 49.7
2019-12-03 | 20:01 | 49.699
2019-12-03 | 20:01 | 49.699
2019-12-03 | 20:01 | 49.701
2019-12-03 | 20:01 | 49.702
2019-12-03 | 20:01 | 49.705
2019-12-03 | 20:01 | 49.707
2019-12-03 | 20:01 | 49.708
2019-12-03 | 20:01 | 49.711
2019-12-03 | 20:01 | 49.711
2019-12-03 | 20:01 | 49.713
2019-12-03 | 20:01 | 49.716
2019-12-03 | 20:01 | 49.717
2019-12-03 | 20:01 | 49.72
2019-12-03 | 20:01 | 49.723
2019-12-03 | 20:01 | 49.728
2019-12-03 | 20:02 | 49.733
2019-12-03 | 20:02 | 49.738
2019-12-03 | 20:02 | 49.744
2019-12-03 | 20:02 | 49.75
2019-12-03 | 20:02 | 49.758
2019-12-03 | 20:02 | 49.764
2019-12-03 | 20:02 | 49.77
2019-12-03 | 20:02 | 49.776
2019-12-03 | 20:02 | 49.781
2019-12-03 | 20:02 | 49.787
2019-12-03 | 20:02 | 49.79
2019-12-03 | 20:02 | 49.796
2019-12-03 | 20:02 | 49.801
2019-12-03 | 20:02 | 49.809
2019-12-03 | 20:02 | 49.814
2019-12-03 | 20:02 | 49.82
2019-12-03 | 20:02 | 49.825
2019-12-03 | 20:02 | 49.83
2019-12-03 | 20:02 | 49.834
2019-12-03 | 20:02 | 49.838
2019-12-03 | 20:02 | 49.842
2019-12-03 | 20:02 | 49.844
2019-12-03 | 20:02 | 49.847
2019-12-03 | 20:02 | 49.847
2019-12-03 | 20:02 | 49.85
2019-12-03 | 20:02 | 49.85
2019-12-03 | 20:02 | 49.851
2019-12-03 | 20:02 | 49.851
2019-12-03 | 20:02 | 49.851
2019-12-03 | 20:02 | 49.849
2019-12-03 | 20:02 | 49.848
2019-12-03 | 20:02 | 49.845
2019-12-03 | 20:02 | 49.844
2019-12-03 | 20:02 | 49.84
2019-12-03 | 20:02 | 49.838
2019-12-03 | 20:02 | 49.835
2019-12-03 | 20:02 | 49.832
2019-12-03 | 20:02 | 49.833
2019-12-03 | 20:02 | 49.83
2019-12-03 | 20:02 | 49.832
2019-12-03 | 20:02 | 49.833
2019-12-03 | 20:02 | 49.834
2019-12-03 | 20:02 | 49.835
2019-12-03 | 20:02 | 49.837
2019-12-03 | 20:02 | 49.839
2019-12-03 | 20:02 | 49.839
2019-12-03 | 20:02 | 49.842
2019-12-03 | 20:02 | 49.845
2019-12-03 | 20:02 | 49.849
2019-12-03 | 20:02 | 49.853
2019-12-03 | 20:02 | 49.856
2019-12-03 | 20:02 | 49.861
2019-12-03 | 20:02 | 49.864
2019-12-03 | 20:02 | 49.867
2019-12-03 | 20:02 | 49.871
2019-12-03 | 20:02 | 49.875
2019-12-03 | 20:02 | 49.88
2019-12-03 | 20:02 | 49.883
2019-12-03 | 20:02 | 49.886
2019-12-03 | 20:02 | 49.89
2019-12-03 | 20:03 | 49.892
2019-12-03 | 20:03 | 49.895
2019-12-03 | 20:03 | 49.898
2019-12-03 | 20:03 | 49.898
2019-12-03 | 20:03 | 49.9
2019-12-03 | 20:03 | 49.901
2019-12-03 | 20:03 | 49.902
2019-12-03 | 20:03 | 49.904
2019-12-03 | 20:03 | 49.906
2019-12-03 | 20:03 | 49.907
2019-12-03 | 20:03 | 49.908
2019-12-03 | 20:03 | 49.909
2019-12-03 | 20:03 | 49.911
2019-12-03 | 20:03 | 49.912
2019-12-03 | 20:03 | 49.911
2019-12-03 | 20:03 | 49.911
2019-12-03 | 20:03 | 49.912
2019-12-03 | 20:03 | 49.911
2019-12-03 | 20:03 | 49.912
2019-12-03 | 20:03 | 49.915
2019-12-03 | 20:03 | 49.916
2019-12-03 | 20:03 | 49.916
2019-12-03 | 20:03 | 49.914
2019-12-03 | 20:03 | 49.915
2019-12-03 | 20:03 | 49.916
2019-12-03 | 20:03 | 49.917
2019-12-03 | 20:03 | 49.92
2019-12-03 | 20:03 | 49.924
2019-12-03 | 20:03 | 49.925
2019-12-03 | 20:03 | 49.927
2019-12-03 | 20:03 | 49.931
2019-12-03 | 20:03 | 49.935
2019-12-03 | 20:03 | 49.936
2019-12-03 | 20:03 | 49.936
2019-12-03 | 20:03 | 49.935
2019-12-03 | 20:03 | 49.935
2019-12-03 | 20:03 | 49.937
2019-12-03 | 20:03 | 49.94
2019-12-03 | 20:03 | 49.941
2019-12-03 | 20:03 | 49.942
2019-12-03 | 20:03 | 49.943
2019-12-03 | 20:03 | 49.945
2019-12-03 | 20:03 | 49.948
2019-12-03 | 20:03 | 49.949
2019-12-03 | 20:03 | 49.951
2019-12-03 | 20:03 | 49.952
2019-12-03 | 20:03 | 49.954
2019-12-03 | 20:03 | 49.955
2019-12-03 | 20:03 | 49.957
2019-12-03 | 20:03 | 49.957
2019-12-03 | 20:03 | 49.956
2019-12-03 | 20:03 | 49.955
2019-12-03 | 20:03 | 49.956
2019-12-03 | 20:03 | 49.957
2019-12-03 | 20:03 | 49.958
2019-12-03 | 20:03 | 49.959
2019-12-03 | 20:03 | 49.96
2019-12-03 | 20:03 | 49.961
2019-12-03 | 20:03 | 49.962
2019-12-03 | 20:03 | 49.962
2019-12-03 | 20:04 | 49.962
2019-12-03 | 20:04 | 49.962
2019-12-03 | 20:04 | 49.962
2019-12-03 | 20:04 | 49.961
2019-12-03 | 20:04 | 49.961
2019-12-03 | 20:04 | 49.959
2019-12-03 | 20:04 | 49.958
2019-12-03 | 20:04 | 49.957
2019-12-03 | 20:04 | 49.957
2019-12-03 | 20:04 | 49.958
2019-12-03 | 20:04 | 49.958
2019-12-03 | 20:04 | 49.958
2019-12-03 | 20:04 | 49.958
2019-12-03 | 20:04 | 49.959
2019-12-03 | 20:04 | 49.958
2019-12-03 | 20:04 | 49.959
2019-12-03 | 20:04 | 49.959
2019-12-03 | 20:04 | 49.959
2019-12-03 | 20:04 | 49.96
2019-12-03 | 20:04 | 49.96
2019-12-03 | 20:04 | 49.96
2019-12-03 | 20:04 | 49.96
2019-12-03 | 20:04 | 49.96
2019-12-03 | 20:04 | 49.96
2019-12-03 | 20:04 | 49.958
2019-12-03 | 20:04 | 49.956
2019-12-03 | 20:04 | 49.954
2019-12-03 | 20:04 | 49.95
2019-12-03 | 20:04 | 49.946
2019-12-03 | 20:04 | 49.939
2019-12-03 | 20:04 | 49.93
2019-12-03 | 20:04 | 49.921
2019-12-03 | 20:04 | 49.912
2019-12-03 | 20:04 | 49.903
2019-12-03 | 20:04 | 49.894
2019-12-03 | 20:04 | 49.889
2019-12-03 | 20:04 | 49.888
2019-12-03 | 20:04 | 49.89
2019-12-03 | 20:04 | 49.894
2019-12-03 | 20:04 | 49.896
2019-12-03 | 20:04 | 49.896
2019-12-03 | 20:04 | 49.899
2019-12-03 | 20:04 | 49.901
2019-12-03 | 20:04 | 49.898
2019-12-03 | 20:04 | 49.893
2019-12-03 | 20:04 | 49.892
2019-12-03 | 20:04 | 49.89
2019-12-03 | 20:04 | 49.889
2019-12-03 | 20:04 | 49.893
2019-12-03 | 20:04 | 49.895
2019-12-03 | 20:04 | 49.901
2019-12-03 | 20:04 | 49.911
2019-12-03 | 20:04 | 49.922
2019-12-03 | 20:04 | 49.931
2019-12-03 | 20:04 | 49.941
2019-12-03 | 20:04 | 49.947
2019-12-03 | 20:04 | 49.951
2019-12-03 | 20:04 | 49.953
2019-12-03 | 20:04 | 49.955
2019-12-03 | 20:04 | 49.955
2019-12-03 | 20:04 | 49.958
2019-12-03 | 20:05 | 49.959
2019-12-03 | 20:05 | 49.961
2019-12-03 | 20:05 | 49.962
2019-12-03 | 20:05 | 49.962
2019-12-03 | 20:05 | 49.962
2019-12-03 | 20:05 | 49.963
2019-12-03 | 20:05 | 49.963
2019-12-03 | 20:05 | 49.962
2019-12-03 | 20:05 | 49.964
2019-12-03 | 20:05 | 49.963
2019-12-03 | 20:05 | 49.963
2019-12-03 | 20:05 | 49.964
2019-12-03 | 20:05 | 49.964
2019-12-03 | 20:05 | 49.963
2019-12-03 | 20:05 | 49.963
2019-12-03 | 20:05 | 49.96
2019-12-03 | 20:05 | 49.96
2019-12-03 | 20:05 | 49.958
2019-12-03 | 20:05 | 49.958
2019-12-03 | 20:05 | 49.958
2019-12-03 | 20:05 | 49.958
2019-12-03 | 20:05 | 49.959
2019-12-03 | 20:05 | 49.959
2019-12-03 | 20:05 | 49.96
2019-12-03 | 20:05 | 49.96
2019-12-03 | 20:05 | 49.961
2019-12-03 | 20:05 | 49.962
2019-12-03 | 20:05 | 49.965
2019-12-03 | 20:05 | 49.967
2019-12-03 | 20:05 | 49.968
2019-12-03 | 20:05 | 49.967
2019-12-03 | 20:05 | 49.967
2019-12-03 | 20:05 | 49.966
2019-12-03 | 20:05 | 49.965
2019-12-03 | 20:05 | 49.964
2019-12-03 | 20:05 | 49.962
2019-12-03 | 20:05 | 49.962
2019-12-03 | 20:05 | 49.962
2019-12-03 | 20:05 | 49.961
2019-12-03 | 20:05 | 49.961
2019-12-03 | 20:05 | 49.962
2019-12-03 | 20:05 | 49.961
2019-12-03 | 20:05 | 49.96
2019-12-03 | 20:05 | 49.959
2019-12-03 | 20:05 | 49.958
2019-12-03 | 20:05 | 49.956
2019-12-03 | 20:05 | 49.958
2019-12-03 | 20:05 | 49.958
2019-12-03 | 20:05 | 49.96
2019-12-03 | 20:05 | 49.962
2019-12-03 | 20:05 | 49.964
2019-12-03 | 20:05 | 49.966
2019-12-03 | 20:05 | 49.967
2019-12-03 | 20:05 | 49.968
2019-12-03 | 20:05 | 49.969
2019-12-03 | 20:05 | 49.969
2019-12-03 | 20:05 | 49.97
2019-12-03 | 20:05 | 49.971
2019-12-03 | 20:05 | 49.973
2019-12-03 | 20:06 | 49.973
2019-12-03 | 20:06 | 49.973
2019-12-03 | 20:06 | 49.973
2019-12-03 | 20:06 | 49.972
2019-12-03 | 20:06 | 49.972
2019-12-03 | 20:06 | 49.974
2019-12-03 | 20:06 | 49.975
2019-12-03 | 20:06 | 49.978
2019-12-03 | 20:06 | 49.981
2019-12-03 | 20:06 | 49.984
2019-12-03 | 20:06 | 49.986
2019-12-03 | 20:06 | 49.988
2019-12-03 | 20:06 | 49.99
2019-12-03 | 20:06 | 49.992
2019-12-03 | 20:06 | 49.994
2019-12-03 | 20:06 | 49.998
2019-12-03 | 20:06 | 50.002
2019-12-03 | 20:06 | 50.007
2019-12-03 | 20:06 | 50.013
2019-12-03 | 20:06 | 50.017
2019-12-03 | 20:06 | 50.02
2019-12-03 | 20:06 | 50.024
2019-12-03 | 20:06 | 50.027
2019-12-03 | 20:06 | 50.031
2019-12-03 | 20:06 | 50.036
2019-12-03 | 20:06 | 50.04
2019-12-03 | 20:06 | 50.044
2019-12-03 | 20:06 | 50.047
2019-12-03 | 20:06 | 50.05
2019-12-03 | 20:06 | 50.052

## Event 20191209-1
In UTC
Date | Time | Freq
2019-12-09 | 16:06 | 49.877
2019-12-09 | 16:06 | 49.871
2019-12-09 | 16:06 | 49.869
2019-12-09 | 16:06 | 49.864
2019-12-09 | 16:06 | 49.862
2019-12-09 | 16:06 | 49.86
2019-12-09 | 16:06 | 49.86
2019-12-09 | 16:06 | 49.86
2019-12-09 | 16:06 | 49.86
2019-12-09 | 16:06 | 49.859
2019-12-09 | 16:06 | 49.855
2019-12-09 | 16:06 | 49.853
2019-12-09 | 16:06 | 49.852
2019-12-09 | 16:06 | 49.853
2019-12-09 | 16:06 | 49.856
2019-12-09 | 16:06 | 49.86
2019-12-09 | 16:06 | 49.87
2019-12-09 | 16:06 | 49.878
2019-12-09 | 16:06 | 49.885
2019-12-09 | 16:06 | 49.891
2019-12-09 | 16:06 | 49.898
2019-12-09 | 16:06 | 49.903
2019-12-09 | 16:06 | 49.908
2019-12-09 | 16:06 | 49.91
2019-12-09 | 16:06 | 49.914
2019-12-09 | 16:06 | 49.916
2019-12-09 | 16:06 | 49.915
2019-12-09 | 16:06 | 49.915
2019-12-09 | 16:06 | 49.914
2019-12-09 | 16:06 | 49.914
2019-12-09 | 16:06 | 49.913
2019-12-09 | 16:07 | 49.911
2019-12-09 | 16:07 | 49.91
2019-12-09 | 16:07 | 49.909
2019-12-09 | 16:07 | 49.907
2019-12-09 | 16:07 | 49.907
2019-12-09 | 16:07 | 49.905
2019-12-09 | 16:07 | 49.904
2019-12-09 | 16:07 | 49.902
2019-12-09 | 16:07 | 49.894
2019-12-09 | 16:07 | 49.886
2019-12-09 | 16:07 | 49.881
2019-12-09 | 16:07 | 49.873
2019-12-09 | 16:07 | 49.869
2019-12-09 | 16:07 | 49.865
2019-12-09 | 16:07 | 49.862
2019-12-09 | 16:07 | 49.858
2019-12-09 | 16:07 | 49.858
2019-12-09 | 16:07 | 49.858
2019-12-09 | 16:07 | 49.859
2019-12-09 | 16:07 | 49.86
2019-12-09 | 16:07 | 49.862
2019-12-09 | 16:07 | 49.865
2019-12-09 | 16:07 | 49.868
2019-12-09 | 16:07 | 49.871
2019-12-09 | 16:07 | 49.871
2019-12-09 | 16:07 | 49.871
2019-12-09 | 16:07 | 49.87
2019-12-09 | 16:07 | 49.869
2019-12-09 | 16:07 | 49.869
2019-12-09 | 16:07 | 49.867
2019-12-09 | 16:07 | 49.864
2019-12-09 | 16:07 | 49.862
2019-12-09 | 16:07 | 49.86
2019-12-09 | 16:07 | 49.859
2019-12-09 | 16:07 | 49.86
2019-12-09 | 16:07 | 49.86
2019-12-09 | 16:07 | 49.86
2019-12-09 | 16:07 | 49.859
2019-12-09 | 16:07 | 49.858
2019-12-09 | 16:07 | 49.858
2019-12-09 | 16:07 | 49.851
2019-12-09 | 16:07 | 49.825
2019-12-09 | 16:07 | 49.804
2019-12-09 | 16:07 | 49.788
2019-12-09 | 16:07 | 49.776
2019-12-09 | 16:07 | 49.768
2019-12-09 | 16:07 | 49.759
2019-12-09 | 16:07 | 49.753
2019-12-09 | 16:07 | 49.746
2019-12-09 | 16:07 | 49.741
2019-12-09 | 16:07 | 49.739
2019-12-09 | 16:07 | 49.734
2019-12-09 | 16:07 | 49.731
2019-12-09 | 16:07 | 49.729
2019-12-09 | 16:07 | 49.727
2019-12-09 | 16:07 | 49.726
2019-12-09 | 16:07 | 49.724
2019-12-09 | 16:07 | 49.721
2019-12-09 | 16:07 | 49.718
2019-12-09 | 16:08 | 49.714
2019-12-09 | 16:08 | 49.711
2019-12-09 | 16:08 | 49.706
2019-12-09 | 16:08 | 49.704
2019-12-09 | 16:08 | 49.701
2019-12-09 | 16:08 | 49.699
2019-12-09 | 16:08 | 49.7
2019-12-09 | 16:08 | 49.707
2019-12-09 | 16:08 | 49.716
2019-12-09 | 16:08 | 49.73
2019-12-09 | 16:08 | 49.745
2019-12-09 | 16:08 | 49.76
2019-12-09 | 16:08 | 49.77
2019-12-09 | 16:08 | 49.781
2019-12-09 | 16:08 | 49.787
2019-12-09 | 16:08 | 49.793
2019-12-09 | 16:08 | 49.795
2019-12-09 | 16:08 | 49.796
2019-12-09 | 16:08 | 49.796
2019-12-09 | 16:08 | 49.794
2019-12-09 | 16:08 | 49.79
2019-12-09 | 16:08 | 49.786
2019-12-09 | 16:08 | 49.781
2019-12-09 | 16:08 | 49.778
2019-12-09 | 16:08 | 49.776
2019-12-09 | 16:08 | 49.773
2019-12-09 | 16:08 | 49.771
2019-12-09 | 16:08 | 49.769
2019-12-09 | 16:08 | 49.768
2019-12-09 | 16:08 | 49.769
2019-12-09 | 16:08 | 49.769
2019-12-09 | 16:08 | 49.771
2019-12-09 | 16:08 | 49.772
2019-12-09 | 16:08 | 49.772
2019-12-09 | 16:08 | 49.773
2019-12-09 | 16:08 | 49.773
2019-12-09 | 16:08 | 49.773
2019-12-09 | 16:08 | 49.77
2019-12-09 | 16:08 | 49.768
2019-12-09 | 16:08 | 49.767
2019-12-09 | 16:08 | 49.766
2019-12-09 | 16:08 | 49.766
2019-12-09 | 16:08 | 49.768
2019-12-09 | 16:08 | 49.77
2019-12-09 | 16:08 | 49.772
2019-12-09 | 16:08 | 49.774
2019-12-09 | 16:08 | 49.776
2019-12-09 | 16:08 | 49.777
2019-12-09 | 16:08 | 49.779
2019-12-09 | 16:08 | 49.781
2019-12-09 | 16:08 | 49.785
2019-12-09 | 16:08 | 49.786
2019-12-09 | 16:08 | 49.791
2019-12-09 | 16:08 | 49.794
2019-12-09 | 16:08 | 49.797
2019-12-09 | 16:08 | 49.799
2019-12-09 | 16:08 | 49.8
2019-12-09 | 16:08 | 49.8
2019-12-09 | 16:08 | 49.801
2019-12-09 | 16:08 | 49.799
2019-12-09 | 16:08 | 49.798
2019-12-09 | 16:09 | 49.796
2019-12-09 | 16:09 | 49.796
2019-12-09 | 16:09 | 49.794
2019-12-09 | 16:09 | 49.795
2019-12-09 | 16:09 | 49.794
2019-12-09 | 16:09 | 49.795
2019-12-09 | 16:09 | 49.795
2019-12-09 | 16:09 | 49.796
2019-12-09 | 16:09 | 49.798
2019-12-09 | 16:09 | 49.799
2019-12-09 | 16:09 | 49.8
2019-12-09 | 16:09 | 49.8
2019-12-09 | 16:09 | 49.8
2019-12-09 | 16:09 | 49.801
2019-12-09 | 16:09 | 49.802
2019-12-09 | 16:09 | 49.804
2019-12-09 | 16:09 | 49.804
2019-12-09 | 16:09 | 49.803
2019-12-09 | 16:09 | 49.803
2019-12-09 | 16:09 | 49.801
2019-12-09 | 16:09 | 49.8
2019-12-09 | 16:09 | 49.8
2019-12-09 | 16:09 | 49.798
2019-12-09 | 16:09 | 49.798
2019-12-09 | 16:09 | 49.796
2019-12-09 | 16:09 | 49.795
2019-12-09 | 16:09 | 49.792
2019-12-09 | 16:09 | 49.79
2019-12-09 | 16:09 | 49.788
2019-12-09 | 16:09 | 49.786
2019-12-09 | 16:09 | 49.784
2019-12-09 | 16:09 | 49.783
2019-12-09 | 16:09 | 49.782
2019-12-09 | 16:09 | 49.782
2019-12-09 | 16:09 | 49.782
2019-12-09 | 16:09 | 49.782
2019-12-09 | 16:09 | 49.779
2019-12-09 | 16:09 | 49.776
2019-12-09 | 16:09 | 49.773
2019-12-09 | 16:09 | 49.768
2019-12-09 | 16:09 | 49.764
2019-12-09 | 16:09 | 49.76
2019-12-09 | 16:09 | 49.757
2019-12-09 | 16:09 | 49.752
2019-12-09 | 16:09 | 49.748
2019-12-09 | 16:09 | 49.747
2019-12-09 | 16:09 | 49.748
2019-12-09 | 16:09 | 49.75
2019-12-09 | 16:09 | 49.754
2019-12-09 | 16:09 | 49.757
2019-12-09 | 16:09 | 49.762
2019-12-09 | 16:09 | 49.764
2019-12-09 | 16:09 | 49.768
2019-12-09 | 16:09 | 49.771
2019-12-09 | 16:09 | 49.775
2019-12-09 | 16:09 | 49.775
2019-12-09 | 16:09 | 49.777
2019-12-09 | 16:09 | 49.776
2019-12-09 | 16:09 | 49.777
2019-12-09 | 16:10 | 49.777
2019-12-09 | 16:10 | 49.776
2019-12-09 | 16:10 | 49.777
2019-12-09 | 16:10 | 49.775
2019-12-09 | 16:10 | 49.778
2019-12-09 | 16:10 | 49.778
2019-12-09 | 16:10 | 49.779
2019-12-09 | 16:10 | 49.782
2019-12-09 | 16:10 | 49.782
2019-12-09 | 16:10 | 49.784
2019-12-09 | 16:10 | 49.782
2019-12-09 | 16:10 | 49.782
2019-12-09 | 16:10 | 49.779
2019-12-09 | 16:10 | 49.777
2019-12-09 | 16:10 | 49.775
2019-12-09 | 16:10 | 49.772
2019-12-09 | 16:10 | 49.77
2019-12-09 | 16:10 | 49.769
2019-12-09 | 16:10 | 49.766
2019-12-09 | 16:10 | 49.765
2019-12-09 | 16:10 | 49.762
2019-12-09 | 16:10 | 49.76
2019-12-09 | 16:10 | 49.757
2019-12-09 | 16:10 | 49.755
2019-12-09 | 16:10 | 49.753
2019-12-09 | 16:10 | 49.752
2019-12-09 | 16:10 | 49.75
2019-12-09 | 16:10 | 49.749
2019-12-09 | 16:10 | 49.75
2019-12-09 | 16:10 | 49.75
2019-12-09 | 16:10 | 49.751
2019-12-09 | 16:10 | 49.751
2019-12-09 | 16:10 | 49.75
2019-12-09 | 16:10 | 49.749
2019-12-09 | 16:10 | 49.751
2019-12-09 | 16:10 | 49.75
2019-12-09 | 16:10 | 49.753
2019-12-09 | 16:10 | 49.755
2019-12-09 | 16:10 | 49.755
2019-12-09 | 16:10 | 49.761
2019-12-09 | 16:10 | 49.767
2019-12-09 | 16:10 | 49.773
2019-12-09 | 16:10 | 49.78
2019-12-09 | 16:10 | 49.787
2019-12-09 | 16:10 | 49.796
2019-12-09 | 16:10 | 49.803
2019-12-09 | 16:10 | 49.81
2019-12-09 | 16:10 | 49.816
2019-12-09 | 16:10 | 49.822
2019-12-09 | 16:10 | 49.828
2019-12-09 | 16:10 | 49.834
2019-12-09 | 16:10 | 49.841
2019-12-09 | 16:10 | 49.844
2019-12-09 | 16:10 | 49.848
2019-12-09 | 16:10 | 49.853
2019-12-09 | 16:10 | 49.855
2019-12-09 | 16:10 | 49.859
2019-12-09 | 16:10 | 49.864
2019-12-09 | 16:10 | 49.864
2019-12-09 | 16:10 | 49.865
2019-12-09 | 16:10 | 49.867
2019-12-09 | 16:11 | 49.869
2019-12-09 | 16:11 | 49.872
2019-12-09 | 16:11 | 49.874
2019-12-09 | 16:11 | 49.874
2019-12-09 | 16:11 | 49.875
2019-12-09 | 16:11 | 49.875
2019-12-09 | 16:11 | 49.875
2019-12-09 | 16:11 | 49.878
2019-12-09 | 16:11 | 49.878
2019-12-09 | 16:11 | 49.878
2019-12-09 | 16:11 | 49.878
2019-12-09 | 16:11 | 49.881
2019-12-09 | 16:11 | 49.881
2019-12-09 | 16:11 | 49.881
2019-12-09 | 16:11 | 49.882
2019-12-09 | 16:11 | 49.881
2019-12-09 | 16:11 | 49.882
2019-12-09 | 16:11 | 49.882
2019-12-09 | 16:11 | 49.883
2019-12-09 | 16:11 | 49.883
2019-12-09 | 16:11 | 49.883
2019-12-09 | 16:11 | 49.882
2019-12-09 | 16:11 | 49.884
2019-12-09 | 16:11 | 49.886
2019-12-09 | 16:11 | 49.888
2019-12-09 | 16:11 | 49.89
2019-12-09 | 16:11 | 49.888
2019-12-09 | 16:11 | 49.888
2019-12-09 | 16:11 | 49.887
2019-12-09 | 16:11 | 49.884
2019-12-09 | 16:11 | 49.884
2019-12-09 | 16:11 | 49.883
2019-12-09 | 16:11 | 49.882
2019-12-09 | 16:11 | 49.881
2019-12-09 | 16:11 | 49.88
2019-12-09 | 16:11 | 49.879
2019-12-09 | 16:11 | 49.877
2019-12-09 | 16:11 | 49.872
2019-12-09 | 16:11 | 49.871
2019-12-09 | 16:11 | 49.868
2019-12-09 | 16:11 | 49.866
2019-12-09 | 16:11 | 49.866
2019-12-09 | 16:11 | 49.865
2019-12-09 | 16:11 | 49.863
2019-12-09 | 16:11 | 49.864
2019-12-09 | 16:11 | 49.864
2019-12-09 | 16:11 | 49.864
2019-12-09 | 16:11 | 49.864
2019-12-09 | 16:11 | 49.861
2019-12-09 | 16:11 | 49.861
2019-12-09 | 16:11 | 49.862
2019-12-09 | 16:11 | 49.863
2019-12-09 | 16:11 | 49.865
2019-12-09 | 16:11 | 49.865
2019-12-09 | 16:11 | 49.866
2019-12-09 | 16:11 | 49.867
2019-12-09 | 16:11 | 49.867
2019-12-09 | 16:11 | 49.868
2019-12-09 | 16:11 | 49.869
2019-12-09 | 16:12 | 49.867
2019-12-09 | 16:12 | 49.868
2019-12-09 | 16:12 | 49.867
2019-12-09 | 16:12 | 49.867
2019-12-09 | 16:12 | 49.867
2019-12-09 | 16:12 | 49.865
2019-12-09 | 16:12 | 49.865
2019-12-09 | 16:12 | 49.862
2019-12-09 | 16:12 | 49.861
2019-12-09 | 16:12 | 49.86
2019-12-09 | 16:12 | 49.857
2019-12-09 | 16:12 | 49.856
2019-12-09 | 16:12 | 49.853
2019-12-09 | 16:12 | 49.853
2019-12-09 | 16:12 | 49.851
2019-12-09 | 16:12 | 49.85
2019-12-09 | 16:12 | 49.849
2019-12-09 | 16:12 | 49.847
2019-12-09 | 16:12 | 49.846
2019-12-09 | 16:12 | 49.843
2019-12-09 | 16:12 | 49.843
2019-12-09 | 16:12 | 49.842
2019-12-09 | 16:12 | 49.843
2019-12-09 | 16:12 | 49.847
2019-12-09 | 16:12 | 49.851
2019-12-09 | 16:12 | 49.855
2019-12-09 | 16:12 | 49.859
2019-12-09 | 16:12 | 49.862
2019-12-09 | 16:12 | 49.867
2019-12-09 | 16:12 | 49.872
2019-12-09 | 16:12 | 49.876
2019-12-09 | 16:12 | 49.879
2019-12-09 | 16:12 | 49.883
2019-12-09 | 16:12 | 49.884
2019-12-09 | 16:12 | 49.883
2019-12-09 | 16:12 | 49.882
2019-12-09 | 16:12 | 49.88
2019-12-09 | 16:12 | 49.878
2019-12-09 | 16:12 | 49.874
2019-12-09 | 16:12 | 49.87
2019-12-09 | 16:12 | 49.868
2019-12-09 | 16:12 | 49.865
2019-12-09 | 16:12 | 49.862
2019-12-09 | 16:12 | 49.859
2019-12-09 | 16:12 | 49.854
2019-12-09 | 16:12 | 49.853
2019-12-09 | 16:12 | 49.85
2019-12-09 | 16:12 | 49.847
2019-12-09 | 16:12 | 49.847
2019-12-09 | 16:12 | 49.845
2019-12-09 | 16:12 | 49.844
2019-12-09 | 16:12 | 49.843
2019-12-09 | 16:12 | 49.842
2019-12-09 | 16:12 | 49.842
2019-12-09 | 16:12 | 49.84
2019-12-09 | 16:12 | 49.839
2019-12-09 | 16:12 | 49.836
2019-12-09 | 16:12 | 49.833
2019-12-09 | 16:12 | 49.834
2019-12-09 | 16:12 | 49.833
2019-12-09 | 16:12 | 49.834
2019-12-09 | 16:13 | 49.835
2019-12-09 | 16:13 | 49.835
2019-12-09 | 16:13 | 49.835
2019-12-09 | 16:13 | 49.835
2019-12-09 | 16:13 | 49.835
2019-12-09 | 16:13 | 49.834
2019-12-09 | 16:13 | 49.833
2019-12-09 | 16:13 | 49.832
2019-12-09 | 16:13 | 49.83
2019-12-09 | 16:13 | 49.829
2019-12-09 | 16:13 | 49.829
2019-12-09 | 16:13 | 49.828
2019-12-09 | 16:13 | 49.828
2019-12-09 | 16:13 | 49.829
2019-12-09 | 16:13 | 49.827
2019-12-09 | 16:13 | 49.826
2019-12-09 | 16:13 | 49.824
2019-12-09 | 16:13 | 49.822
2019-12-09 | 16:13 | 49.824
2019-12-09 | 16:13 | 49.825
2019-12-09 | 16:13 | 49.825
2019-12-09 | 16:13 | 49.825
2019-12-09 | 16:13 | 49.824
2019-12-09 | 16:13 | 49.824
2019-12-09 | 16:13 | 49.825
2019-12-09 | 16:13 | 49.824
2019-12-09 | 16:13 | 49.825
2019-12-09 | 16:13 | 49.824
2019-12-09 | 16:13 | 49.822
2019-12-09 | 16:13 | 49.821
2019-12-09 | 16:13 | 49.817
2019-12-09 | 16:13 | 49.817
2019-12-09 | 16:13 | 49.816
2019-12-09 | 16:13 | 49.815
2019-12-09 | 16:13 | 49.814
2019-12-09 | 16:13 | 49.811
2019-12-09 | 16:13 | 49.808
2019-12-09 | 16:13 | 49.805
2019-12-09 | 16:13 | 49.802
2019-12-09 | 16:13 | 49.8
2019-12-09 | 16:13 | 49.797
2019-12-09 | 16:13 | 49.795
2019-12-09 | 16:13 | 49.794
2019-12-09 | 16:13 | 49.793
2019-12-09 | 16:13 | 49.793
2019-12-09 | 16:13 | 49.792
2019-12-09 | 16:13 | 49.794
2019-12-09 | 16:13 | 49.796
2019-12-09 | 16:13 | 49.795
2019-12-09 | 16:13 | 49.795
2019-12-09 | 16:13 | 49.793
2019-12-09 | 16:13 | 49.79
2019-12-09 | 16:13 | 49.786
2019-12-09 | 16:13 | 49.784
2019-12-09 | 16:13 | 49.783
2019-12-09 | 16:13 | 49.782
2019-12-09 | 16:13 | 49.785
2019-12-09 | 16:13 | 49.784
2019-12-09 | 16:13 | 49.786
2019-12-09 | 16:14 | 49.789
2019-12-09 | 16:14 | 49.791
2019-12-09 | 16:14 | 49.793
2019-12-09 | 16:14 | 49.794
2019-12-09 | 16:14 | 49.795
2019-12-09 | 16:14 | 49.798
2019-12-09 | 16:14 | 49.8
2019-12-09 | 16:14 | 49.803
2019-12-09 | 16:14 | 49.806
2019-12-09 | 16:14 | 49.809
2019-12-09 | 16:14 | 49.815
2019-12-09 | 16:14 | 49.818
2019-12-09 | 16:14 | 49.825
2019-12-09 | 16:14 | 49.83
2019-12-09 | 16:14 | 49.835
2019-12-09 | 16:14 | 49.838
2019-12-09 | 16:14 | 49.839
2019-12-09 | 16:14 | 49.842
2019-12-09 | 16:14 | 49.844
2019-12-09 | 16:14 | 49.846
2019-12-09 | 16:14 | 49.851
2019-12-09 | 16:14 | 49.855
2019-12-09 | 16:14 | 49.857
2019-12-09 | 16:14 | 49.86
2019-12-09 | 16:14 | 49.86
2019-12-09 | 16:14 | 49.86
2019-12-09 | 16:14 | 49.856
2019-12-09 | 16:14 | 49.856
2019-12-09 | 16:14 | 49.854
2019-12-09 | 16:14 | 49.853
2019-12-09 | 16:14 | 49.851
2019-12-09 | 16:14 | 49.848
2019-12-09 | 16:14 | 49.846
2019-12-09 | 16:14 | 49.841
2019-12-09 | 16:14 | 49.841
2019-12-09 | 16:14 | 49.84
2019-12-09 | 16:14 | 49.839
2019-12-09 | 16:14 | 49.841
2019-12-09 | 16:14 | 49.845
2019-12-09 | 16:14 | 49.851
2019-12-09 | 16:14 | 49.859
2019-12-09 | 16:14 | 49.864
2019-12-09 | 16:14 | 49.872
2019-12-09 | 16:14 | 49.879
2019-12-09 | 16:14 | 49.884
2019-12-09 | 16:14 | 49.887
2019-12-09 | 16:14 | 49.89
2019-12-09 | 16:14 | 49.892
2019-12-09 | 16:14 | 49.897
2019-12-09 | 16:14 | 49.903
2019-12-09 | 16:14 | 49.909
2019-12-09 | 16:14 | 49.914
2019-12-09 | 16:14 | 49.92
2019-12-09 | 16:14 | 49.923
2019-12-09 | 16:14 | 49.929
2019-12-09 | 16:14 | 49.934
2019-12-09 | 16:14 | 49.938
2019-12-09 | 16:14 | 49.944
2019-12-09 | 16:14 | 49.95
2019-12-09 | 16:14 | 49.954
2019-12-09 | 16:14 | 49.958
2019-12-09 | 16:15 | 49.962
2019-12-09 | 16:15 | 49.964
2019-12-09 | 16:15 | 49.963
2019-12-09 | 16:15 | 49.962
2019-12-09 | 16:15 | 49.96
2019-12-09 | 16:15 | 49.961
2019-12-09 | 16:15 | 49.961
2019-12-09 | 16:15 | 49.962
2019-12-09 | 16:15 | 49.962
2019-12-09 | 16:15 | 49.961
2019-12-09 | 16:15 | 49.961
2019-12-09 | 16:15 | 49.961
2019-12-09 | 16:15 | 49.958
2019-12-09 | 16:15 | 49.957
2019-12-09 | 16:15 | 49.956
2019-12-09 | 16:15 | 49.953
2019-12-09 | 16:15 | 49.952
2019-12-09 | 16:15 | 49.952
2019-12-09 | 16:15 | 49.951
2019-12-09 | 16:15 | 49.953
2019-12-09 | 16:15 | 49.954
2019-12-09 | 16:15 | 49.955
2019-12-09 | 16:15 | 49.957
2019-12-09 | 16:15 | 49.959
2019-12-09 | 16:15 | 49.961
2019-12-09 | 16:15 | 49.963
2019-12-09 | 16:15 | 49.964
2019-12-09 | 16:15 | 49.964
2019-12-09 | 16:15 | 49.966
2019-12-09 | 16:15 | 49.965
2019-12-09 | 16:15 | 49.963
2019-12-09 | 16:15 | 49.961
2019-12-09 | 16:15 | 49.958
2019-12-09 | 16:15 | 49.957
2019-12-09 | 16:15 | 49.954
2019-12-09 | 16:15 | 49.952
2019-12-09 | 16:15 | 49.949
2019-12-09 | 16:15 | 49.949
2019-12-09 | 16:15 | 49.947
2019-12-09 | 16:15 | 49.945
2019-12-09 | 16:15 | 49.948
2019-12-09 | 16:15 | 49.95
2019-12-09 | 16:15 | 49.951
2019-12-09 | 16:15 | 49.954
2019-12-09 | 16:15 | 49.954
2019-12-09 | 16:15 | 49.954
2019-12-09 | 16:15 | 49.954
2019-12-09 | 16:15 | 49.95
2019-12-09 | 16:15 | 49.948
2019-12-09 | 16:15 | 49.947
2019-12-09 | 16:15 | 49.945
2019-12-09 | 16:15 | 49.946
2019-12-09 | 16:15 | 49.941
2019-12-09 | 16:15 | 49.939
2019-12-09 | 16:15 | 49.938
2019-12-09 | 16:15 | 49.934
2019-12-09 | 16:15 | 49.932
2019-12-09 | 16:15 | 49.929
2019-12-09 | 16:15 | 49.928
2019-12-09 | 16:16 | 49.927
2019-12-09 | 16:16 | 49.927
2019-12-09 | 16:16 | 49.925
2019-12-09 | 16:16 | 49.924
2019-12-09 | 16:16 | 49.924
2019-12-09 | 16:16 | 49.923
2019-12-09 | 16:16 | 49.923
2019-12-09 | 16:16 | 49.923
2019-12-09 | 16:16 | 49.922
2019-12-09 | 16:16 | 49.922
2019-12-09 | 16:16 | 49.922
2019-12-09 | 16:16 | 49.921
2019-12-09 | 16:16 | 49.922
2019-12-09 | 16:16 | 49.922
2019-12-09 | 16:16 | 49.922
2019-12-09 | 16:16 | 49.925
2019-12-09 | 16:16 | 49.926
2019-12-09 | 16:16 | 49.928
2019-12-09 | 16:16 | 49.929
2019-12-09 | 16:16 | 49.929
2019-12-09 | 16:16 | 49.929
2019-12-09 | 16:16 | 49.928
2019-12-09 | 16:16 | 49.925
2019-12-09 | 16:16 | 49.923
2019-12-09 | 16:16 | 49.922
2019-12-09 | 16:16 | 49.918
2019-12-09 | 16:16 | 49.916
2019-12-09 | 16:16 | 49.917
2019-12-09 | 16:16 | 49.915
2019-12-09 | 16:16 | 49.913
2019-12-09 | 16:16 | 49.912
2019-12-09 | 16:16 | 49.91
2019-12-09 | 16:16 | 49.909
2019-12-09 | 16:16 | 49.908
2019-12-09 | 16:16 | 49.907
2019-12-09 | 16:16 | 49.906
2019-12-09 | 16:16 | 49.904
2019-12-09 | 16:16 | 49.903
2019-12-09 | 16:16 | 49.904
2019-12-09 | 16:16 | 49.903
2019-12-09 | 16:16 | 49.902
2019-12-09 | 16:16 | 49.9
2019-12-09 | 16:16 | 49.899
2019-12-09 | 16:16 | 49.898
2019-12-09 | 16:16 | 49.899
2019-12-09 | 16:16 | 49.898
2019-12-09 | 16:16 | 49.899
2019-12-09 | 16:16 | 49.897
2019-12-09 | 16:16 | 49.896
2019-12-09 | 16:16 | 49.895
2019-12-09 | 16:16 | 49.893
2019-12-09 | 16:16 | 49.892
2019-12-09 | 16:16 | 49.893
2019-12-09 | 16:16 | 49.891
2019-12-09 | 16:16 | 49.89
2019-12-09 | 16:16 | 49.89
2019-12-09 | 16:16 | 49.891
2019-12-09 | 16:16 | 49.893
2019-12-09 | 16:16 | 49.895
2019-12-09 | 16:16 | 49.898
2019-12-09 | 16:16 | 49.902
2019-12-09 | 16:17 | 49.906
2019-12-09 | 16:17 | 49.91
2019-12-09 | 16:17 | 49.913
2019-12-09 | 16:17 | 49.916
2019-12-09 | 16:17 | 49.918
2019-12-09 | 16:17 | 49.918
2019-12-09 | 16:17 | 49.918
2019-12-09 | 16:17 | 49.919
2019-12-09 | 16:17 | 49.918
2019-12-09 | 16:17 | 49.919
2019-12-09 | 16:17 | 49.92
2019-12-09 | 16:17 | 49.92
2019-12-09 | 16:17 | 49.92
2019-12-09 | 16:17 | 49.922
2019-12-09 | 16:17 | 49.923
2019-12-09 | 16:17 | 49.924
2019-12-09 | 16:17 | 49.926
2019-12-09 | 16:17 | 49.926
2019-12-09 | 16:17 | 49.927
2019-12-09 | 16:17 | 49.929
2019-12-09 | 16:17 | 49.93
2019-12-09 | 16:17 | 49.933
2019-12-09 | 16:17 | 49.935
2019-12-09 | 16:17 | 49.935
2019-12-09 | 16:17 | 49.935
2019-12-09 | 16:17 | 49.935
2019-12-09 | 16:17 | 49.934
2019-12-09 | 16:17 | 49.936
2019-12-09 | 16:17 | 49.935
2019-12-09 | 16:17 | 49.934
2019-12-09 | 16:17 | 49.935
2019-12-09 | 16:17 | 49.933
2019-12-09 | 16:17 | 49.931
2019-12-09 | 16:17 | 49.93
2019-12-09 | 16:17 | 49.929
2019-12-09 | 16:17 | 49.93
2019-12-09 | 16:17 | 49.931
2019-12-09 | 16:17 | 49.931
2019-12-09 | 16:17 | 49.932
2019-12-09 | 16:17 | 49.933
2019-12-09 | 16:17 | 49.933
2019-12-09 | 16:17 | 49.935
2019-12-09 | 16:17 | 49.935
2019-12-09 | 16:17 | 49.936
2019-12-09 | 16:17 | 49.937
2019-12-09 | 16:17 | 49.937
2019-12-09 | 16:17 | 49.939
2019-12-09 | 16:17 | 49.939
2019-12-09 | 16:17 | 49.94
2019-12-09 | 16:17 | 49.94
2019-12-09 | 16:17 | 49.94
2019-12-09 | 16:17 | 49.942
2019-12-09 | 16:17 | 49.942
2019-12-09 | 16:17 | 49.942
2019-12-09 | 16:17 | 49.94
2019-12-09 | 16:17 | 49.938
2019-12-09 | 16:17 | 49.937
2019-12-09 | 16:17 | 49.936
2019-12-09 | 16:17 | 49.934
2019-12-09 | 16:18 | 49.935
2019-12-09 | 16:18 | 49.935
2019-12-09 | 16:18 | 49.936
2019-12-09 | 16:18 | 49.936
2019-12-09 | 16:18 | 49.937
2019-12-09 | 16:18 | 49.94
2019-12-09 | 16:18 | 49.938
2019-12-09 | 16:18 | 49.939
2019-12-09 | 16:18 | 49.94
2019-12-09 | 16:18 | 49.941
2019-12-09 | 16:18 | 49.942
2019-12-09 | 16:18 | 49.941
2019-12-09 | 16:18 | 49.941
2019-12-09 | 16:18 | 49.941
2019-12-09 | 16:18 | 49.941
2019-12-09 | 16:18 | 49.941
2019-12-09 | 16:18 | 49.942
2019-12-09 | 16:18 | 49.942
2019-12-09 | 16:18 | 49.94
2019-12-09 | 16:18 | 49.941
2019-12-09 | 16:18 | 49.938
2019-12-09 | 16:18 | 49.941
2019-12-09 | 16:18 | 49.94
2019-12-09 | 16:18 | 49.938
2019-12-09 | 16:18 | 49.938
2019-12-09 | 16:18 | 49.936
2019-12-09 | 16:18 | 49.936
2019-12-09 | 16:18 | 49.936
2019-12-09 | 16:18 | 49.937
2019-12-09 | 16:18 | 49.937
2019-12-09 | 16:18 | 49.936
2019-12-09 | 16:18 | 49.938
2019-12-09 | 16:18 | 49.939
2019-12-09 | 16:18 | 49.94
2019-12-09 | 16:18 | 49.942
2019-12-09 | 16:18 | 49.944
2019-12-09 | 16:18 | 49.945
2019-12-09 | 16:18 | 49.946
2019-12-09 | 16:18 | 49.946
2019-12-09 | 16:18 | 49.944
2019-12-09 | 16:18 | 49.943
2019-12-09 | 16:18 | 49.941
2019-12-09 | 16:18 | 49.938
2019-12-09 | 16:18 | 49.937
2019-12-09 | 16:18 | 49.935
2019-12-09 | 16:18 | 49.935
2019-12-09 | 16:18 | 49.936
2019-12-09 | 16:18 | 49.935
2019-12-09 | 16:18 | 49.935
2019-12-09 | 16:18 | 49.936
2019-12-09 | 16:18 | 49.936
2019-12-09 | 16:18 | 49.936
2019-12-09 | 16:18 | 49.938
2019-12-09 | 16:18 | 49.939
2019-12-09 | 16:18 | 49.939
2019-12-09 | 16:18 | 49.939
2019-12-09 | 16:18 | 49.94
2019-12-09 | 16:18 | 49.941
2019-12-09 | 16:18 | 49.943
2019-12-09 | 16:18 | 49.946
2019-12-09 | 16:18 | 49.947
2019-12-09 | 16:19 | 49.949
2019-12-09 | 16:19 | 49.95
2019-12-09 | 16:19 | 49.95
2019-12-09 | 16:19 | 49.951
2019-12-09 | 16:19 | 49.946
2019-12-09 | 16:19 | 49.941
2019-12-09 | 16:19 | 49.938
2019-12-09 | 16:19 | 49.935
2019-12-09 | 16:19 | 49.935
2019-12-09 | 16:19 | 49.933
2019-12-09 | 16:19 | 49.932
2019-12-09 | 16:19 | 49.932
2019-12-09 | 16:19 | 49.93
2019-12-09 | 16:19 | 49.929
2019-12-09 | 16:19 | 49.928
2019-12-09 | 16:19 | 49.925
2019-12-09 | 16:19 | 49.925
2019-12-09 | 16:19 | 49.923
2019-12-09 | 16:19 | 49.924
2019-12-09 | 16:19 | 49.923
2019-12-09 | 16:19 | 49.923
2019-12-09 | 16:19 | 49.923
2019-12-09 | 16:19 | 49.922
2019-12-09 | 16:19 | 49.922
2019-12-09 | 16:19 | 49.922
2019-12-09 | 16:19 | 49.921
2019-12-09 | 16:19 | 49.922
2019-12-09 | 16:19 | 49.921
2019-12-09 | 16:19 | 49.919
2019-12-09 | 16:19 | 49.918
2019-12-09 | 16:19 | 49.917
2019-12-09 | 16:19 | 49.919
2019-12-09 | 16:19 | 49.918
2019-12-09 | 16:19 | 49.919
2019-12-09 | 16:19 | 49.916
2019-12-09 | 16:19 | 49.917
2019-12-09 | 16:19 | 49.914
2019-12-09 | 16:19 | 49.914
2019-12-09 | 16:19 | 49.912
2019-12-09 | 16:19 | 49.914
2019-12-09 | 16:19 | 49.91
2019-12-09 | 16:19 | 49.909
2019-12-09 | 16:19 | 49.906
2019-12-09 | 16:19 | 49.904
2019-12-09 | 16:19 | 49.902
2019-12-09 | 16:19 | 49.9
2019-12-09 | 16:19 | 49.897
2019-12-09 | 16:19 | 49.895
2019-12-09 | 16:19 | 49.893
2019-12-09 | 16:19 | 49.892
2019-12-09 | 16:19 | 49.891
2019-12-09 | 16:19 | 49.891
2019-12-09 | 16:19 | 49.891
2019-12-09 | 16:19 | 49.891
2019-12-09 | 16:19 | 49.892
2019-12-09 | 16:19 | 49.891
2019-12-09 | 16:19 | 49.892
2019-12-09 | 16:19 | 49.891
2019-12-09 | 16:19 | 49.892
2019-12-09 | 16:20 | 49.89
2019-12-09 | 16:20 | 49.891
2019-12-09 | 16:20 | 49.89
2019-12-09 | 16:20 | 49.89
2019-12-09 | 16:20 | 49.891
2019-12-09 | 16:20 | 49.892
2019-12-09 | 16:20 | 49.892
2019-12-09 | 16:20 | 49.892
2019-12-09 | 16:20 | 49.894
2019-12-09 | 16:20 | 49.894
2019-12-09 | 16:20 | 49.895
2019-12-09 | 16:20 | 49.895
2019-12-09 | 16:20 | 49.895
2019-12-09 | 16:20 | 49.897
2019-12-09 | 16:20 | 49.899
2019-12-09 | 16:20 | 49.9
2019-12-09 | 16:20 | 49.901
2019-12-09 | 16:20 | 49.902
2019-12-09 | 16:20 | 49.904
2019-12-09 | 16:20 | 49.905
2019-12-09 | 16:20 | 49.907
2019-12-09 | 16:20 | 49.909
2019-12-09 | 16:20 | 49.909
2019-12-09 | 16:20 | 49.913
2019-12-09 | 16:20 | 49.915
2019-12-09 | 16:20 | 49.916
2019-12-09 | 16:20 | 49.918
2019-12-09 | 16:20 | 49.92
2019-12-09 | 16:20 | 49.922
2019-12-09 | 16:20 | 49.925
2019-12-09 | 16:20 | 49.925
2019-12-09 | 16:20 | 49.927
2019-12-09 | 16:20 | 49.927
2019-12-09 | 16:20 | 49.93
2019-12-09 | 16:20 | 49.933
2019-12-09 | 16:20 | 49.934
2019-12-09 | 16:20 | 49.937
2019-12-09 | 16:20 | 49.938
2019-12-09 | 16:20 | 49.938
2019-12-09 | 16:20 | 49.939
2019-12-09 | 16:20 | 49.939
2019-12-09 | 16:20 | 49.938
2019-12-09 | 16:20 | 49.939
2019-12-09 | 16:20 | 49.939
2019-12-09 | 16:20 | 49.937
2019-12-09 | 16:20 | 49.939
2019-12-09 | 16:20 | 49.939
2019-12-09 | 16:20 | 49.938
2019-12-09 | 16:20 | 49.939
2019-12-09 | 16:20 | 49.94
2019-12-09 | 16:20 | 49.94
2019-12-09 | 16:20 | 49.944
2019-12-09 | 16:20 | 49.945
2019-12-09 | 16:20 | 49.948
2019-12-09 | 16:20 | 49.952
2019-12-09 | 16:20 | 49.955
2019-12-09 | 16:20 | 49.959
2019-12-09 | 16:20 | 49.961
2019-12-09 | 16:20 | 49.962
2019-12-09 | 16:20 | 49.962
2019-12-09 | 16:20 | 49.962
2019-12-09 | 16:21 | 49.962
2019-12-09 | 16:21 | 49.962
2019-12-09 | 16:21 | 49.96
2019-12-09 | 16:21 | 49.96
2019-12-09 | 16:21 | 49.96
2019-12-09 | 16:21 | 49.958
2019-12-09 | 16:21 | 49.957
2019-12-09 | 16:21 | 49.956
2019-12-09 | 16:21 | 49.955
2019-12-09 | 16:21 | 49.955
2019-12-09 | 16:21 | 49.956
2019-12-09 | 16:21 | 49.957
2019-12-09 | 16:21 | 49.957
2019-12-09 | 16:21 | 49.958
2019-12-09 | 16:21 | 49.958
2019-12-09 | 16:21 | 49.957
2019-12-09 | 16:21 | 49.957
2019-12-09 | 16:21 | 49.955
2019-12-09 | 16:21 | 49.955
2019-12-09 | 16:21 | 49.955
2019-12-09 | 16:21 | 49.955
2019-12-09 | 16:21 | 49.954
2019-12-09 | 16:21 | 49.954
2019-12-09 | 16:21 | 49.952
2019-12-09 | 16:21 | 49.948
2019-12-09 | 16:21 | 49.943
2019-12-09 | 16:21 | 49.939
2019-12-09 | 16:21 | 49.934
2019-12-09 | 16:21 | 49.928
2019-12-09 | 16:21 | 49.924
2019-12-09 | 16:21 | 49.922
2019-12-09 | 16:21 | 49.92
2019-12-09 | 16:21 | 49.922
2019-12-09 | 16:21 | 49.922
2019-12-09 | 16:21 | 49.923
2019-12-09 | 16:21 | 49.924
2019-12-09 | 16:21 | 49.926
2019-12-09 | 16:21 | 49.926
2019-12-09 | 16:21 | 49.928
2019-12-09 | 16:21 | 49.93
2019-12-09 | 16:21 | 49.93
2019-12-09 | 16:21 | 49.933
2019-12-09 | 16:21 | 49.933
2019-12-09 | 16:21 | 49.933
2019-12-09 | 16:21 | 49.934
2019-12-09 | 16:21 | 49.935
2019-12-09 | 16:21 | 49.934
2019-12-09 | 16:21 | 49.934
2019-12-09 | 16:21 | 49.933
2019-12-09 | 16:21 | 49.933
2019-12-09 | 16:21 | 49.933
2019-12-09 | 16:21 | 49.936
2019-12-09 | 16:21 | 49.935
2019-12-09 | 16:21 | 49.936
2019-12-09 | 16:21 | 49.937
2019-12-09 | 16:21 | 49.936
2019-12-09 | 16:21 | 49.937
2019-12-09 | 16:21 | 49.938
2019-12-09 | 16:21 | 49.939
2019-12-09 | 16:22 | 49.941
2019-12-09 | 16:22 | 49.941
2019-12-09 | 16:22 | 49.942
2019-12-09 | 16:22 | 49.942
2019-12-09 | 16:22 | 49.941
2019-12-09 | 16:22 | 49.943
2019-12-09 | 16:22 | 49.94
2019-12-09 | 16:22 | 49.94
2019-12-09 | 16:22 | 49.939
2019-12-09 | 16:22 | 49.937
2019-12-09 | 16:22 | 49.936
2019-12-09 | 16:22 | 49.935
2019-12-09 | 16:22 | 49.935
2019-12-09 | 16:22 | 49.936
2019-12-09 | 16:22 | 49.936
2019-12-09 | 16:22 | 49.936
2019-12-09 | 16:22 | 49.936
2019-12-09 | 16:22 | 49.936
2019-12-09 | 16:22 | 49.934
2019-12-09 | 16:22 | 49.932
2019-12-09 | 16:22 | 49.931
2019-12-09 | 16:22 | 49.93
2019-12-09 | 16:22 | 49.928
2019-12-09 | 16:22 | 49.927
2019-12-09 | 16:22 | 49.927
2019-12-09 | 16:22 | 49.928
2019-12-09 | 16:22 | 49.932
2019-12-09 | 16:22 | 49.933
2019-12-09 | 16:22 | 49.936
2019-12-09 | 16:22 | 49.938
2019-12-09 | 16:22 | 49.939
2019-12-09 | 16:22 | 49.941
2019-12-09 | 16:22 | 49.941
2019-12-09 | 16:22 | 49.942
2019-12-09 | 16:22 | 49.944
2019-12-09 | 16:22 | 49.946
2019-12-09 | 16:22 | 49.947
2019-12-09 | 16:22 | 49.948
2019-12-09 | 16:22 | 49.947
2019-12-09 | 16:22 | 49.948
2019-12-09 | 16:22 | 49.947
2019-12-09 | 16:22 | 49.949
2019-12-09 | 16:22 | 49.949
2019-12-09 | 16:22 | 49.95
2019-12-09 | 16:22 | 49.951
2019-12-09 | 16:22 | 49.952
2019-12-09 | 16:22 | 49.951
2019-12-09 | 16:22 | 49.951
2019-12-09 | 16:22 | 49.951
2019-12-09 | 16:22 | 49.95
2019-12-09 | 16:22 | 49.95
2019-12-09 | 16:22 | 49.949
2019-12-09 | 16:22 | 49.949
2019-12-09 | 16:22 | 49.951
2019-12-09 | 16:22 | 49.95
2019-12-09 | 16:22 | 49.95
2019-12-09 | 16:22 | 49.951
2019-12-09 | 16:22 | 49.95
2019-12-09 | 16:22 | 49.95
2019-12-09 | 16:22 | 49.95
2019-12-09 | 16:22 | 49.949
2019-12-09 | 16:23 | 49.948
2019-12-09 | 16:23 | 49.946
2019-12-09 | 16:23 | 49.944
2019-12-09 | 16:23 | 49.944
2019-12-09 | 16:23 | 49.942
2019-12-09 | 16:23 | 49.942
2019-12-09 | 16:23 | 49.943
2019-12-09 | 16:23 | 49.944
2019-12-09 | 16:23 | 49.945
2019-12-09 | 16:23 | 49.945
2019-12-09 | 16:23 | 49.947
2019-12-09 | 16:23 | 49.948
2019-12-09 | 16:23 | 49.95
2019-12-09 | 16:23 | 49.952
2019-12-09 | 16:23 | 49.954
2019-12-09 | 16:23 | 49.957
2019-12-09 | 16:23 | 49.958
2019-12-09 | 16:23 | 49.959
2019-12-09 | 16:23 | 49.96
2019-12-09 | 16:23 | 49.96
2019-12-09 | 16:23 | 49.958
2019-12-09 | 16:23 | 49.957
2019-12-09 | 16:23 | 49.957
2019-12-09 | 16:23 | 49.956
2019-12-09 | 16:23 | 49.956
2019-12-09 | 16:23 | 49.956
2019-12-09 | 16:23 | 49.954
2019-12-09 | 16:23 | 49.952
2019-12-09 | 16:23 | 49.95
2019-12-09 | 16:23 | 49.946
2019-12-09 | 16:23 | 49.944
2019-12-09 | 16:23 | 49.941
2019-12-09 | 16:23 | 49.94
2019-12-09 | 16:23 | 49.94
2019-12-09 | 16:23 | 49.94
2019-12-09 | 16:23 | 49.939
2019-12-09 | 16:23 | 49.939
2019-12-09 | 16:23 | 49.938
2019-12-09 | 16:23 | 49.938
2019-12-09 | 16:23 | 49.939
2019-12-09 | 16:23 | 49.942
2019-12-09 | 16:23 | 49.942
2019-12-09 | 16:23 | 49.944
2019-12-09 | 16:23 | 49.946
2019-12-09 | 16:23 | 49.947
2019-12-09 | 16:23 | 49.948
2019-12-09 | 16:23 | 49.949
2019-12-09 | 16:23 | 49.949
2019-12-09 | 16:23 | 49.949
2019-12-09 | 16:23 | 49.95
2019-12-09 | 16:23 | 49.95
2019-12-09 | 16:23 | 49.95
2019-12-09 | 16:23 | 49.949
2019-12-09 | 16:23 | 49.949
2019-12-09 | 16:23 | 49.948
2019-12-09 | 16:23 | 49.948
2019-12-09 | 16:23 | 49.948
2019-12-09 | 16:23 | 49.947
2019-12-09 | 16:23 | 49.946
2019-12-09 | 16:24 | 49.945
2019-12-09 | 16:24 | 49.945
2019-12-09 | 16:24 | 49.946
2019-12-09 | 16:24 | 49.947
2019-12-09 | 16:24 | 49.948
2019-12-09 | 16:24 | 49.946
2019-12-09 | 16:24 | 49.947
2019-12-09 | 16:24 | 49.944
2019-12-09 | 16:24 | 49.942
2019-12-09 | 16:24 | 49.941
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.939
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.941
2019-12-09 | 16:24 | 49.942
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.943
2019-12-09 | 16:24 | 49.943
2019-12-09 | 16:24 | 49.946
2019-12-09 | 16:24 | 49.948
2019-12-09 | 16:24 | 49.95
2019-12-09 | 16:24 | 49.952
2019-12-09 | 16:24 | 49.953
2019-12-09 | 16:24 | 49.955
2019-12-09 | 16:24 | 49.957
2019-12-09 | 16:24 | 49.959
2019-12-09 | 16:24 | 49.959
2019-12-09 | 16:24 | 49.959
2019-12-09 | 16:24 | 49.959
2019-12-09 | 16:24 | 49.958
2019-12-09 | 16:24 | 49.956
2019-12-09 | 16:24 | 49.954
2019-12-09 | 16:24 | 49.952
2019-12-09 | 16:24 | 49.95
2019-12-09 | 16:24 | 49.947
2019-12-09 | 16:24 | 49.944
2019-12-09 | 16:24 | 49.941
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.939
2019-12-09 | 16:24 | 49.938
2019-12-09 | 16:24 | 49.938
2019-12-09 | 16:24 | 49.937
2019-12-09 | 16:24 | 49.937
2019-12-09 | 16:24 | 49.937
2019-12-09 | 16:24 | 49.938
2019-12-09 | 16:24 | 49.938
2019-12-09 | 16:24 | 49.937
2019-12-09 | 16:24 | 49.937
2019-12-09 | 16:24 | 49.938
2019-12-09 | 16:24 | 49.938
2019-12-09 | 16:24 | 49.94
2019-12-09 | 16:24 | 49.944
2019-12-09 | 16:24 | 49.946
2019-12-09 | 16:24 | 49.948
2019-12-09 | 16:25 | 49.951
2019-12-09 | 16:25 | 49.954
2019-12-09 | 16:25 | 49.957
2019-12-09 | 16:25 | 49.961
2019-12-09 | 16:25 | 49.962
2019-12-09 | 16:25 | 49.964
2019-12-09 | 16:25 | 49.966
2019-12-09 | 16:25 | 49.967
2019-12-09 | 16:25 | 49.969
2019-12-09 | 16:25 | 49.973
2019-12-09 | 16:25 | 49.974
2019-12-09 | 16:25 | 49.976
2019-12-09 | 16:25 | 49.98
2019-12-09 | 16:25 | 49.982
2019-12-09 | 16:25 | 49.986
2019-12-09 | 16:25 | 49.989
2019-12-09 | 16:25 | 49.991
2019-12-09 | 16:25 | 49.995
2019-12-09 | 16:25 | 49.996
2019-12-09 | 16:25 | 49.998
2019-12-09 | 16:25 | 49.999
2019-12-09 | 16:25 | 50
2019-12-09 | 16:25 | 50.001
2019-12-09 | 16:25 | 50.001
2019-12-09 | 16:25 | 49.999
2019-12-09 | 16:25 | 49.998
2019-12-09 | 16:25 | 49.997
2019-12-09 | 16:25 | 49.996
2019-12-09 | 16:25 | 49.995
2019-12-09 | 16:25 | 49.992
2019-12-09 | 16:25 | 49.991
2019-12-09 | 16:25 | 49.989
2019-12-09 | 16:25 | 49.986
2019-12-09 | 16:25 | 49.984
2019-12-09 | 16:25 | 49.981
2019-12-09 | 16:25 | 49.979
2019-12-09 | 16:25 | 49.979
2019-12-09 | 16:25 | 49.978
2019-12-09 | 16:25 | 49.981
2019-12-09 | 16:25 | 49.981
2019-12-09 | 16:25 | 49.985
2019-12-09 | 16:25 | 49.987
2019-12-09 | 16:25 | 49.988
2019-12-09 | 16:25 | 49.99
2019-12-09 | 16:25 | 49.991
2019-12-09 | 16:25 | 49.991
2019-12-09 | 16:25 | 49.992
2019-12-09 | 16:25 | 49.991
2019-12-09 | 16:25 | 49.992
2019-12-09 | 16:25 | 49.992
2019-12-09 | 16:25 | 49.993
2019-12-09 | 16:25 | 49.995
2019-12-09 | 16:25 | 49.996
2019-12-09 | 16:25 | 49.995
2019-12-09 | 16:25 | 49.996
2019-12-09 | 16:25 | 49.996
2019-12-09 | 16:25 | 49.997
2019-12-09 | 16:25 | 49.998
2019-12-09 | 16:25 | 49.998
2019-12-09 | 16:25 | 49.997
2019-12-09 | 16:26 | 49.999
2019-12-09 | 16:26 | 49.999
2019-12-09 | 16:26 | 50.001
2019-12-09 | 16:26 | 50.005
2019-12-09 | 16:26 | 50.007
2019-12-09 | 16:26 | 50.008
2019-12-09 | 16:26 | 50.011
2019-12-09 | 16:26 | 50.012
2019-12-09 | 16:26 | 50.013
2019-12-09 | 16:26 | 50.015
2019-12-09 | 16:26 | 50.015
2019-12-09 | 16:26 | 50.014
2019-12-09 | 16:26 | 50.016
2019-12-09 | 16:26 | 50.015
2019-12-09 | 16:26 | 50.014
2019-12-09 | 16:26 | 50.016
2019-12-09 | 16:26 | 50.016
2019-12-09 | 16:26 | 50.018
2019-12-09 | 16:26 | 50.02
2019-12-09 | 16:26 | 50.022
2019-12-09 | 16:26 | 50.025
2019-12-09 | 16:26 | 50.028
2019-12-09 | 16:26 | 50.032
2019-12-09 | 16:26 | 50.036
2019-12-09 | 16:26 | 50.038
2019-12-09 | 16:26 | 50.037
2019-12-09 | 16:26 | 50.037
2019-12-09 | 16:26 | 50.034
2019-12-09 | 16:26 | 50.033
2019-12-09 | 16:26 | 50.032

## Event 20191212-1
In UTC
Date | Time | Freq
2019-12-12 | 6:01 | 49.827
2019-12-12 | 6:01 | 49.827
2019-12-12 | 6:01 | 49.824
2019-12-12 | 6:01 | 49.823
2019-12-12 | 6:01 | 49.823
2019-12-12 | 6:01 | 49.822
2019-12-12 | 6:01 | 49.83
2019-12-12 | 6:01 | 49.82
2019-12-12 | 6:01 | 49.818
2019-12-12 | 6:01 | 49.818
2019-12-12 | 6:01 | 49.817
2019-12-12 | 6:01 | 49.817
2019-12-12 | 6:01 | 49.817
2019-12-12 | 6:01 | 49.818
2019-12-12 | 6:01 | 49.824
2019-12-12 | 6:01 | 49.829
2019-12-12 | 6:01 | 49.833
2019-12-12 | 6:01 | 49.839
2019-12-12 | 6:01 | 49.844
2019-12-12 | 6:01 | 49.848
2019-12-12 | 6:01 | 49.853
2019-12-12 | 6:01 | 49.857
2019-12-12 | 6:01 | 49.862
2019-12-12 | 6:01 | 49.866
2019-12-12 | 6:01 | 49.87
2019-12-12 | 6:01 | 49.874
2019-12-12 | 6:01 | 49.879
2019-12-12 | 6:01 | 49.882
2019-12-12 | 6:01 | 49.887
2019-12-12 | 6:01 | 49.89
2019-12-12 | 6:02 | 49.893
2019-12-12 | 6:02 | 49.896
2019-12-12 | 6:02 | 49.898
2019-12-12 | 6:02 | 49.898
2019-12-12 | 6:02 | 49.901
2019-12-12 | 6:02 | 49.902
2019-12-12 | 6:02 | 49.904
2019-12-12 | 6:02 | 49.904
2019-12-12 | 6:02 | 49.905
2019-12-12 | 6:02 | 49.907
2019-12-12 | 6:02 | 49.905
2019-12-12 | 6:02 | 49.906
2019-12-12 | 6:02 | 49.905
2019-12-12 | 6:02 | 49.903
2019-12-12 | 6:02 | 49.902
2019-12-12 | 6:02 | 49.902
2019-12-12 | 6:02 | 49.905
2019-12-12 | 6:02 | 49.906
2019-12-12 | 6:02 | 49.906
2019-12-12 | 6:02 | 49.908
2019-12-12 | 6:02 | 49.912
2019-12-12 | 6:02 | 49.914
2019-12-12 | 6:02 | 49.917
2019-12-12 | 6:02 | 49.922
2019-12-12 | 6:02 | 49.923
2019-12-12 | 6:02 | 49.924
2019-12-12 | 6:02 | 49.925
2019-12-12 | 6:02 | 49.927
2019-12-12 | 6:02 | 49.927
2019-12-12 | 6:02 | 49.928
2019-12-12 | 6:02 | 49.927
2019-12-12 | 6:02 | 49.927
2019-12-12 | 6:02 | 49.929
2019-12-12 | 6:02 | 49.929
2019-12-12 | 6:02 | 49.931
2019-12-12 | 6:02 | 49.93
2019-12-12 | 6:02 | 49.929
2019-12-12 | 6:02 | 49.929
2019-12-12 | 6:02 | 49.927
2019-12-12 | 6:02 | 49.926
2019-12-12 | 6:02 | 49.927
2019-12-12 | 6:02 | 49.924
2019-12-12 | 6:02 | 49.925
2019-12-12 | 6:02 | 49.925
2019-12-12 | 6:02 | 49.921
2019-12-12 | 6:02 | 49.902
2019-12-12 | 6:02 | 49.883
2019-12-12 | 6:02 | 49.872
2019-12-12 | 6:02 | 49.861
2019-12-12 | 6:02 | 49.857
2019-12-12 | 6:02 | 49.851
2019-12-12 | 6:02 | 49.847
2019-12-12 | 6:02 | 49.842
2019-12-12 | 6:02 | 49.841
2019-12-12 | 6:02 | 49.839
2019-12-12 | 6:02 | 49.838
2019-12-12 | 6:02 | 49.837
2019-12-12 | 6:02 | 49.839
2019-12-12 | 6:02 | 49.842
2019-12-12 | 6:02 | 49.846
2019-12-12 | 6:02 | 49.848
2019-12-12 | 6:03 | 49.853
2019-12-12 | 6:03 | 49.855
2019-12-12 | 6:03 | 49.861
2019-12-12 | 6:03 | 49.864
2019-12-12 | 6:03 | 49.864
2019-12-12 | 6:03 | 49.865
2019-12-12 | 6:03 | 49.866
2019-12-12 | 6:03 | 49.866
2019-12-12 | 6:03 | 49.869
2019-12-12 | 6:03 | 49.869
2019-12-12 | 6:03 | 49.869
2019-12-12 | 6:03 | 49.869
2019-12-12 | 6:03 | 49.869
2019-12-12 | 6:03 | 49.87
2019-12-12 | 6:03 | 49.869
2019-12-12 | 6:03 | 49.868
2019-12-12 | 6:03 | 49.866
2019-12-12 | 6:03 | 49.866
2019-12-12 | 6:03 | 49.866
2019-12-12 | 6:03 | 49.866
2019-12-12 | 6:03 | 49.863
2019-12-12 | 6:03 | 49.862
2019-12-12 | 6:03 | 49.86
2019-12-12 | 6:03 | 49.858
2019-12-12 | 6:03 | 49.857
2019-12-12 | 6:03 | 49.854
2019-12-12 | 6:03 | 49.854
2019-12-12 | 6:03 | 49.853
2019-12-12 | 6:03 | 49.852
2019-12-12 | 6:03 | 49.85
2019-12-12 | 6:03 | 49.849
2019-12-12 | 6:03 | 49.848
2019-12-12 | 6:03 | 49.846
2019-12-12 | 6:03 | 49.845
2019-12-12 | 6:03 | 49.844
2019-12-12 | 6:03 | 49.843
2019-12-12 | 6:03 | 49.842
2019-12-12 | 6:03 | 49.841
2019-12-12 | 6:03 | 49.84
2019-12-12 | 6:03 | 49.839
2019-12-12 | 6:03 | 49.838
2019-12-12 | 6:03 | 49.837
2019-12-12 | 6:03 | 49.838
2019-12-12 | 6:03 | 49.84
2019-12-12 | 6:03 | 49.841
2019-12-12 | 6:03 | 49.843
2019-12-12 | 6:03 | 49.845
2019-12-12 | 6:03 | 49.848
2019-12-12 | 6:03 | 49.85
2019-12-12 | 6:03 | 49.852
2019-12-12 | 6:03 | 49.853
2019-12-12 | 6:03 | 49.856
2019-12-12 | 6:03 | 49.861
2019-12-12 | 6:03 | 49.864
2019-12-12 | 6:03 | 49.866
2019-12-12 | 6:03 | 49.867
2019-12-12 | 6:03 | 49.866
2019-12-12 | 6:03 | 49.868
2019-12-12 | 6:03 | 49.865
2019-12-12 | 6:04 | 49.866
2019-12-12 | 6:04 | 49.866
2019-12-12 | 6:04 | 49.864
2019-12-12 | 6:04 | 49.865
2019-12-12 | 6:04 | 49.865
2019-12-12 | 6:04 | 49.867
2019-12-12 | 6:04 | 49.867
2019-12-12 | 6:04 | 49.869
2019-12-12 | 6:04 | 49.871
2019-12-12 | 6:04 | 49.871
2019-12-12 | 6:04 | 49.87
2019-12-12 | 6:04 | 49.868
2019-12-12 | 6:04 | 49.869
2019-12-12 | 6:04 | 49.867
2019-12-12 | 6:04 | 49.869
2019-12-12 | 6:04 | 49.871
2019-12-12 | 6:04 | 49.872
2019-12-12 | 6:04 | 49.873
2019-12-12 | 6:04 | 49.874
2019-12-12 | 6:04 | 49.876
2019-12-12 | 6:04 | 49.875
2019-12-12 | 6:04 | 49.876
2019-12-12 | 6:04 | 49.872
2019-12-12 | 6:04 | 49.87
2019-12-12 | 6:04 | 49.87
2019-12-12 | 6:04 | 49.871
2019-12-12 | 6:04 | 49.874
2019-12-12 | 6:04 | 49.877
2019-12-12 | 6:04 | 49.881
2019-12-12 | 6:04 | 49.885
2019-12-12 | 6:04 | 49.887
2019-12-12 | 6:04 | 49.887
2019-12-12 | 6:04 | 49.89
2019-12-12 | 6:04 | 49.89
2019-12-12 | 6:04 | 49.889
2019-12-12 | 6:04 | 49.887
2019-12-12 | 6:04 | 49.886
2019-12-12 | 6:04 | 49.883
2019-12-12 | 6:04 | 49.885
2019-12-12 | 6:04 | 49.879
2019-12-12 | 6:04 | 49.876
2019-12-12 | 6:04 | 49.874
2019-12-12 | 6:04 | 49.873
2019-12-12 | 6:04 | 49.872
2019-12-12 | 6:04 | 49.869
2019-12-12 | 6:04 | 49.868
2019-12-12 | 6:04 | 49.867
2019-12-12 | 6:04 | 49.867
2019-12-12 | 6:04 | 49.866
2019-12-12 | 6:04 | 49.865
2019-12-12 | 6:04 | 49.865
2019-12-12 | 6:04 | 49.864
2019-12-12 | 6:04 | 49.866
2019-12-12 | 6:04 | 49.866
2019-12-12 | 6:04 | 49.866
2019-12-12 | 6:04 | 49.869
2019-12-12 | 6:04 | 49.871
2019-12-12 | 6:04 | 49.873
2019-12-12 | 6:04 | 49.874
2019-12-12 | 6:04 | 49.877
2019-12-12 | 6:04 | 49.878
2019-12-12 | 6:05 | 49.88
2019-12-12 | 6:05 | 49.881
2019-12-12 | 6:05 | 49.883
2019-12-12 | 6:05 | 49.885
2019-12-12 | 6:05 | 49.886
2019-12-12 | 6:05 | 49.894
2019-12-12 | 6:05 | 49.888
2019-12-12 | 6:05 | 49.889
2019-12-12 | 6:05 | 49.89
2019-12-12 | 6:05 | 49.891
2019-12-12 | 6:05 | 49.894
2019-12-12 | 6:05 | 49.896
2019-12-12 | 6:05 | 49.898
2019-12-12 | 6:05 | 49.9
2019-12-12 | 6:05 | 49.902
2019-12-12 | 6:05 | 49.901
2019-12-12 | 6:05 | 49.901
2019-12-12 | 6:05 | 49.899
2019-12-12 | 6:05 | 49.899
2019-12-12 | 6:05 | 49.898
2019-12-12 | 6:05 | 49.899
2019-12-12 | 6:05 | 49.9
2019-12-12 | 6:05 | 49.901
2019-12-12 | 6:05 | 49.902
2019-12-12 | 6:05 | 49.903
2019-12-12 | 6:05 | 49.905
2019-12-12 | 6:05 | 49.907
2019-12-12 | 6:05 | 49.91
2019-12-12 | 6:05 | 49.911
2019-12-12 | 6:05 | 49.915
2019-12-12 | 6:05 | 49.916
2019-12-12 | 6:05 | 49.918
2019-12-12 | 6:05 | 49.918
2019-12-12 | 6:05 | 49.922
2019-12-12 | 6:05 | 49.924
2019-12-12 | 6:05 | 49.927
2019-12-12 | 6:05 | 49.93
2019-12-12 | 6:05 | 49.932
2019-12-12 | 6:05 | 49.933
2019-12-12 | 6:05 | 49.935
2019-12-12 | 6:05 | 49.936
2019-12-12 | 6:05 | 49.94
2019-12-12 | 6:05 | 49.942
2019-12-12 | 6:05 | 49.943
2019-12-12 | 6:05 | 49.945
2019-12-12 | 6:05 | 49.947
2019-12-12 | 6:05 | 49.948
2019-12-12 | 6:05 | 49.949
2019-12-12 | 6:05 | 49.95
2019-12-12 | 6:05 | 49.951
2019-12-12 | 6:05 | 49.954
2019-12-12 | 6:05 | 49.955
2019-12-12 | 6:05 | 49.956
2019-12-12 | 6:05 | 49.956
2019-12-12 | 6:05 | 49.955
2019-12-12 | 6:05 | 49.953
2019-12-12 | 6:05 | 49.95
2019-12-12 | 6:05 | 49.948
2019-12-12 | 6:05 | 49.948
2019-12-12 | 6:06 | 49.948
2019-12-12 | 6:06 | 49.951
2019-12-12 | 6:06 | 49.953
2019-12-12 | 6:06 | 49.957
2019-12-12 | 6:06 | 49.96
2019-12-12 | 6:06 | 49.964
2019-12-12 | 6:06 | 49.97
2019-12-12 | 6:06 | 49.974
2019-12-12 | 6:06 | 49.978
2019-12-12 | 6:06 | 49.982
2019-12-12 | 6:06 | 49.985
2019-12-12 | 6:06 | 49.988
2019-12-12 | 6:06 | 49.992
2019-12-12 | 6:06 | 49.997
2019-12-12 | 6:06 | 50.002
2019-12-12 | 6:06 | 50.007
2019-12-12 | 6:06 | 50.01
2019-12-12 | 6:06 | 50.015
2019-12-12 | 6:06 | 50.018
2019-12-12 | 6:06 | 50.021
2019-12-12 | 6:06 | 50.025
2019-12-12 | 6:06 | 50.027
2019-12-12 | 6:06 | 50.029
2019-12-12 | 6:06 | 50.028
2019-12-12 | 6:06 | 50.028
2019-12-12 | 6:06 | 50.026
2019-12-12 | 6:06 | 50.025
2019-12-12 | 6:06 | 50.024
2019-12-12 | 6:06 | 50.024
2019-12-12 | 6:06 | 50.027

## Event 20191216-1
In UTC
Date | Time | Freq
2019-12-16 | 6:50 | 50.07
2019-12-16 | 6:50 | 50.072
2019-12-16 | 6:50 | 50.074
2019-12-16 | 6:50 | 50.076
2019-12-16 | 6:50 | 50.078
2019-12-16 | 6:50 | 50.076
2019-12-16 | 6:50 | 50.079
2019-12-16 | 6:50 | 50.076
2019-12-16 | 6:50 | 50.078
2019-12-16 | 6:50 | 50.076
2019-12-16 | 6:50 | 50.077
2019-12-16 | 6:50 | 50.076
2019-12-16 | 6:50 | 50.075
2019-12-16 | 6:50 | 50.075
2019-12-16 | 6:50 | 50.073
2019-12-16 | 6:50 | 50.074
2019-12-16 | 6:50 | 50.071
2019-12-16 | 6:50 | 50.072
2019-12-16 | 6:50 | 50.07
2019-12-16 | 6:50 | 50.072
2019-12-16 | 6:50 | 50.072
2019-12-16 | 6:50 | 50.073
2019-12-16 | 6:50 | 50.076
2019-12-16 | 6:50 | 50.074
2019-12-16 | 6:50 | 50.079
2019-12-16 | 6:50 | 50.078
2019-12-16 | 6:50 | 50.083
2019-12-16 | 6:50 | 50.084
2019-12-16 | 6:50 | 50.091
2019-12-16 | 6:50 | 50.094
2019-12-16 | 6:50 | 50.099
2019-12-16 | 6:51 | 50.101
2019-12-16 | 6:51 | 50.105
2019-12-16 | 6:51 | 50.106
2019-12-16 | 6:51 | 50.108
2019-12-16 | 6:51 | 50.109
2019-12-16 | 6:51 | 50.109
2019-12-16 | 6:51 | 50.108
2019-12-16 | 6:51 | 50.11
2019-12-16 | 6:51 | 50.11
2019-12-16 | 6:51 | 50.108
2019-12-16 | 6:51 | 50.107
2019-12-16 | 6:51 | 50.107
2019-12-16 | 6:51 | 50.105
2019-12-16 | 6:51 | 50.107
2019-12-16 | 6:51 | 50.106
2019-12-16 | 6:51 | 50.105
2019-12-16 | 6:51 | 50.103
2019-12-16 | 6:51 | 50.103
2019-12-16 | 6:51 | 50.103
2019-12-16 | 6:51 | 50.102
2019-12-16 | 6:51 | 50.103
2019-12-16 | 6:51 | 50.101
2019-12-16 | 6:51 | 50.101
2019-12-16 | 6:51 | 50.103
2019-12-16 | 6:51 | 50.104
2019-12-16 | 6:51 | 50.103
2019-12-16 | 6:51 | 50.103
2019-12-16 | 6:51 | 50.102
2019-12-16 | 6:51 | 50.103
2019-12-16 | 6:51 | 50.103
2019-12-16 | 6:51 | 50.104
2019-12-16 | 6:51 | 50.103
2019-12-16 | 6:51 | 50.1
2019-12-16 | 6:51 | 50.1
2019-12-16 | 6:51 | 50.098
2019-12-16 | 6:51 | 50.099
2019-12-16 | 6:51 | 50.1
2019-12-16 | 6:51 | 50.1
2019-12-16 | 6:51 | 50.1
2019-12-16 | 6:51 | 50.1
2019-12-16 | 6:51 | 50.1
2019-12-16 | 6:51 | 50.1
2019-12-16 | 6:51 | 50.101
2019-12-16 | 6:51 | 50.1
2019-12-16 | 6:51 | 50.101
2019-12-16 | 6:51 | 50.105
2019-12-16 | 6:51 | 50.105
2019-12-16 | 6:51 | 50.106
2019-12-16 | 6:51 | 50.106
2019-12-16 | 6:51 | 50.106
2019-12-16 | 6:51 | 50.106
2019-12-16 | 6:51 | 50.107
2019-12-16 | 6:51 | 50.105
2019-12-16 | 6:51 | 50.108
2019-12-16 | 6:51 | 50.111
2019-12-16 | 6:51 | 50.114
2019-12-16 | 6:51 | 50.116
2019-12-16 | 6:51 | 50.119
2019-12-16 | 6:51 | 50.121
2019-12-16 | 6:52 | 50.124
2019-12-16 | 6:52 | 50.127
2019-12-16 | 6:52 | 50.129
2019-12-16 | 6:52 | 50.131
2019-12-16 | 6:52 | 50.132
2019-12-16 | 6:52 | 50.134
2019-12-16 | 6:52 | 50.137
2019-12-16 | 6:52 | 50.139
2019-12-16 | 6:52 | 50.14
2019-12-16 | 6:52 | 50.142
2019-12-16 | 6:52 | 50.144
2019-12-16 | 6:52 | 50.144
2019-12-16 | 6:52 | 50.143
2019-12-16 | 6:52 | 50.144
2019-12-16 | 6:52 | 50.144
2019-12-16 | 6:52 | 50.144
2019-12-16 | 6:52 | 50.141
2019-12-16 | 6:52 | 50.138
2019-12-16 | 6:52 | 50.135
2019-12-16 | 6:52 | 50.131
2019-12-16 | 6:52 | 50.128
2019-12-16 | 6:52 | 50.123
2019-12-16 | 6:52 | 50.12
2019-12-16 | 6:52 | 50.119
2019-12-16 | 6:52 | 50.119
2019-12-16 | 6:52 | 50.121
2019-12-16 | 6:52 | 50.122
2019-12-16 | 6:52 | 50.124
2019-12-16 | 6:52 | 50.126
2019-12-16 | 6:52 | 50.129
2019-12-16 | 6:52 | 50.133
2019-12-16 | 6:52 | 50.134
2019-12-16 | 6:52 | 50.135
2019-12-16 | 6:52 | 50.134
2019-12-16 | 6:52 | 50.134
2019-12-16 | 6:52 | 50.132
2019-12-16 | 6:52 | 50.131
2019-12-16 | 6:52 | 50.13
2019-12-16 | 6:52 | 50.129
2019-12-16 | 6:52 | 50.129
2019-12-16 | 6:52 | 50.131
2019-12-16 | 6:52 | 50.131
2019-12-16 | 6:52 | 50.132
2019-12-16 | 6:52 | 50.133
2019-12-16 | 6:52 | 50.136
2019-12-16 | 6:52 | 50.138
2019-12-16 | 6:52 | 50.142
2019-12-16 | 6:52 | 50.146
2019-12-16 | 6:52 | 50.151
2019-12-16 | 6:52 | 50.155
2019-12-16 | 6:52 | 50.157
2019-12-16 | 6:52 | 50.16
2019-12-16 | 6:52 | 50.163
2019-12-16 | 6:52 | 50.167
2019-12-16 | 6:52 | 50.172
2019-12-16 | 6:52 | 50.175
2019-12-16 | 6:52 | 50.178
2019-12-16 | 6:52 | 50.182
2019-12-16 | 6:52 | 50.184
2019-12-16 | 6:52 | 50.187
2019-12-16 | 6:52 | 50.19
2019-12-16 | 6:53 | 50.192
2019-12-16 | 6:53 | 50.194
2019-12-16 | 6:53 | 50.195
2019-12-16 | 6:53 | 50.197
2019-12-16 | 6:53 | 50.198
2019-12-16 | 6:53 | 50.2
2019-12-16 | 6:53 | 50.202
2019-12-16 | 6:53 | 50.203
2019-12-16 | 6:53 | 50.204
2019-12-16 | 6:53 | 50.205
2019-12-16 | 6:53 | 50.206
2019-12-16 | 6:53 | 50.209
2019-12-16 | 6:53 | 50.21
2019-12-16 | 6:53 | 50.212
2019-12-16 | 6:53 | 50.212
2019-12-16 | 6:53 | 50.213
2019-12-16 | 6:53 | 50.213
2019-12-16 | 6:53 | 50.215
2019-12-16 | 6:53 | 50.217
2019-12-16 | 6:53 | 50.218
2019-12-16 | 6:53 | 50.22
2019-12-16 | 6:53 | 50.222
2019-12-16 | 6:53 | 50.225
2019-12-16 | 6:53 | 50.226
2019-12-16 | 6:53 | 50.231
2019-12-16 | 6:53 | 50.236
2019-12-16 | 6:53 | 50.241
2019-12-16 | 6:53 | 50.246
2019-12-16 | 6:53 | 50.248
2019-12-16 | 6:53 | 50.251
2019-12-16 | 6:53 | 50.252
2019-12-16 | 6:53 | 50.253
2019-12-16 | 6:53 | 50.252
2019-12-16 | 6:53 | 50.255
2019-12-16 | 6:53 | 50.255
2019-12-16 | 6:53 | 50.256
2019-12-16 | 6:53 | 50.256
2019-12-16 | 6:53 | 50.256
2019-12-16 | 6:53 | 50.254
2019-12-16 | 6:53 | 50.254
2019-12-16 | 6:53 | 50.253
2019-12-16 | 6:53 | 50.251
2019-12-16 | 6:53 | 50.249
2019-12-16 | 6:53 | 50.244
2019-12-16 | 6:53 | 50.242
2019-12-16 | 6:53 | 50.24
2019-12-16 | 6:53 | 50.238
2019-12-16 | 6:53 | 50.237
2019-12-16 | 6:53 | 50.238
2019-12-16 | 6:53 | 50.239
2019-12-16 | 6:53 | 50.243
2019-12-16 | 6:53 | 50.245
2019-12-16 | 6:53 | 50.247
2019-12-16 | 6:53 | 50.249
2019-12-16 | 6:53 | 50.252
2019-12-16 | 6:53 | 50.253
2019-12-16 | 6:53 | 50.256
2019-12-16 | 6:53 | 50.258
2019-12-16 | 6:53 | 50.259
2019-12-16 | 6:53 | 50.261
2019-12-16 | 6:54 | 50.264
2019-12-16 | 6:54 | 50.265
2019-12-16 | 6:54 | 50.268
2019-12-16 | 6:54 | 50.271
2019-12-16 | 6:54 | 50.274
2019-12-16 | 6:54 | 50.278
2019-12-16 | 6:54 | 50.28
2019-12-16 | 6:54 | 50.281
2019-12-16 | 6:54 | 50.284
2019-12-16 | 6:54 | 50.287
2019-12-16 | 6:54 | 50.29
2019-12-16 | 6:54 | 50.294
2019-12-16 | 6:54 | 50.295
2019-12-16 | 6:54 | 50.296
2019-12-16 | 6:54 | 50.295
2019-12-16 | 6:54 | 50.296
2019-12-16 | 6:54 | 50.297
2019-12-16 | 6:54 | 50.296
2019-12-16 | 6:54 | 50.298
2019-12-16 | 6:54 | 50.298
2019-12-16 | 6:54 | 50.299
2019-12-16 | 6:54 | 50.299
2019-12-16 | 6:54 | 50.299
2019-12-16 | 6:54 | 50.301
2019-12-16 | 6:54 | 50.302
2019-12-16 | 6:54 | 50.3
2019-12-16 | 6:54 | 50.3
2019-12-16 | 6:54 | 50.297
2019-12-16 | 6:54 | 50.295
2019-12-16 | 6:54 | 50.294
2019-12-16 | 6:54 | 50.292
2019-12-16 | 6:54 | 50.291
2019-12-16 | 6:54 | 50.289
2019-12-16 | 6:54 | 50.29
2019-12-16 | 6:54 | 50.29
2019-12-16 | 6:54 | 50.291
2019-12-16 | 6:54 | 50.293
2019-12-16 | 6:54 | 50.292
2019-12-16 | 6:54 | 50.294
2019-12-16 | 6:54 | 50.295
2019-12-16 | 6:54 | 50.296
2019-12-16 | 6:54 | 50.297
2019-12-16 | 6:54 | 50.296
2019-12-16 | 6:54 | 50.295
2019-12-16 | 6:54 | 50.295
2019-12-16 | 6:54 | 50.293
2019-12-16 | 6:54 | 50.291
2019-12-16 | 6:54 | 50.29
2019-12-16 | 6:54 | 50.291
2019-12-16 | 6:54 | 50.292
2019-12-16 | 6:54 | 50.292
2019-12-16 | 6:54 | 50.293
2019-12-16 | 6:54 | 50.292
2019-12-16 | 6:54 | 50.292
2019-12-16 | 6:54 | 50.29
2019-12-16 | 6:54 | 50.288
2019-12-16 | 6:54 | 50.286
2019-12-16 | 6:54 | 50.284
2019-12-16 | 6:54 | 50.284
2019-12-16 | 6:54 | 50.283
2019-12-16 | 6:55 | 50.282
2019-12-16 | 6:55 | 50.281
2019-12-16 | 6:55 | 50.281
2019-12-16 | 6:55 | 50.28
2019-12-16 | 6:55 | 50.284
2019-12-16 | 6:55 | 50.285
2019-12-16 | 6:55 | 50.289
2019-12-16 | 6:55 | 50.293
2019-12-16 | 6:55 | 50.295
2019-12-16 | 6:55 | 50.298
2019-12-16 | 6:55 | 50.299
2019-12-16 | 6:55 | 50.303
2019-12-16 | 6:55 | 50.302
2019-12-16 | 6:55 | 50.303
2019-12-16 | 6:55 | 50.302
2019-12-16 | 6:55 | 50.303
2019-12-16 | 6:55 | 50.303
2019-12-16 | 6:55 | 50.304
2019-12-16 | 6:55 | 50.303
2019-12-16 | 6:55 | 50.302
2019-12-16 | 6:55 | 50.301
2019-12-16 | 6:55 | 50.301
2019-12-16 | 6:55 | 50.302
2019-12-16 | 6:55 | 50.304
2019-12-16 | 6:55 | 50.304
2019-12-16 | 6:55 | 50.306
2019-12-16 | 6:55 | 50.308
2019-12-16 | 6:55 | 50.31
2019-12-16 | 6:55 | 50.309
2019-12-16 | 6:55 | 50.308
2019-12-16 | 6:55 | 50.309
2019-12-16 | 6:55 | 50.309
2019-12-16 | 6:55 | 50.308
2019-12-16 | 6:55 | 50.307
2019-12-16 | 6:55 | 50.306
2019-12-16 | 6:55 | 50.306
2019-12-16 | 6:55 | 50.305
2019-12-16 | 6:55 | 50.306
2019-12-16 | 6:55 | 50.308
2019-12-16 | 6:55 | 50.31
2019-12-16 | 6:55 | 50.312
2019-12-16 | 6:55 | 50.312
2019-12-16 | 6:55 | 50.311
2019-12-16 | 6:55 | 50.31
2019-12-16 | 6:55 | 50.308
2019-12-16 | 6:55 | 50.306
2019-12-16 | 6:55 | 50.305
2019-12-16 | 6:55 | 50.302
2019-12-16 | 6:55 | 50.302
2019-12-16 | 6:55 | 50.302
2019-12-16 | 6:55 | 50.301
2019-12-16 | 6:55 | 50.302
2019-12-16 | 6:55 | 50.301
2019-12-16 | 6:55 | 50.3
2019-12-16 | 6:55 | 50.297
2019-12-16 | 6:55 | 50.294
2019-12-16 | 6:55 | 50.291
2019-12-16 | 6:55 | 50.289
2019-12-16 | 6:55 | 50.288
2019-12-16 | 6:55 | 50.286
2019-12-16 | 6:56 | 50.285
2019-12-16 | 6:56 | 50.285
2019-12-16 | 6:56 | 50.285
2019-12-16 | 6:56 | 50.283
2019-12-16 | 6:56 | 50.282
2019-12-16 | 6:56 | 50.28
2019-12-16 | 6:56 | 50.278
2019-12-16 | 6:56 | 50.276
2019-12-16 | 6:56 | 50.277
2019-12-16 | 6:56 | 50.276
2019-12-16 | 6:56 | 50.278
2019-12-16 | 6:56 | 50.276
2019-12-16 | 6:56 | 50.277
2019-12-16 | 6:56 | 50.278
2019-12-16 | 6:56 | 50.279
2019-12-16 | 6:56 | 50.279
2019-12-16 | 6:56 | 50.28
2019-12-16 | 6:56 | 50.28
2019-12-16 | 6:56 | 50.282
2019-12-16 | 6:56 | 50.282
2019-12-16 | 6:56 | 50.283
2019-12-16 | 6:56 | 50.284
2019-12-16 | 6:56 | 50.285
2019-12-16 | 6:56 | 50.285
2019-12-16 | 6:56 | 50.282
2019-12-16 | 6:56 | 50.282
2019-12-16 | 6:56 | 50.281
2019-12-16 | 6:56 | 50.28
2019-12-16 | 6:56 | 50.278
2019-12-16 | 6:56 | 50.279
2019-12-16 | 6:56 | 50.276
2019-12-16 | 6:56 | 50.277
2019-12-16 | 6:56 | 50.277
2019-12-16 | 6:56 | 50.277
2019-12-16 | 6:56 | 50.272
2019-12-16 | 6:56 | 50.267
2019-12-16 | 6:56 | 50.26
2019-12-16 | 6:56 | 50.251
2019-12-16 | 6:56 | 50.241
2019-12-16 | 6:56 | 50.232
2019-12-16 | 6:56 | 50.227
2019-12-16 | 6:56 | 50.223
2019-12-16 | 6:56 | 50.221
2019-12-16 | 6:56 | 50.218
2019-12-16 | 6:56 | 50.217
2019-12-16 | 6:56 | 50.214
2019-12-16 | 6:56 | 50.215
2019-12-16 | 6:56 | 50.214
2019-12-16 | 6:56 | 50.213
2019-12-16 | 6:56 | 50.211
2019-12-16 | 6:56 | 50.21
2019-12-16 | 6:56 | 50.208
2019-12-16 | 6:56 | 50.206
2019-12-16 | 6:56 | 50.202
2019-12-16 | 6:56 | 50.2
2019-12-16 | 6:56 | 50.198
2019-12-16 | 6:56 | 50.197
2019-12-16 | 6:56 | 50.195
2019-12-16 | 6:56 | 50.194
2019-12-16 | 6:56 | 50.193
2019-12-16 | 6:57 | 50.192
2019-12-16 | 6:57 | 50.192
2019-12-16 | 6:57 | 50.191
2019-12-16 | 6:57 | 50.189
2019-12-16 | 6:57 | 50.188
2019-12-16 | 6:57 | 50.185
2019-12-16 | 6:57 | 50.183
2019-12-16 | 6:57 | 50.182
2019-12-16 | 6:57 | 50.18
2019-12-16 | 6:57 | 50.177
2019-12-16 | 6:57 | 50.174
2019-12-16 | 6:57 | 50.172
2019-12-16 | 6:57 | 50.169
2019-12-16 | 6:57 | 50.167
2019-12-16 | 6:57 | 50.163
2019-12-16 | 6:57 | 50.16
2019-12-16 | 6:57 | 50.156
2019-12-16 | 6:57 | 50.153
2019-12-16 | 6:57 | 50.15
2019-12-16 | 6:57 | 50.149
2019-12-16 | 6:57 | 50.15
2019-12-16 | 6:57 | 50.148
2019-12-16 | 6:57 | 50.147
2019-12-16 | 6:57 | 50.141
2019-12-16 | 6:57 | 50.139
2019-12-16 | 6:57 | 50.137
2019-12-16 | 6:57 | 50.134
2019-12-16 | 6:57 | 50.132
2019-12-16 | 6:57 | 50.132
2019-12-16 | 6:57 | 50.129
2019-12-16 | 6:57 | 50.127
2019-12-16 | 6:57 | 50.125
2019-12-16 | 6:57 | 50.125
2019-12-16 | 6:57 | 50.123
2019-12-16 | 6:57 | 50.12
2019-12-16 | 6:57 | 50.119
2019-12-16 | 6:57 | 50.117
2019-12-16 | 6:57 | 50.117
2019-12-16 | 6:57 | 50.116
2019-12-16 | 6:57 | 50.115
2019-12-16 | 6:57 | 50.114
2019-12-16 | 6:57 | 50.113
2019-12-16 | 6:57 | 50.111
2019-12-16 | 6:57 | 50.11
2019-12-16 | 6:57 | 50.108
2019-12-16 | 6:57 | 50.106
2019-12-16 | 6:57 | 50.105
2019-12-16 | 6:57 | 50.102
2019-12-16 | 6:57 | 50.1
2019-12-16 | 6:57 | 50.097
2019-12-16 | 6:57 | 50.094
2019-12-16 | 6:57 | 50.092
2019-12-16 | 6:57 | 50.091
2019-12-16 | 6:57 | 50.09
2019-12-16 | 6:57 | 50.085
2019-12-16 | 6:57 | 50.083
2019-12-16 | 6:57 | 50.081
2019-12-16 | 6:57 | 50.079
2019-12-16 | 6:57 | 50.077
2019-12-16 | 6:57 | 50.075
2019-12-16 | 6:58 | 50.074
2019-12-16 | 6:58 | 50.075
2019-12-16 | 6:58 | 50.075
2019-12-16 | 6:58 | 50.072
2019-12-16 | 6:58 | 50.07
2019-12-16 | 6:58 | 50.069
2019-12-16 | 6:58 | 50.067
2019-12-16 | 6:58 | 50.065
2019-12-16 | 6:58 | 50.063
2019-12-16 | 6:58 | 50.062
2019-12-16 | 6:58 | 50.06
2019-12-16 | 6:58 | 50.06
2019-12-16 | 6:58 | 50.059
2019-12-16 | 6:58 | 50.057
2019-12-16 | 6:58 | 50.056
2019-12-16 | 6:58 | 50.055
2019-12-16 | 6:58 | 50.056
2019-12-16 | 6:58 | 50.055
2019-12-16 | 6:58 | 50.055
2019-12-16 | 6:58 | 50.053
2019-12-16 | 6:58 | 50.05
2019-12-16 | 6:58 | 50.046
2019-12-16 | 6:58 | 50.042
2019-12-16 | 6:58 | 50.041
2019-12-16 | 6:58 | 50.04
2019-12-16 | 6:58 | 50.039
2019-12-16 | 6:58 | 50.037
2019-12-16 | 6:58 | 50.034
2019-12-16 | 6:58 | 50.032
2019-12-16 | 6:58 | 50.029
2019-12-16 | 6:58 | 50.025
2019-12-16 | 6:58 | 50.023
2019-12-16 | 6:58 | 50.017
2019-12-16 | 6:58 | 50.015
2019-12-16 | 6:58 | 50.012
2019-12-16 | 6:58 | 50.01
2019-12-16 | 6:58 | 50.008
2019-12-16 | 6:58 | 50.007
2019-12-16 | 6:58 | 50.006
2019-12-16 | 6:58 | 50.006
2019-12-16 | 6:58 | 50.004
2019-12-16 | 6:58 | 50.001
2019-12-16 | 6:58 | 49.998
2019-12-16 | 6:58 | 49.997
2019-12-16 | 6:58 | 49.996
2019-12-16 | 6:58 | 49.997
2019-12-16 | 6:58 | 49.997
2019-12-16 | 6:58 | 49.997
2019-12-16 | 6:58 | 49.997
2019-12-16 | 6:58 | 49.997
2019-12-16 | 6:58 | 49.997
2019-12-16 | 6:58 | 49.995
2019-12-16 | 6:58 | 49.993
2019-12-16 | 6:58 | 49.99
2019-12-16 | 6:58 | 49.987
2019-12-16 | 6:58 | 49.986
2019-12-16 | 6:58 | 49.989
2019-12-16 | 6:58 | 49.993
2019-12-16 | 6:58 | 49.995
2019-12-16 | 6:58 | 49.998
2019-12-16 | 6:59 | 49.997
2019-12-16 | 6:59 | 49.997
2019-12-16 | 6:59 | 49.995
2019-12-16 | 6:59 | 49.993
2019-12-16 | 6:59 | 49.992
2019-12-16 | 6:59 | 49.991
2019-12-16 | 6:59 | 49.989
2019-12-16 | 6:59 | 49.989
2019-12-16 | 6:59 | 49.989
2019-12-16 | 6:59 | 49.989
2019-12-16 | 6:59 | 49.99
2019-12-16 | 6:59 | 49.991
2019-12-16 | 6:59 | 49.994
2019-12-16 | 6:59 | 49.997
2019-12-16 | 6:59 | 49.998
2019-12-16 | 6:59 | 49.997
2019-12-16 | 6:59 | 49.995
2019-12-16 | 6:59 | 49.989
2019-12-16 | 6:59 | 49.983
2019-12-16 | 6:59 | 49.979
2019-12-16 | 6:59 | 49.975
2019-12-16 | 6:59 | 49.974
2019-12-16 | 6:59 | 49.973
2019-12-16 | 6:59 | 49.973
2019-12-16 | 6:59 | 49.973
2019-12-16 | 6:59 | 49.971
2019-12-16 | 6:59 | 49.972
2019-12-16 | 6:59 | 49.971
2019-12-16 | 6:59 | 49.968

## Event 20191217-1
In UTC
Date | Time | Freq
2019-12-17 | 10:52 | 50.094
2019-12-17 | 10:52 | 50.095
2019-12-17 | 10:52 | 50.095
2019-12-17 | 10:52 | 50.095
2019-12-17 | 10:52 | 50.096
2019-12-17 | 10:52 | 50.095
2019-12-17 | 10:52 | 50.093
2019-12-17 | 10:52 | 50.093
2019-12-17 | 10:52 | 50.092
2019-12-17 | 10:52 | 50.092
2019-12-17 | 10:52 | 50.092
2019-12-17 | 10:52 | 50.09
2019-12-17 | 10:52 | 50.09
2019-12-17 | 10:52 | 50.089
2019-12-17 | 10:52 | 50.088
2019-12-17 | 10:52 | 50.088
2019-12-17 | 10:52 | 50.086
2019-12-17 | 10:52 | 50.085
2019-12-17 | 10:52 | 50.083
2019-12-17 | 10:52 | 50.082
2019-12-17 | 10:52 | 50.083
2019-12-17 | 10:52 | 50.084
2019-12-17 | 10:52 | 50.082
2019-12-17 | 10:52 | 50.084
2019-12-17 | 10:52 | 50.084
2019-12-17 | 10:52 | 50.085
2019-12-17 | 10:52 | 50.084
2019-12-17 | 10:52 | 50.082
2019-12-17 | 10:52 | 50.081
2019-12-17 | 10:52 | 50.082
2019-12-17 | 10:52 | 50.082
2019-12-17 | 10:53 | 50.082
2019-12-17 | 10:53 | 50.082
2019-12-17 | 10:53 | 50.081
2019-12-17 | 10:53 | 50.081
2019-12-17 | 10:53 | 50.082
2019-12-17 | 10:53 | 50.084
2019-12-17 | 10:53 | 50.085
2019-12-17 | 10:53 | 50.084
2019-12-17 | 10:53 | 50.084
2019-12-17 | 10:53 | 50.084
2019-12-17 | 10:53 | 50.084
2019-12-17 | 10:53 | 50.084
2019-12-17 | 10:53 | 50.085
2019-12-17 | 10:53 | 50.085
2019-12-17 | 10:53 | 50.086
2019-12-17 | 10:53 | 50.086
2019-12-17 | 10:53 | 50.087
2019-12-17 | 10:53 | 50.09
2019-12-17 | 10:53 | 50.091
2019-12-17 | 10:53 | 50.091
2019-12-17 | 10:53 | 50.091
2019-12-17 | 10:53 | 50.093
2019-12-17 | 10:53 | 50.095
2019-12-17 | 10:53 | 50.095
2019-12-17 | 10:53 | 50.096
2019-12-17 | 10:53 | 50.095
2019-12-17 | 10:53 | 50.093
2019-12-17 | 10:53 | 50.09
2019-12-17 | 10:53 | 50.089
2019-12-17 | 10:53 | 50.087
2019-12-17 | 10:53 | 50.06
2019-12-17 | 10:53 | 50.024
2019-12-17 | 10:53 | 49.967
2019-12-17 | 10:53 | 49.921
2019-12-17 | 10:53 | 49.882
2019-12-17 | 10:53 | 49.853
2019-12-17 | 10:53 | 49.819
2019-12-17 | 10:53 | 49.802
2019-12-17 | 10:53 | 49.786
2019-12-17 | 10:53 | 49.773
2019-12-17 | 10:53 | 49.763
2019-12-17 | 10:53 | 49.756
2019-12-17 | 10:53 | 49.753
2019-12-17 | 10:53 | 49.751
2019-12-17 | 10:53 | 49.751
2019-12-17 | 10:53 | 49.751
2019-12-17 | 10:53 | 49.754
2019-12-17 | 10:53 | 49.756
2019-12-17 | 10:53 | 49.756
2019-12-17 | 10:53 | 49.758
2019-12-17 | 10:53 | 49.76
2019-12-17 | 10:53 | 49.766
2019-12-17 | 10:53 | 49.771
2019-12-17 | 10:53 | 49.774
2019-12-17 | 10:53 | 49.779
2019-12-17 | 10:53 | 49.783
2019-12-17 | 10:53 | 49.785
2019-12-17 | 10:53 | 49.786
2019-12-17 | 10:53 | 49.787
2019-12-17 | 10:54 | 49.79
2019-12-17 | 10:54 | 49.789
2019-12-17 | 10:54 | 49.787
2019-12-17 | 10:54 | 49.786
2019-12-17 | 10:54 | 49.785
2019-12-17 | 10:54 | 49.783
2019-12-17 | 10:54 | 49.781
2019-12-17 | 10:54 | 49.78
2019-12-17 | 10:54 | 49.778
2019-12-17 | 10:54 | 49.777
2019-12-17 | 10:54 | 49.774
2019-12-17 | 10:54 | 49.771
2019-12-17 | 10:54 | 49.769
2019-12-17 | 10:54 | 49.768
2019-12-17 | 10:54 | 49.766
2019-12-17 | 10:54 | 49.763
2019-12-17 | 10:54 | 49.763
2019-12-17 | 10:54 | 49.763
2019-12-17 | 10:54 | 49.765
2019-12-17 | 10:54 | 49.764
2019-12-17 | 10:54 | 49.764
2019-12-17 | 10:54 | 49.762
2019-12-17 | 10:54 | 49.761
2019-12-17 | 10:54 | 49.762
2019-12-17 | 10:54 | 49.761
2019-12-17 | 10:54 | 49.759
2019-12-17 | 10:54 | 49.755
2019-12-17 | 10:54 | 49.753
2019-12-17 | 10:54 | 49.75
2019-12-17 | 10:54 | 49.746
2019-12-17 | 10:54 | 49.743
2019-12-17 | 10:54 | 49.741
2019-12-17 | 10:54 | 49.739
2019-12-17 | 10:54 | 49.737
2019-12-17 | 10:54 | 49.735
2019-12-17 | 10:54 | 49.735
2019-12-17 | 10:54 | 49.738
2019-12-17 | 10:54 | 49.742
2019-12-17 | 10:54 | 49.744
2019-12-17 | 10:54 | 49.746
2019-12-17 | 10:54 | 49.75
2019-12-17 | 10:54 | 49.751
2019-12-17 | 10:54 | 49.752
2019-12-17 | 10:54 | 49.749
2019-12-17 | 10:54 | 49.746
2019-12-17 | 10:54 | 49.744
2019-12-17 | 10:54 | 49.742
2019-12-17 | 10:54 | 49.738
2019-12-17 | 10:54 | 49.734
2019-12-17 | 10:54 | 49.729
2019-12-17 | 10:54 | 49.725
2019-12-17 | 10:54 | 49.723
2019-12-17 | 10:54 | 49.717
2019-12-17 | 10:54 | 49.716
2019-12-17 | 10:54 | 49.718
2019-12-17 | 10:54 | 49.717
2019-12-17 | 10:54 | 49.716
2019-12-17 | 10:54 | 49.714
2019-12-17 | 10:54 | 49.714
2019-12-17 | 10:54 | 49.711
2019-12-17 | 10:54 | 49.713
2019-12-17 | 10:55 | 49.717
2019-12-17 | 10:55 | 49.722
2019-12-17 | 10:55 | 49.735
2019-12-17 | 10:55 | 49.746
2019-12-17 | 10:55 | 49.759
2019-12-17 | 10:55 | 49.769
2019-12-17 | 10:55 | 49.779
2019-12-17 | 10:55 | 49.783
2019-12-17 | 10:55 | 49.786
2019-12-17 | 10:55 | 49.791
2019-12-17 | 10:55 | 49.795
2019-12-17 | 10:55 | 49.796
2019-12-17 | 10:55 | 49.798
2019-12-17 | 10:55 | 49.799
2019-12-17 | 10:55 | 49.8
2019-12-17 | 10:55 | 49.8
2019-12-17 | 10:55 | 49.801
2019-12-17 | 10:55 | 49.804
2019-12-17 | 10:55 | 49.803
2019-12-17 | 10:55 | 49.805
2019-12-17 | 10:55 | 49.806
2019-12-17 | 10:55 | 49.808
2019-12-17 | 10:55 | 49.811
2019-12-17 | 10:55 | 49.814
2019-12-17 | 10:55 | 49.818
2019-12-17 | 10:55 | 49.821
2019-12-17 | 10:55 | 49.826
2019-12-17 | 10:55 | 49.831
2019-12-17 | 10:55 | 49.836
2019-12-17 | 10:55 | 49.839
2019-12-17 | 10:55 | 49.841
2019-12-17 | 10:55 | 49.843
2019-12-17 | 10:55 | 49.846
2019-12-17 | 10:55 | 49.848
2019-12-17 | 10:55 | 49.851
2019-12-17 | 10:55 | 49.852
2019-12-17 | 10:55 | 49.853
2019-12-17 | 10:55 | 49.856
2019-12-17 | 10:55 | 49.858
2019-12-17 | 10:55 | 49.86
2019-12-17 | 10:55 | 49.861
2019-12-17 | 10:55 | 49.862
2019-12-17 | 10:55 | 49.864
2019-12-17 | 10:55 | 49.865
2019-12-17 | 10:55 | 49.864
2019-12-17 | 10:55 | 49.863
2019-12-17 | 10:55 | 49.865
2019-12-17 | 10:55 | 49.864
2019-12-17 | 10:55 | 49.864
2019-12-17 | 10:55 | 49.863
2019-12-17 | 10:55 | 49.865
2019-12-17 | 10:55 | 49.868
2019-12-17 | 10:55 | 49.87
2019-12-17 | 10:55 | 49.873
2019-12-17 | 10:55 | 49.88
2019-12-17 | 10:55 | 49.886
2019-12-17 | 10:55 | 49.89
2019-12-17 | 10:55 | 49.897
2019-12-17 | 10:55 | 49.903
2019-12-17 | 10:56 | 49.909
2019-12-17 | 10:56 | 49.913
2019-12-17 | 10:56 | 49.921
2019-12-17 | 10:56 | 49.93
2019-12-17 | 10:56 | 49.939
2019-12-17 | 10:56 | 49.944
2019-12-17 | 10:56 | 49.948
2019-12-17 | 10:56 | 49.951
2019-12-17 | 10:56 | 49.958
2019-12-17 | 10:56 | 49.962
2019-12-17 | 10:56 | 49.966
2019-12-17 | 10:56 | 49.969
2019-12-17 | 10:56 | 49.971
2019-12-17 | 10:56 | 49.971
2019-12-17 | 10:56 | 49.971
2019-12-17 | 10:56 | 49.972
2019-12-17 | 10:56 | 49.974
2019-12-17 | 10:56 | 49.978
2019-12-17 | 10:56 | 49.979
2019-12-17 | 10:56 | 49.983
2019-12-17 | 10:56 | 49.982
2019-12-17 | 10:56 | 49.984
2019-12-17 | 10:56 | 49.985
2019-12-17 | 10:56 | 49.986
2019-12-17 | 10:56 | 49.989
2019-12-17 | 10:56 | 49.988
2019-12-17 | 10:56 | 49.988
2019-12-17 | 10:56 | 49.99
2019-12-17 | 10:56 | 49.991
2019-12-17 | 10:56 | 49.99
2019-12-17 | 10:56 | 49.991
2019-12-17 | 10:56 | 49.993
2019-12-17 | 10:56 | 49.994
2019-12-17 | 10:56 | 49.994
2019-12-17 | 10:56 | 49.994
2019-12-17 | 10:56 | 49.994
2019-12-17 | 10:56 | 49.996
2019-12-17 | 10:56 | 49.995
2019-12-17 | 10:56 | 49.995
2019-12-17 | 10:56 | 49.998
2019-12-17 | 10:56 | 49.999
2019-12-17 | 10:56 | 50.001
2019-12-17 | 10:56 | 50.002
2019-12-17 | 10:56 | 50.003
2019-12-17 | 10:56 | 50.005
2019-12-17 | 10:56 | 50.005
2019-12-17 | 10:56 | 50.003
2019-12-17 | 10:56 | 50.002
2019-12-17 | 10:56 | 50.004
2019-12-17 | 10:56 | 50.003
2019-12-17 | 10:56 | 50.003
2019-12-17 | 10:56 | 50.005
2019-12-17 | 10:56 | 50.008
2019-12-17 | 10:56 | 50.009
2019-12-17 | 10:56 | 50.01
2019-12-17 | 10:56 | 50.013
2019-12-17 | 10:56 | 50.014
2019-12-17 | 10:56 | 50.016
2019-12-17 | 10:56 | 50.02
2019-12-17 | 10:56 | 50.022
2019-12-17 | 10:56 | 50.023
2019-12-17 | 10:57 | 50.025
2019-12-17 | 10:57 | 50.029
2019-12-17 | 10:57 | 50.031
2019-12-17 | 10:57 | 50.034
2019-12-17 | 10:57 | 50.037
2019-12-17 | 10:57 | 50.037
2019-12-17 | 10:57 | 50.039
2019-12-17 | 10:57 | 50.041
2019-12-17 | 10:57 | 50.042
2019-12-17 | 10:57 | 50.042
2019-12-17 | 10:57 | 50.042
2019-12-17 | 10:57 | 50.045
2019-12-17 | 10:57 | 50.047
2019-12-17 | 10:57 | 50.048
2019-12-17 | 10:57 | 50.048
2019-12-17 | 10:57 | 50.049
2019-12-17 | 10:57 | 50.05
2019-12-17 | 10:57 | 50.051
2019-12-17 | 10:57 | 50.05
2019-12-17 | 10:57 | 50.049
2019-12-17 | 10:57 | 50.049
2019-12-17 | 10:57 | 50.048
2019-12-17 | 10:57 | 50.047
2019-12-17 | 10:57 | 50.049
2019-12-17 | 10:57 | 50.051
2019-12-17 | 10:57 | 50.052
2019-12-17 | 10:57 | 50.057
2019-12-17 | 10:57 | 50.06
2019-12-17 | 10:57 | 50.063

## Event 20191221-1
In UTC
Date | Time | Freq
2019-12-21 | 22:10 | 49.977
2019-12-21 | 22:10 | 49.976
2019-12-21 | 22:10 | 49.97
2019-12-21 | 22:10 | 49.968
2019-12-21 | 22:10 | 49.968
2019-12-21 | 22:10 | 49.968
2019-12-21 | 22:10 | 49.969
2019-12-21 | 22:10 | 49.972
2019-12-21 | 22:10 | 49.972
2019-12-21 | 22:10 | 49.977
2019-12-21 | 22:10 | 49.978
2019-12-21 | 22:10 | 49.982
2019-12-21 | 22:10 | 49.985
2019-12-21 | 22:10 | 49.988
2019-12-21 | 22:10 | 49.991
2019-12-21 | 22:10 | 49.993
2019-12-21 | 22:10 | 49.995
2019-12-21 | 22:10 | 49.994
2019-12-21 | 22:10 | 49.994
2019-12-21 | 22:10 | 49.996
2019-12-21 | 22:10 | 49.995
2019-12-21 | 22:10 | 49.997
2019-12-21 | 22:10 | 49.998
2019-12-21 | 22:10 | 50.003
2019-12-21 | 22:10 | 50.009
2019-12-21 | 22:10 | 50.014
2019-12-21 | 22:10 | 50.017
2019-12-21 | 22:10 | 50.019
2019-12-21 | 22:10 | 50.018
2019-12-21 | 22:10 | 50.02
2019-12-21 | 22:10 | 50.021
2019-12-21 | 22:11 | 50.022
2019-12-21 | 22:11 | 50.022
2019-12-21 | 22:11 | 50.023
2019-12-21 | 22:11 | 50.025
2019-12-21 | 22:11 | 50.025
2019-12-21 | 22:11 | 50.022
2019-12-21 | 22:11 | 50.02
2019-12-21 | 22:11 | 50.017
2019-12-21 | 22:11 | 50.012
2019-12-21 | 22:11 | 50.008
2019-12-21 | 22:11 | 50.006
2019-12-21 | 22:11 | 50.005
2019-12-21 | 22:11 | 50.003
2019-12-21 | 22:11 | 50.005
2019-12-21 | 22:11 | 50.004
2019-12-21 | 22:11 | 50.005
2019-12-21 | 22:11 | 50.006
2019-12-21 | 22:11 | 50.004
2019-12-21 | 22:11 | 50.006
2019-12-21 | 22:11 | 50.006
2019-12-21 | 22:11 | 50.005
2019-12-21 | 22:11 | 50.007
2019-12-21 | 22:11 | 50.008
2019-12-21 | 22:11 | 50.008
2019-12-21 | 22:11 | 50.008
2019-12-21 | 22:11 | 50.008
2019-12-21 | 22:11 | 50.01
2019-12-21 | 22:11 | 50.013
2019-12-21 | 22:11 | 50.013
2019-12-21 | 22:11 | 50.014
2019-12-21 | 22:11 | 50.013
2019-12-21 | 22:11 | 50.013
2019-12-21 | 22:11 | 50.011
2019-12-21 | 22:11 | 50.01
2019-12-21 | 22:11 | 50.008
2019-12-21 | 22:11 | 50.005
2019-12-21 | 22:11 | 50.003
2019-12-21 | 22:11 | 50.001
2019-12-21 | 22:11 | 50
2019-12-21 | 22:11 | 49.998
2019-12-21 | 22:11 | 49.997
2019-12-21 | 22:11 | 49.995
2019-12-21 | 22:11 | 49.996
2019-12-21 | 22:11 | 49.997
2019-12-21 | 22:11 | 49.997
2019-12-21 | 22:11 | 50
2019-12-21 | 22:11 | 50.003
2019-12-21 | 22:11 | 50.005
2019-12-21 | 22:11 | 50.006
2019-12-21 | 22:11 | 50.007
2019-12-21 | 22:11 | 50.01
2019-12-21 | 22:11 | 50.012
2019-12-21 | 22:11 | 50.011
2019-12-21 | 22:11 | 50.014
2019-12-21 | 22:11 | 50.011
2019-12-21 | 22:11 | 50.011
2019-12-21 | 22:11 | 50.012
2019-12-21 | 22:11 | 50.01
2019-12-21 | 22:11 | 50.011
2019-12-21 | 22:12 | 50.009
2019-12-21 | 22:12 | 50.009
2019-12-21 | 22:12 | 50.008
2019-12-21 | 22:12 | 50.007
2019-12-21 | 22:12 | 50.006
2019-12-21 | 22:12 | 50.007
2019-12-21 | 22:12 | 50.006
2019-12-21 | 22:12 | 50.007
2019-12-21 | 22:12 | 50.009
2019-12-21 | 22:12 | 50.011
2019-12-21 | 22:12 | 50.018
2019-12-21 | 22:12 | 50.019
2019-12-21 | 22:12 | 50.022
2019-12-21 | 22:12 | 50.023
2019-12-21 | 22:12 | 50.024
2019-12-21 | 22:12 | 50.025
2019-12-21 | 22:12 | 50.024
2019-12-21 | 22:12 | 50.024
2019-12-21 | 22:12 | 50.026
2019-12-21 | 22:12 | 50.027
2019-12-21 | 22:12 | 50.027
2019-12-21 | 22:12 | 50.026
2019-12-21 | 22:12 | 50.028
2019-12-21 | 22:12 | 50.026
2019-12-21 | 22:12 | 50.025
2019-12-21 | 22:12 | 50.024
2019-12-21 | 22:12 | 50.021
2019-12-21 | 22:12 | 50.021
2019-12-21 | 22:12 | 50.021
2019-12-21 | 22:12 | 50.021
2019-12-21 | 22:12 | 50.02
2019-12-21 | 22:12 | 50.018
2019-12-21 | 22:12 | 50.018
2019-12-21 | 22:12 | 50.014
2019-12-21 | 22:12 | 50.014
2019-12-21 | 22:12 | 50.01
2019-12-21 | 22:12 | 50.009
2019-12-21 | 22:12 | 50.01
2019-12-21 | 22:12 | 50.01
2019-12-21 | 22:12 | 50.011
2019-12-21 | 22:12 | 50.011
2019-12-21 | 22:12 | 50.009
2019-12-21 | 22:12 | 50.011
2019-12-21 | 22:12 | 50.009
2019-12-21 | 22:12 | 49.991
2019-12-21 | 22:12 | 49.965
2019-12-21 | 22:12 | 49.945
2019-12-21 | 22:12 | 49.93
2019-12-21 | 22:12 | 49.917
2019-12-21 | 22:12 | 49.91
2019-12-21 | 22:12 | 49.906
2019-12-21 | 22:12 | 49.903
2019-12-21 | 22:12 | 49.903
2019-12-21 | 22:12 | 49.904
2019-12-21 | 22:12 | 49.905
2019-12-21 | 22:12 | 49.908
2019-12-21 | 22:12 | 49.911
2019-12-21 | 22:12 | 49.914
2019-12-21 | 22:12 | 49.916
2019-12-21 | 22:12 | 49.917
2019-12-21 | 22:12 | 49.918
2019-12-21 | 22:13 | 49.919
2019-12-21 | 22:13 | 49.917
2019-12-21 | 22:13 | 49.918
2019-12-21 | 22:13 | 49.921
2019-12-21 | 22:13 | 49.921
2019-12-21 | 22:13 | 49.92
2019-12-21 | 22:13 | 49.919
2019-12-21 | 22:13 | 49.917
2019-12-21 | 22:13 | 49.915
2019-12-21 | 22:13 | 49.914
2019-12-21 | 22:13 | 49.91
2019-12-21 | 22:13 | 49.908
2019-12-21 | 22:13 | 49.907
2019-12-21 | 22:13 | 49.905
2019-12-21 | 22:13 | 49.906
2019-12-21 | 22:13 | 49.908
2019-12-21 | 22:13 | 49.908
2019-12-21 | 22:13 | 49.911
2019-12-21 | 22:13 | 49.912
2019-12-21 | 22:13 | 49.915
2019-12-21 | 22:13 | 49.917
2019-12-21 | 22:13 | 49.921
2019-12-21 | 22:13 | 49.924
2019-12-21 | 22:13 | 49.925
2019-12-21 | 22:13 | 49.925
2019-12-21 | 22:13 | 49.929
2019-12-21 | 22:13 | 49.932
2019-12-21 | 22:13 | 49.933
2019-12-21 | 22:13 | 49.931
2019-12-21 | 22:13 | 49.931
2019-12-21 | 22:13 | 49.933
2019-12-21 | 22:13 | 49.932
2019-12-21 | 22:13 | 49.932
2019-12-21 | 22:13 | 49.933
2019-12-21 | 22:13 | 49.932
2019-12-21 | 22:13 | 49.929
2019-12-21 | 22:13 | 49.93
2019-12-21 | 22:13 | 49.93
2019-12-21 | 22:13 | 49.929
2019-12-21 | 22:13 | 49.932
2019-12-21 | 22:13 | 49.933
2019-12-21 | 22:13 | 49.93
2019-12-21 | 22:13 | 49.93
2019-12-21 | 22:13 | 49.929
2019-12-21 | 22:13 | 49.932
2019-12-21 | 22:13 | 49.934
2019-12-21 | 22:13 | 49.935
2019-12-21 | 22:13 | 49.935
2019-12-21 | 22:13 | 49.937
2019-12-21 | 22:13 | 49.938
2019-12-21 | 22:13 | 49.939
2019-12-21 | 22:13 | 49.941
2019-12-21 | 22:13 | 49.94
2019-12-21 | 22:13 | 49.941
2019-12-21 | 22:13 | 49.941
2019-12-21 | 22:13 | 49.94
2019-12-21 | 22:13 | 49.939
2019-12-21 | 22:13 | 49.937
2019-12-21 | 22:13 | 49.936
2019-12-21 | 22:14 | 49.937
2019-12-21 | 22:14 | 49.935
2019-12-21 | 22:14 | 49.933
2019-12-21 | 22:14 | 49.932
2019-12-21 | 22:14 | 49.931
2019-12-21 | 22:14 | 49.928
2019-12-21 | 22:14 | 49.927
2019-12-21 | 22:14 | 49.927
2019-12-21 | 22:14 | 49.926
2019-12-21 | 22:14 | 49.927
2019-12-21 | 22:14 | 49.926
2019-12-21 | 22:14 | 49.926
2019-12-21 | 22:14 | 49.927
2019-12-21 | 22:14 | 49.928
2019-12-21 | 22:14 | 49.93
2019-12-21 | 22:14 | 49.931
2019-12-21 | 22:14 | 49.931
2019-12-21 | 22:14 | 49.932
2019-12-21 | 22:14 | 49.933
2019-12-21 | 22:14 | 49.934
2019-12-21 | 22:14 | 49.933
2019-12-21 | 22:14 | 49.931
2019-12-21 | 22:14 | 49.931
2019-12-21 | 22:14 | 49.93
2019-12-21 | 22:14 | 49.929
2019-12-21 | 22:14 | 49.93
2019-12-21 | 22:14 | 49.931
2019-12-21 | 22:14 | 49.934
2019-12-21 | 22:14 | 49.933
2019-12-21 | 22:14 | 49.933
2019-12-21 | 22:14 | 49.933
2019-12-21 | 22:14 | 49.93
2019-12-21 | 22:14 | 49.928
2019-12-21 | 22:14 | 49.93
2019-12-21 | 22:14 | 49.927
2019-12-21 | 22:14 | 49.926
2019-12-21 | 22:14 | 49.926
2019-12-21 | 22:14 | 49.924
2019-12-21 | 22:14 | 49.922
2019-12-21 | 22:14 | 49.923
2019-12-21 | 22:14 | 49.924
2019-12-21 | 22:14 | 49.924
2019-12-21 | 22:14 | 49.922
2019-12-21 | 22:14 | 49.923
2019-12-21 | 22:14 | 49.922
2019-12-21 | 22:14 | 49.921
2019-12-21 | 22:14 | 49.92
2019-12-21 | 22:14 | 49.917
2019-12-21 | 22:14 | 49.913
2019-12-21 | 22:14 | 49.91
2019-12-21 | 22:14 | 49.909
2019-12-21 | 22:14 | 49.908
2019-12-21 | 22:14 | 49.909
2019-12-21 | 22:14 | 49.91
2019-12-21 | 22:14 | 49.913
2019-12-21 | 22:14 | 49.914
2019-12-21 | 22:14 | 49.913
2019-12-21 | 22:14 | 49.916
2019-12-21 | 22:14 | 49.917
2019-12-21 | 22:14 | 49.92
2019-12-21 | 22:14 | 49.923
2019-12-21 | 22:15 | 49.922
2019-12-21 | 22:15 | 49.926
2019-12-21 | 22:15 | 49.928
2019-12-21 | 22:15 | 49.931
2019-12-21 | 22:15 | 49.931
2019-12-21 | 22:15 | 49.932
2019-12-21 | 22:15 | 49.931
2019-12-21 | 22:15 | 49.931
2019-12-21 | 22:15 | 49.929
2019-12-21 | 22:15 | 49.928
2019-12-21 | 22:15 | 49.925
2019-12-21 | 22:15 | 49.923
2019-12-21 | 22:15 | 49.921
2019-12-21 | 22:15 | 49.919
2019-12-21 | 22:15 | 49.918
2019-12-21 | 22:15 | 49.917
2019-12-21 | 22:15 | 49.917
2019-12-21 | 22:15 | 49.918
2019-12-21 | 22:15 | 49.916
2019-12-21 | 22:15 | 49.913
2019-12-21 | 22:15 | 49.913
2019-12-21 | 22:15 | 49.911
2019-12-21 | 22:15 | 49.91
2019-12-21 | 22:15 | 49.905
2019-12-21 | 22:15 | 49.904
2019-12-21 | 22:15 | 49.901
2019-12-21 | 22:15 | 49.898
2019-12-21 | 22:15 | 49.894
2019-12-21 | 22:15 | 49.893
2019-12-21 | 22:15 | 49.89
2019-12-21 | 22:15 | 49.888
2019-12-21 | 22:15 | 49.888
2019-12-21 | 22:15 | 49.89
2019-12-21 | 22:15 | 49.892
2019-12-21 | 22:15 | 49.894
2019-12-21 | 22:15 | 49.894
2019-12-21 | 22:15 | 49.897
2019-12-21 | 22:15 | 49.899
2019-12-21 | 22:15 | 49.897
2019-12-21 | 22:15 | 49.899
2019-12-21 | 22:15 | 49.9
2019-12-21 | 22:15 | 49.899
2019-12-21 | 22:15 | 49.897
2019-12-21 | 22:15 | 49.896
2019-12-21 | 22:15 | 49.893
2019-12-21 | 22:15 | 49.892
2019-12-21 | 22:15 | 49.89
2019-12-21 | 22:15 | 49.888
2019-12-21 | 22:15 | 49.888
2019-12-21 | 22:15 | 49.889
2019-12-21 | 22:15 | 49.889
2019-12-21 | 22:15 | 49.887
2019-12-21 | 22:15 | 49.886
2019-12-21 | 22:15 | 49.884
2019-12-21 | 22:15 | 49.882
2019-12-21 | 22:15 | 49.882
2019-12-21 | 22:15 | 49.882
2019-12-21 | 22:15 | 49.881
2019-12-21 | 22:15 | 49.881
2019-12-21 | 22:16 | 49.88
2019-12-21 | 22:16 | 49.879
2019-12-21 | 22:16 | 49.879
2019-12-21 | 22:16 | 49.879
2019-12-21 | 22:16 | 49.881
2019-12-21 | 22:16 | 49.881
2019-12-21 | 22:16 | 49.883
2019-12-21 | 22:16 | 49.885
2019-12-21 | 22:16 | 49.887
2019-12-21 | 22:16 | 49.889
2019-12-21 | 22:16 | 49.891
2019-12-21 | 22:16 | 49.892
2019-12-21 | 22:16 | 49.893
2019-12-21 | 22:16 | 49.891
2019-12-21 | 22:16 | 49.893
2019-12-21 | 22:16 | 49.894
2019-12-21 | 22:16 | 49.893
2019-12-21 | 22:16 | 49.892
2019-12-21 | 22:16 | 49.892
2019-12-21 | 22:16 | 49.893
2019-12-21 | 22:16 | 49.891
2019-12-21 | 22:16 | 49.89
2019-12-21 | 22:16 | 49.889
2019-12-21 | 22:16 | 49.888
2019-12-21 | 22:16 | 49.886
2019-12-21 | 22:16 | 49.885
2019-12-21 | 22:16 | 49.884
2019-12-21 | 22:16 | 49.883
2019-12-21 | 22:16 | 49.886
2019-12-21 | 22:16 | 49.886
2019-12-21 | 22:16 | 49.889
2019-12-21 | 22:16 | 49.887
2019-12-21 | 22:16 | 49.884
2019-12-21 | 22:16 | 49.884
2019-12-21 | 22:16 | 49.883
2019-12-21 | 22:16 | 49.88
2019-12-21 | 22:16 | 49.878
2019-12-21 | 22:16 | 49.877
2019-12-21 | 22:16 | 49.876
2019-12-21 | 22:16 | 49.877
2019-12-21 | 22:16 | 49.88
2019-12-21 | 22:16 | 49.881
2019-12-21 | 22:16 | 49.881
2019-12-21 | 22:16 | 49.88
2019-12-21 | 22:16 | 49.879
2019-12-21 | 22:16 | 49.877
2019-12-21 | 22:16 | 49.876
2019-12-21 | 22:16 | 49.877
2019-12-21 | 22:16 | 49.877
2019-12-21 | 22:16 | 49.878
2019-12-21 | 22:16 | 49.878
2019-12-21 | 22:16 | 49.878
2019-12-21 | 22:16 | 49.879
2019-12-21 | 22:16 | 49.878
2019-12-21 | 22:16 | 49.88
2019-12-21 | 22:16 | 49.878
2019-12-21 | 22:16 | 49.878
2019-12-21 | 22:16 | 49.879
2019-12-21 | 22:16 | 49.882
2019-12-21 | 22:16 | 49.885
2019-12-21 | 22:16 | 49.887
2019-12-21 | 22:17 | 49.891
2019-12-21 | 22:17 | 49.893
2019-12-21 | 22:17 | 49.892
2019-12-21 | 22:17 | 49.891
2019-12-21 | 22:17 | 49.888
2019-12-21 | 22:17 | 49.886
2019-12-21 | 22:17 | 49.883
2019-12-21 | 22:17 | 49.882
2019-12-21 | 22:17 | 49.881
2019-12-21 | 22:17 | 49.879
2019-12-21 | 22:17 | 49.879
2019-12-21 | 22:17 | 49.876
2019-12-21 | 22:17 | 49.873
2019-12-21 | 22:17 | 49.871
2019-12-21 | 22:17 | 49.871
2019-12-21 | 22:17 | 49.867
2019-12-21 | 22:17 | 49.867
2019-12-21 | 22:17 | 49.865
2019-12-21 | 22:17 | 49.864
2019-12-21 | 22:17 | 49.862
2019-12-21 | 22:17 | 49.861
2019-12-21 | 22:17 | 49.859
2019-12-21 | 22:17 | 49.859
2019-12-21 | 22:17 | 49.859
2019-12-21 | 22:17 | 49.86
2019-12-21 | 22:17 | 49.861
2019-12-21 | 22:17 | 49.862
2019-12-21 | 22:17 | 49.864
2019-12-21 | 22:17 | 49.865
2019-12-21 | 22:17 | 49.866
2019-12-21 | 22:17 | 49.866
2019-12-21 | 22:17 | 49.866
2019-12-21 | 22:17 | 49.868
2019-12-21 | 22:17 | 49.87
2019-12-21 | 22:17 | 49.873
2019-12-21 | 22:17 | 49.876
2019-12-21 | 22:17 | 49.879
2019-12-21 | 22:17 | 49.882
2019-12-21 | 22:17 | 49.886
2019-12-21 | 22:17 | 49.89
2019-12-21 | 22:17 | 49.894
2019-12-21 | 22:17 | 49.897
2019-12-21 | 22:17 | 49.897
2019-12-21 | 22:17 | 49.897
2019-12-21 | 22:17 | 49.898
2019-12-21 | 22:17 | 49.896
2019-12-21 | 22:17 | 49.896
2019-12-21 | 22:17 | 49.899
2019-12-21 | 22:17 | 49.901
2019-12-21 | 22:17 | 49.902
2019-12-21 | 22:17 | 49.903
2019-12-21 | 22:17 | 49.904
2019-12-21 | 22:17 | 49.904
2019-12-21 | 22:17 | 49.903
2019-12-21 | 22:17 | 49.902
2019-12-21 | 22:17 | 49.901
2019-12-21 | 22:17 | 49.9
2019-12-21 | 22:17 | 49.901
2019-12-21 | 22:17 | 49.9
2019-12-21 | 22:18 | 49.903
2019-12-21 | 22:18 | 49.906
2019-12-21 | 22:18 | 49.908
2019-12-21 | 22:18 | 49.911
2019-12-21 | 22:18 | 49.914
2019-12-21 | 22:18 | 49.914
2019-12-21 | 22:18 | 49.916
2019-12-21 | 22:18 | 49.916
2019-12-21 | 22:18 | 49.916
2019-12-21 | 22:18 | 49.916
2019-12-21 | 22:18 | 49.917
2019-12-21 | 22:18 | 49.919
2019-12-21 | 22:18 | 49.922
2019-12-21 | 22:18 | 49.923
2019-12-21 | 22:18 | 49.923
2019-12-21 | 22:18 | 49.925
2019-12-21 | 22:18 | 49.925
2019-12-21 | 22:18 | 49.924
2019-12-21 | 22:18 | 49.925
2019-12-21 | 22:18 | 49.925
2019-12-21 | 22:18 | 49.924
2019-12-21 | 22:18 | 49.927
2019-12-21 | 22:18 | 49.93
2019-12-21 | 22:18 | 49.931
2019-12-21 | 22:18 | 49.933
2019-12-21 | 22:18 | 49.935
2019-12-21 | 22:18 | 49.937
2019-12-21 | 22:18 | 49.939
2019-12-21 | 22:18 | 49.94
2019-12-21 | 22:18 | 49.94
2019-12-21 | 22:18 | 49.938
2019-12-21 | 22:18 | 49.937
2019-12-21 | 22:18 | 49.934
2019-12-21 | 22:18 | 49.928
2019-12-21 | 22:18 | 49.922
2019-12-21 | 22:18 | 49.92
2019-12-21 | 22:18 | 49.918
2019-12-21 | 22:18 | 49.914
2019-12-21 | 22:18 | 49.913
2019-12-21 | 22:18 | 49.912
2019-12-21 | 22:18 | 49.912
2019-12-21 | 22:18 | 49.913
2019-12-21 | 22:18 | 49.914
2019-12-21 | 22:18 | 49.912
2019-12-21 | 22:18 | 49.913
2019-12-21 | 22:18 | 49.913
2019-12-21 | 22:18 | 49.91
2019-12-21 | 22:18 | 49.911
2019-12-21 | 22:18 | 49.91
2019-12-21 | 22:18 | 49.908
2019-12-21 | 22:18 | 49.91
2019-12-21 | 22:18 | 49.91
2019-12-21 | 22:18 | 49.91
2019-12-21 | 22:18 | 49.912
2019-12-21 | 22:18 | 49.913
2019-12-21 | 22:18 | 49.913
2019-12-21 | 22:18 | 49.914
2019-12-21 | 22:18 | 49.916
2019-12-21 | 22:18 | 49.915
2019-12-21 | 22:18 | 49.916
2019-12-21 | 22:18 | 49.917
2019-12-21 | 22:19 | 49.917
2019-12-21 | 22:19 | 49.917
2019-12-21 | 22:19 | 49.917
2019-12-21 | 22:19 | 49.919
2019-12-21 | 22:19 | 49.919
2019-12-21 | 22:19 | 49.92
2019-12-21 | 22:19 | 49.919
2019-12-21 | 22:19 | 49.919
2019-12-21 | 22:19 | 49.917
2019-12-21 | 22:19 | 49.92
2019-12-21 | 22:19 | 49.92
2019-12-21 | 22:19 | 49.919
2019-12-21 | 22:19 | 49.918
2019-12-21 | 22:19 | 49.916
2019-12-21 | 22:19 | 49.915
2019-12-21 | 22:19 | 49.913
2019-12-21 | 22:19 | 49.914
2019-12-21 | 22:19 | 49.915
2019-12-21 | 22:19 | 49.915
2019-12-21 | 22:19 | 49.916
2019-12-21 | 22:19 | 49.915
2019-12-21 | 22:19 | 49.916
2019-12-21 | 22:19 | 49.913
2019-12-21 | 22:19 | 49.916
2019-12-21 | 22:19 | 49.915
2019-12-21 | 22:19 | 49.916
2019-12-21 | 22:19 | 49.919
2019-12-21 | 22:19 | 49.924
2019-12-21 | 22:19 | 49.926
2019-12-21 | 22:19 | 49.93
2019-12-21 | 22:19 | 49.931
2019-12-21 | 22:19 | 49.932
2019-12-21 | 22:19 | 49.932
2019-12-21 | 22:19 | 49.933
2019-12-21 | 22:19 | 49.934
2019-12-21 | 22:19 | 49.933
2019-12-21 | 22:19 | 49.933
2019-12-21 | 22:19 | 49.933
2019-12-21 | 22:19 | 49.933
2019-12-21 | 22:19 | 49.933
2019-12-21 | 22:19 | 49.933
2019-12-21 | 22:19 | 49.934
2019-12-21 | 22:19 | 49.935
2019-12-21 | 22:19 | 49.933
2019-12-21 | 22:19 | 49.931
2019-12-21 | 22:19 | 49.931
2019-12-21 | 22:19 | 49.931
2019-12-21 | 22:19 | 49.93
2019-12-21 | 22:19 | 49.932
2019-12-21 | 22:19 | 49.931
2019-12-21 | 22:19 | 49.928
2019-12-21 | 22:19 | 49.931
2019-12-21 | 22:19 | 49.931
2019-12-21 | 22:19 | 49.935
2019-12-21 | 22:19 | 49.937
2019-12-21 | 22:19 | 49.939
2019-12-21 | 22:19 | 49.941
2019-12-21 | 22:19 | 49.94
2019-12-21 | 22:19 | 49.942
2019-12-21 | 22:20 | 49.941
2019-12-21 | 22:20 | 49.942
2019-12-21 | 22:20 | 49.945
2019-12-21 | 22:20 | 49.942
2019-12-21 | 22:20 | 49.94
2019-12-21 | 22:20 | 49.941
2019-12-21 | 22:20 | 49.938
2019-12-21 | 22:20 | 49.938
2019-12-21 | 22:20 | 49.94
2019-12-21 | 22:20 | 49.943
2019-12-21 | 22:20 | 49.943
2019-12-21 | 22:20 | 49.948
2019-12-21 | 22:20 | 49.952
2019-12-21 | 22:20 | 49.952
2019-12-21 | 22:20 | 49.956
2019-12-21 | 22:20 | 49.957
2019-12-21 | 22:20 | 49.958
2019-12-21 | 22:20 | 49.962
2019-12-21 | 22:20 | 49.962
2019-12-21 | 22:20 | 49.962
2019-12-21 | 22:20 | 49.963
2019-12-21 | 22:20 | 49.96
2019-12-21 | 22:20 | 49.958
2019-12-21 | 22:20 | 49.955
2019-12-21 | 22:20 | 49.954
2019-12-21 | 22:20 | 49.953
2019-12-21 | 22:20 | 49.953
2019-12-21 | 22:20 | 49.954
2019-12-21 | 22:20 | 49.953
2019-12-21 | 22:20 | 49.951
2019-12-21 | 22:20 | 49.951
2019-12-21 | 22:20 | 49.951
2019-12-21 | 22:20 | 49.95
2019-12-21 | 22:20 | 49.954
2019-12-21 | 22:20 | 49.955
2019-12-21 | 22:20 | 49.956
2019-12-21 | 22:20 | 49.957
2019-12-21 | 22:20 | 49.957
2019-12-21 | 22:20 | 49.956
2019-12-21 | 22:20 | 49.952
2019-12-21 | 22:20 | 49.953
2019-12-21 | 22:20 | 49.952
2019-12-21 | 22:20 | 49.949
2019-12-21 | 22:20 | 49.948
2019-12-21 | 22:20 | 49.943
2019-12-21 | 22:20 | 49.942
2019-12-21 | 22:20 | 49.942
2019-12-21 | 22:20 | 49.945
2019-12-21 | 22:20 | 49.943
2019-12-21 | 22:20 | 49.943
2019-12-21 | 22:20 | 49.945
2019-12-21 | 22:20 | 49.945
2019-12-21 | 22:20 | 49.945
2019-12-21 | 22:20 | 49.946
2019-12-21 | 22:20 | 49.946
2019-12-21 | 22:20 | 49.946
2019-12-21 | 22:20 | 49.948
2019-12-21 | 22:20 | 49.947
2019-12-21 | 22:20 | 49.948
2019-12-21 | 22:20 | 49.951
2019-12-21 | 22:20 | 49.951
2019-12-21 | 22:21 | 49.951
2019-12-21 | 22:21 | 49.953
2019-12-21 | 22:21 | 49.957
2019-12-21 | 22:21 | 49.961
2019-12-21 | 22:21 | 49.964
2019-12-21 | 22:21 | 49.969
2019-12-21 | 22:21 | 49.97
2019-12-21 | 22:21 | 49.97
2019-12-21 | 22:21 | 49.969
2019-12-21 | 22:21 | 49.97
2019-12-21 | 22:21 | 49.969
2019-12-21 | 22:21 | 49.968
2019-12-21 | 22:21 | 49.97
2019-12-21 | 22:21 | 49.97
2019-12-21 | 22:21 | 49.969
2019-12-21 | 22:21 | 49.966
2019-12-21 | 22:21 | 49.967
2019-12-21 | 22:21 | 49.966
2019-12-21 | 22:21 | 49.964
2019-12-21 | 22:21 | 49.965
2019-12-21 | 22:21 | 49.963
2019-12-21 | 22:21 | 49.961
2019-12-21 | 22:21 | 49.961
2019-12-21 | 22:21 | 49.962
2019-12-21 | 22:21 | 49.961
2019-12-21 | 22:21 | 49.962
2019-12-21 | 22:21 | 49.961
2019-12-21 | 22:21 | 49.956
2019-12-21 | 22:21 | 49.955
2019-12-21 | 22:21 | 49.951
2019-12-21 | 22:21 | 49.949
2019-12-21 | 22:21 | 49.949
2019-12-21 | 22:21 | 49.948
2019-12-21 | 22:21 | 49.95
2019-12-21 | 22:21 | 49.951
2019-12-21 | 22:21 | 49.949
2019-12-21 | 22:21 | 49.95
2019-12-21 | 22:21 | 49.947
2019-12-21 | 22:21 | 49.949
2019-12-21 | 22:21 | 49.95
2019-12-21 | 22:21 | 49.949
2019-12-21 | 22:21 | 49.95
2019-12-21 | 22:21 | 49.951
2019-12-21 | 22:21 | 49.953
2019-12-21 | 22:21 | 49.952
2019-12-21 | 22:21 | 49.955
2019-12-21 | 22:21 | 49.955
2019-12-21 | 22:21 | 49.956
2019-12-21 | 22:21 | 49.956
2019-12-21 | 22:21 | 49.955
2019-12-21 | 22:21 | 49.955
2019-12-21 | 22:21 | 49.955
2019-12-21 | 22:21 | 49.958
2019-12-21 | 22:21 | 49.955
2019-12-21 | 22:21 | 49.957
2019-12-21 | 22:21 | 49.955
2019-12-21 | 22:21 | 49.957
2019-12-21 | 22:21 | 49.961
2019-12-21 | 22:21 | 49.963
2019-12-21 | 22:22 | 49.965
2019-12-21 | 22:22 | 49.967
2019-12-21 | 22:22 | 49.971
2019-12-21 | 22:22 | 49.971
2019-12-21 | 22:22 | 49.975
2019-12-21 | 22:22 | 49.977
2019-12-21 | 22:22 | 49.981
2019-12-21 | 22:22 | 49.983
2019-12-21 | 22:22 | 49.988
2019-12-21 | 22:22 | 49.989
2019-12-21 | 22:22 | 49.992
2019-12-21 | 22:22 | 49.992
2019-12-21 | 22:22 | 49.996
2019-12-21 | 22:22 | 49.997
2019-12-21 | 22:22 | 49.998
2019-12-21 | 22:22 | 50
2019-12-21 | 22:22 | 49.998
2019-12-21 | 22:22 | 50
2019-12-21 | 22:22 | 49.999
2019-12-21 | 22:22 | 50
2019-12-21 | 22:22 | 50.002
2019-12-21 | 22:22 | 50.003
2019-12-21 | 22:22 | 50.006
2019-12-21 | 22:22 | 50.005
2019-12-21 | 22:22 | 50.008
2019-12-21 | 22:22 | 50.011
2019-12-21 | 22:22 | 50.012
2019-12-21 | 22:22 | 50.015
2019-12-21 | 22:22 | 50.014
2019-12-21 | 22:22 | 50.016

## Event 20191222-1
In UTC
Date | Time | Freq
2019-12-22 | 18:01 | 50.055
2019-12-22 | 18:01 | 50.054
2019-12-22 | 18:01 | 50.053
2019-12-22 | 18:01 | 50.053
2019-12-22 | 18:01 | 50.05
2019-12-22 | 18:01 | 50.047
2019-12-22 | 18:01 | 50.048
2019-12-22 | 18:01 | 50.046
2019-12-22 | 18:01 | 50.046
2019-12-22 | 18:01 | 50.045
2019-12-22 | 18:01 | 50.044
2019-12-22 | 18:01 | 50.041
2019-12-22 | 18:01 | 50.039
2019-12-22 | 18:01 | 50.04
2019-12-22 | 18:01 | 50.039
2019-12-22 | 18:01 | 50.039
2019-12-22 | 18:01 | 50.039
2019-12-22 | 18:01 | 50.041
2019-12-22 | 18:01 | 50.04
2019-12-22 | 18:01 | 50.039
2019-12-22 | 18:01 | 50.039
2019-12-22 | 18:01 | 50.039
2019-12-22 | 18:01 | 50.038
2019-12-22 | 18:01 | 50.038
2019-12-22 | 18:01 | 50.04
2019-12-22 | 18:01 | 50.04
2019-12-22 | 18:01 | 50.042
2019-12-22 | 18:01 | 50.042
2019-12-22 | 18:01 | 50.044
2019-12-22 | 18:01 | 50.046
2019-12-22 | 18:02 | 50.047
2019-12-22 | 18:02 | 50.047
2019-12-22 | 18:02 | 50.048
2019-12-22 | 18:02 | 50.051
2019-12-22 | 18:02 | 50.051
2019-12-22 | 18:02 | 50.053
2019-12-22 | 18:02 | 50.053
2019-12-22 | 18:02 | 50.053
2019-12-22 | 18:02 | 50.051
2019-12-22 | 18:02 | 50.049
2019-12-22 | 18:02 | 50.047
2019-12-22 | 18:02 | 50.047
2019-12-22 | 18:02 | 50.047
2019-12-22 | 18:02 | 50.044
2019-12-22 | 18:02 | 50.043
2019-12-22 | 18:02 | 50.042
2019-12-22 | 18:02 | 50.04
2019-12-22 | 18:02 | 50.037
2019-12-22 | 18:02 | 50.034
2019-12-22 | 18:02 | 50.034
2019-12-22 | 18:02 | 50.033
2019-12-22 | 18:02 | 50.033
2019-12-22 | 18:02 | 50.034
2019-12-22 | 18:02 | 50.038
2019-12-22 | 18:02 | 50.041
2019-12-22 | 18:02 | 50.044
2019-12-22 | 18:02 | 50.049
2019-12-22 | 18:02 | 50.053
2019-12-22 | 18:02 | 50.055
2019-12-22 | 18:02 | 50.055
2019-12-22 | 18:02 | 50.056
2019-12-22 | 18:02 | 50.057
2019-12-22 | 18:02 | 50.059
2019-12-22 | 18:02 | 50.058
2019-12-22 | 18:02 | 50.06
2019-12-22 | 18:02 | 50.057
2019-12-22 | 18:02 | 50.057
2019-12-22 | 18:02 | 50.056
2019-12-22 | 18:02 | 50.054
2019-12-22 | 18:02 | 50.051
2019-12-22 | 18:02 | 50.046
2019-12-22 | 18:02 | 50.044
2019-12-22 | 18:02 | 50.042
2019-12-22 | 18:02 | 50.039
2019-12-22 | 18:02 | 50.037
2019-12-22 | 18:02 | 50.034
2019-12-22 | 18:02 | 50.034
2019-12-22 | 18:02 | 50.033
2019-12-22 | 18:02 | 50.033
2019-12-22 | 18:02 | 50.033
2019-12-22 | 18:02 | 50.032
2019-12-22 | 18:02 | 50.034
2019-12-22 | 18:02 | 49.996
2019-12-22 | 18:02 | 49.928
2019-12-22 | 18:02 | 49.864
2019-12-22 | 18:02 | 49.814
2019-12-22 | 18:02 | 49.775
2019-12-22 | 18:02 | 49.745
2019-12-22 | 18:02 | 49.721
2019-12-22 | 18:02 | 49.71
2019-12-22 | 18:02 | 49.701
2019-12-22 | 18:03 | 49.697
2019-12-22 | 18:03 | 49.696
2019-12-22 | 18:03 | 49.697
2019-12-22 | 18:03 | 49.7
2019-12-22 | 18:03 | 49.701
2019-12-22 | 18:03 | 49.704
2019-12-22 | 18:03 | 49.709
2019-12-22 | 18:03 | 49.712
2019-12-22 | 18:03 | 49.714
2019-12-22 | 18:03 | 49.716
2019-12-22 | 18:03 | 49.718
2019-12-22 | 18:03 | 49.719
2019-12-22 | 18:03 | 49.72
2019-12-22 | 18:03 | 49.718
2019-12-22 | 18:03 | 49.721
2019-12-22 | 18:03 | 49.724
2019-12-22 | 18:03 | 49.725
2019-12-22 | 18:03 | 49.729
2019-12-22 | 18:03 | 49.734
2019-12-22 | 18:03 | 49.738
2019-12-22 | 18:03 | 49.741
2019-12-22 | 18:03 | 49.745
2019-12-22 | 18:03 | 49.743
2019-12-22 | 18:03 | 49.744
2019-12-22 | 18:03 | 49.744
2019-12-22 | 18:03 | 49.741
2019-12-22 | 18:03 | 49.74
2019-12-22 | 18:03 | 49.737
2019-12-22 | 18:03 | 49.735
2019-12-22 | 18:03 | 49.734
2019-12-22 | 18:03 | 49.729
2019-12-22 | 18:03 | 49.727
2019-12-22 | 18:03 | 49.724
2019-12-22 | 18:03 | 49.722
2019-12-22 | 18:03 | 49.721
2019-12-22 | 18:03 | 49.719
2019-12-22 | 18:03 | 49.716
2019-12-22 | 18:03 | 49.717
2019-12-22 | 18:03 | 49.717
2019-12-22 | 18:03 | 49.718
2019-12-22 | 18:03 | 49.72
2019-12-22 | 18:03 | 49.721
2019-12-22 | 18:03 | 49.719
2019-12-22 | 18:03 | 49.72
2019-12-22 | 18:03 | 49.719
2019-12-22 | 18:03 | 49.717
2019-12-22 | 18:03 | 49.717
2019-12-22 | 18:03 | 49.717
2019-12-22 | 18:03 | 49.716
2019-12-22 | 18:03 | 49.714
2019-12-22 | 18:03 | 49.711
2019-12-22 | 18:03 | 49.711
2019-12-22 | 18:03 | 49.713
2019-12-22 | 18:03 | 49.714
2019-12-22 | 18:03 | 49.714
2019-12-22 | 18:03 | 49.714
2019-12-22 | 18:03 | 49.717
2019-12-22 | 18:03 | 49.716
2019-12-22 | 18:03 | 49.716
2019-12-22 | 18:04 | 49.717
2019-12-22 | 18:04 | 49.719
2019-12-22 | 18:04 | 49.721
2019-12-22 | 18:04 | 49.722
2019-12-22 | 18:04 | 49.722
2019-12-22 | 18:04 | 49.723
2019-12-22 | 18:04 | 49.726
2019-12-22 | 18:04 | 49.726
2019-12-22 | 18:04 | 49.728
2019-12-22 | 18:04 | 49.732
2019-12-22 | 18:04 | 49.735
2019-12-22 | 18:04 | 49.737
2019-12-22 | 18:04 | 49.741
2019-12-22 | 18:04 | 49.742
2019-12-22 | 18:04 | 49.744
2019-12-22 | 18:04 | 49.747
2019-12-22 | 18:04 | 49.747
2019-12-22 | 18:04 | 49.747
2019-12-22 | 18:04 | 49.746
2019-12-22 | 18:04 | 49.745
2019-12-22 | 18:04 | 49.747
2019-12-22 | 18:04 | 49.746
2019-12-22 | 18:04 | 49.746
2019-12-22 | 18:04 | 49.745
2019-12-22 | 18:04 | 49.746
2019-12-22 | 18:04 | 49.748
2019-12-22 | 18:04 | 49.748
2019-12-22 | 18:04 | 49.752
2019-12-22 | 18:04 | 49.752
2019-12-22 | 18:04 | 49.751
2019-12-22 | 18:04 | 49.755
2019-12-22 | 18:04 | 49.755
2019-12-22 | 18:04 | 49.756
2019-12-22 | 18:04 | 49.759
2019-12-22 | 18:04 | 49.76
2019-12-22 | 18:04 | 49.763
2019-12-22 | 18:04 | 49.766
2019-12-22 | 18:04 | 49.769
2019-12-22 | 18:04 | 49.771
2019-12-22 | 18:04 | 49.776
2019-12-22 | 18:04 | 49.78
2019-12-22 | 18:04 | 49.78
2019-12-22 | 18:04 | 49.784
2019-12-22 | 18:04 | 49.786
2019-12-22 | 18:04 | 49.787
2019-12-22 | 18:04 | 49.788
2019-12-22 | 18:04 | 49.791
2019-12-22 | 18:04 | 49.791
2019-12-22 | 18:04 | 49.789
2019-12-22 | 18:04 | 49.789
2019-12-22 | 18:04 | 49.791
2019-12-22 | 18:04 | 49.793
2019-12-22 | 18:04 | 49.791
2019-12-22 | 18:04 | 49.793
2019-12-22 | 18:04 | 49.795
2019-12-22 | 18:04 | 49.797
2019-12-22 | 18:04 | 49.798
2019-12-22 | 18:04 | 49.804
2019-12-22 | 18:04 | 49.811
2019-12-22 | 18:04 | 49.816
2019-12-22 | 18:04 | 49.824
2019-12-22 | 18:05 | 49.832
2019-12-22 | 18:05 | 49.839
2019-12-22 | 18:05 | 49.848
2019-12-22 | 18:05 | 49.858
2019-12-22 | 18:05 | 49.866
2019-12-22 | 18:05 | 49.878
2019-12-22 | 18:05 | 49.888
2019-12-22 | 18:05 | 49.899
2019-12-22 | 18:05 | 49.909
2019-12-22 | 18:05 | 49.917
2019-12-22 | 18:05 | 49.93
2019-12-22 | 18:05 | 49.941
2019-12-22 | 18:05 | 49.949
2019-12-22 | 18:05 | 49.957
2019-12-22 | 18:05 | 49.964
2019-12-22 | 18:05 | 49.97
2019-12-22 | 18:05 | 49.978
2019-12-22 | 18:05 | 49.986
2019-12-22 | 18:05 | 49.994
2019-12-22 | 18:05 | 50
2019-12-22 | 18:05 | 50.009
2019-12-22 | 18:05 | 50.016
2019-12-22 | 18:05 | 50.02
2019-12-22 | 18:05 | 50.026
2019-12-22 | 18:05 | 50.031
2019-12-22 | 18:05 | 50.032
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:05 | 50.037
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.033
2019-12-22 | 18:05 | 50.033
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.037
2019-12-22 | 18:05 | 50.038
2019-12-22 | 18:05 | 50.04
2019-12-22 | 18:05 | 50.04
2019-12-22 | 18:05 | 50.039
2019-12-22 | 18:05 | 50.04
2019-12-22 | 18:05 | 50.04
2019-12-22 | 18:05 | 50.038
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.033
2019-12-22 | 18:05 | 50.032
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.033
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.033
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:06 | 50.036
2019-12-22 | 18:06 | 50.034
2019-12-22 | 18:06 | 50.032
2019-12-22 | 18:06 | 50.033
2019-12-22 | 18:06 | 50.032
2019-12-22 | 18:06 | 50.03
2019-12-22 | 18:06 | 50.031
2019-12-22 | 18:06 | 50.034
2019-12-22 | 18:06 | 50.037
2019-12-22 | 18:06 | 50.04
2019-12-22 | 18:06 | 50.043
2019-12-22 | 18:06 | 50.047
2019-12-22 | 18:06 | 50.052
2019-12-22 | 18:06 | 50.055
2019-12-22 | 18:06 | 50.061
2019-12-22 | 18:06 | 50.066
2019-12-22 | 18:06 | 50.067
2019-12-22 | 18:06 | 50.07
2019-12-22 | 18:06 | 50.071
2019-12-22 | 18:06 | 50.071
2019-12-22 | 18:06 | 50.075
2019-12-22 | 18:06 | 50.077
2019-12-22 | 18:06 | 50.078
2019-12-22 | 18:06 | 50.083
2019-12-22 | 18:06 | 50.084
2019-12-22 | 18:06 | 50.083
2019-12-22 | 18:06 | 50.086
2019-12-22 | 18:06 | 50.086
2019-12-22 | 18:06 | 50.085
2019-12-22 | 18:06 | 50.087

## Event 20191226-1
In UTC
Date | Time | Freq
2019-12-26 | 7:41 | 50.046
2019-12-26 | 7:41 | 50.045
2019-12-26 | 7:41 | 50.044
2019-12-26 | 7:41 | 50.044
2019-12-26 | 7:41 | 50.045
2019-12-26 | 7:41 | 50.044
2019-12-26 | 7:41 | 50.044
2019-12-26 | 7:41 | 50.046
2019-12-26 | 7:41 | 50.046
2019-12-26 | 7:41 | 50.05
2019-12-26 | 7:41 | 50.051
2019-12-26 | 7:41 | 50.05
2019-12-26 | 7:41 | 50.05
2019-12-26 | 7:41 | 50.053
2019-12-26 | 7:41 | 50.051
2019-12-26 | 7:41 | 50.052
2019-12-26 | 7:41 | 50.054
2019-12-26 | 7:41 | 50.054
2019-12-26 | 7:41 | 50.055
2019-12-26 | 7:41 | 50.055
2019-12-26 | 7:41 | 50.053
2019-12-26 | 7:41 | 50.054
2019-12-26 | 7:41 | 50.052
2019-12-26 | 7:41 | 50.049
2019-12-26 | 7:41 | 50.047
2019-12-26 | 7:41 | 50.044
2019-12-26 | 7:41 | 50.045
2019-12-26 | 7:41 | 50.043
2019-12-26 | 7:41 | 50.041
2019-12-26 | 7:41 | 50.041
2019-12-26 | 7:41 | 50.041
2019-12-26 | 7:42 | 50.039
2019-12-26 | 7:42 | 50.039
2019-12-26 | 7:42 | 50.038
2019-12-26 | 7:42 | 50.04
2019-12-26 | 7:42 | 50.038
2019-12-26 | 7:42 | 50.039
2019-12-26 | 7:42 | 50.039
2019-12-26 | 7:42 | 50.039
2019-12-26 | 7:42 | 50.041
2019-12-26 | 7:42 | 50.04
2019-12-26 | 7:42 | 50.039
2019-12-26 | 7:42 | 50.039
2019-12-26 | 7:42 | 50.037
2019-12-26 | 7:42 | 50.037
2019-12-26 | 7:42 | 50.037
2019-12-26 | 7:42 | 50.037
2019-12-26 | 7:42 | 50.038
2019-12-26 | 7:42 | 50.04
2019-12-26 | 7:42 | 50.042
2019-12-26 | 7:42 | 50.046
2019-12-26 | 7:42 | 50.048
2019-12-26 | 7:42 | 50.052
2019-12-26 | 7:42 | 50.051
2019-12-26 | 7:42 | 50.051
2019-12-26 | 7:42 | 50.054
2019-12-26 | 7:42 | 50.053
2019-12-26 | 7:42 | 50.053
2019-12-26 | 7:42 | 50.052
2019-12-26 | 7:42 | 50.051
2019-12-26 | 7:42 | 50.051
2019-12-26 | 7:42 | 50.051
2019-12-26 | 7:42 | 50.052
2019-12-26 | 7:42 | 50.051
2019-12-26 | 7:42 | 50.052
2019-12-26 | 7:42 | 50.05
2019-12-26 | 7:42 | 50.05
2019-12-26 | 7:42 | 50.05
2019-12-26 | 7:42 | 50.047
2019-12-26 | 7:42 | 50.047
2019-12-26 | 7:42 | 50.05
2019-12-26 | 7:42 | 50.037
2019-12-26 | 7:42 | 50.003
2019-12-26 | 7:42 | 49.961
2019-12-26 | 7:42 | 49.93
2019-12-26 | 7:42 | 49.915
2019-12-26 | 7:42 | 49.908
2019-12-26 | 7:42 | 49.909
2019-12-26 | 7:42 | 49.914
2019-12-26 | 7:42 | 49.917
2019-12-26 | 7:42 | 49.919
2019-12-26 | 7:42 | 49.923
2019-12-26 | 7:42 | 49.924
2019-12-26 | 7:42 | 49.924
2019-12-26 | 7:42 | 49.925
2019-12-26 | 7:42 | 49.925
2019-12-26 | 7:42 | 49.926
2019-12-26 | 7:42 | 49.93
2019-12-26 | 7:42 | 49.929
2019-12-26 | 7:42 | 49.928
2019-12-26 | 7:42 | 49.93
2019-12-26 | 7:43 | 49.929
2019-12-26 | 7:43 | 49.928
2019-12-26 | 7:43 | 49.929
2019-12-26 | 7:43 | 49.927
2019-12-26 | 7:43 | 49.929
2019-12-26 | 7:43 | 49.929
2019-12-26 | 7:43 | 49.928
2019-12-26 | 7:43 | 49.929
2019-12-26 | 7:43 | 49.929
2019-12-26 | 7:43 | 49.926
2019-12-26 | 7:43 | 49.925
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.922
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.922
2019-12-26 | 7:43 | 49.922
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.92
2019-12-26 | 7:43 | 49.919
2019-12-26 | 7:43 | 49.918
2019-12-26 | 7:43 | 49.917
2019-12-26 | 7:43 | 49.917
2019-12-26 | 7:43 | 49.917
2019-12-26 | 7:43 | 49.917
2019-12-26 | 7:43 | 49.918
2019-12-26 | 7:43 | 49.922
2019-12-26 | 7:43 | 49.921
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.925
2019-12-26 | 7:43 | 49.924
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.924
2019-12-26 | 7:43 | 49.922
2019-12-26 | 7:43 | 49.922
2019-12-26 | 7:43 | 49.923
2019-12-26 | 7:43 | 49.921
2019-12-26 | 7:43 | 49.919
2019-12-26 | 7:43 | 49.92
2019-12-26 | 7:43 | 49.918
2019-12-26 | 7:43 | 49.918
2019-12-26 | 7:43 | 49.918
2019-12-26 | 7:43 | 49.916
2019-12-26 | 7:43 | 49.914
2019-12-26 | 7:43 | 49.914
2019-12-26 | 7:43 | 49.912
2019-12-26 | 7:43 | 49.913
2019-12-26 | 7:43 | 49.914
2019-12-26 | 7:43 | 49.916
2019-12-26 | 7:43 | 49.92
2019-12-26 | 7:43 | 49.925
2019-12-26 | 7:43 | 49.929
2019-12-26 | 7:43 | 49.935
2019-12-26 | 7:43 | 49.938
2019-12-26 | 7:43 | 49.944
2019-12-26 | 7:44 | 49.949
2019-12-26 | 7:44 | 49.955
2019-12-26 | 7:44 | 49.962
2019-12-26 | 7:44 | 49.967
2019-12-26 | 7:44 | 49.972
2019-12-26 | 7:44 | 49.976
2019-12-26 | 7:44 | 49.977
2019-12-26 | 7:44 | 49.979
2019-12-26 | 7:44 | 49.981
2019-12-26 | 7:44 | 49.979
2019-12-26 | 7:44 | 49.985
2019-12-26 | 7:44 | 49.986
2019-12-26 | 7:44 | 49.987
2019-12-26 | 7:44 | 49.99
2019-12-26 | 7:44 | 49.992
2019-12-26 | 7:44 | 49.991
2019-12-26 | 7:44 | 49.993
2019-12-26 | 7:44 | 49.997
2019-12-26 | 7:44 | 49.998
2019-12-26 | 7:44 | 50
2019-12-26 | 7:44 | 50.002
2019-12-26 | 7:44 | 50.005
2019-12-26 | 7:44 | 50.004
2019-12-26 | 7:44 | 50.003
2019-12-26 | 7:44 | 50
2019-12-26 | 7:44 | 49.996
2019-12-26 | 7:44 | 49.993
2019-12-26 | 7:44 | 49.991
2019-12-26 | 7:44 | 49.991
2019-12-22 | 18:04 | 49.755
2019-12-22 | 18:04 | 49.755
2019-12-22 | 18:04 | 49.756
2019-12-22 | 18:04 | 49.759
2019-12-22 | 18:04 | 49.76
2019-12-22 | 18:04 | 49.763
2019-12-22 | 18:04 | 49.766
2019-12-22 | 18:04 | 49.769
2019-12-22 | 18:04 | 49.771
2019-12-22 | 18:04 | 49.776
2019-12-22 | 18:04 | 49.78
2019-12-22 | 18:04 | 49.78
2019-12-22 | 18:04 | 49.784
2019-12-22 | 18:04 | 49.786
2019-12-22 | 18:04 | 49.787
2019-12-22 | 18:04 | 49.788
2019-12-22 | 18:04 | 49.791
2019-12-22 | 18:04 | 49.791
2019-12-22 | 18:04 | 49.789
2019-12-22 | 18:04 | 49.789
2019-12-22 | 18:04 | 49.791
2019-12-22 | 18:04 | 49.793
2019-12-22 | 18:04 | 49.791
2019-12-22 | 18:04 | 49.793
2019-12-22 | 18:04 | 49.795
2019-12-22 | 18:04 | 49.797
2019-12-22 | 18:04 | 49.798
2019-12-22 | 18:04 | 49.804
2019-12-22 | 18:04 | 49.811
2019-12-22 | 18:04 | 49.816
2019-12-22 | 18:04 | 49.824
2019-12-22 | 18:05 | 49.832
2019-12-22 | 18:05 | 49.839
2019-12-22 | 18:05 | 49.848
2019-12-22 | 18:05 | 49.858
2019-12-22 | 18:05 | 49.866
2019-12-22 | 18:05 | 49.878
2019-12-22 | 18:05 | 49.888
2019-12-22 | 18:05 | 49.899
2019-12-22 | 18:05 | 49.909
2019-12-22 | 18:05 | 49.917
2019-12-22 | 18:05 | 49.93
2019-12-22 | 18:05 | 49.941
2019-12-22 | 18:05 | 49.949
2019-12-22 | 18:05 | 49.957
2019-12-22 | 18:05 | 49.964
2019-12-22 | 18:05 | 49.97
2019-12-22 | 18:05 | 49.978
2019-12-22 | 18:05 | 49.986
2019-12-22 | 18:05 | 49.994
2019-12-22 | 18:05 | 50
2019-12-22 | 18:05 | 50.009
2019-12-22 | 18:05 | 50.016
2019-12-22 | 18:05 | 50.02
2019-12-22 | 18:05 | 50.026
2019-12-22 | 18:05 | 50.031
2019-12-22 | 18:05 | 50.032
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:05 | 50.037
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.033
2019-12-22 | 18:05 | 50.033
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.037
2019-12-22 | 18:05 | 50.038
2019-12-22 | 18:05 | 50.04
2019-12-22 | 18:05 | 50.04
2019-12-22 | 18:05 | 50.039
2019-12-22 | 18:05 | 50.04
2019-12-22 | 18:05 | 50.04
2019-12-22 | 18:05 | 50.038
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.033
2019-12-22 | 18:05 | 50.032
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.033
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.036
2019-12-22 | 18:05 | 50.034
2019-12-22 | 18:05 | 50.033
2019-12-22 | 18:05 | 50.035
2019-12-22 | 18:06 | 50.036
2019-12-22 | 18:06 | 50.034
2019-12-22 | 18:06 | 50.032
2019-12-22 | 18:06 | 50.033
2019-12-22 | 18:06 | 50.032
2019-12-22 | 18:06 | 50.03
2019-12-22 | 18:06 | 50.031
2019-12-22 | 18:06 | 50.034
2019-12-22 | 18:06 | 50.037
2019-12-22 | 18:06 | 50.04
2019-12-22 | 18:06 | 50.043
2019-12-22 | 18:06 | 50.047
2019-12-22 | 18:06 | 50.052
2019-12-22 | 18:06 | 50.055
2019-12-22 | 18:06 | 50.061
2019-12-22 | 18:06 | 50.066
2019-12-22 | 18:06 | 50.067
2019-12-22 | 18:06 | 50.07
2019-12-22 | 18:06 | 50.071
2019-12-22 | 18:06 | 50.071
2019-12-22 | 18:06 | 50.075
2019-12-22 | 18:06 | 50.077
2019-12-22 | 18:06 | 50.078
2019-12-22 | 18:06 | 50.083
2019-12-22 | 18:06 | 50.084
2019-12-22 | 18:06 | 50.083
2019-12-22 | 18:06 | 50.086
2019-12-22 | 18:06 | 50.086
2019-12-22 | 18:06 | 50.085
2019-12-22 | 18:06 | 50.087